## Index
File | Description | Notes
result_summary.csv | (판정기준) | (기능시험 결과 요약)
frt_rms_100.csv | LH1 Ride-Through 시험 (출력 100%) (기능시험결과 1) | (결과검토1)
frt_rms_100
frt_rms_20.csv | LH1 Ride-Through 시험 (출력 20%) (기능시험결과 2) | (결과검토2)
frt_rms_20

## result_summary.csv
Result | Test Name | Ride Through Freq(Hz) | Ride Through Duration(s) | Power Level | Dataset File
Pass | SA10_ride_through_HF1 | 62 | 299 | 100 | frt_rms_100.csv
Pass | SA10_ride_through_HF1 | 62 | 299 | 20 | frt_rms_20.csv

## frt_rms_100.csv
TIME | AC_VRMS_1 | AC_IRMS_1 | AC_P_1 | AC_S_1 | AC_Q_1 | AC_PF_1 | AC_FREQ_1 | AC_VRMS_2 | AC_IRMS_2 | AC_P_2 | AC_S_2 | AC_Q_2 | AC_PF_2 | AC_FREQ_2 | AC_VRMS_3 | AC_IRMS_3 | AC_P_3 | AC_S_3 | AC_Q_3 | AC_PF_3 | AC_FREQ_3 | DC_V | DC_I | DC_P | AC_IRMS_MIN
0 | 277.347 | 5.83 | 1614 |  |  |  | 59.999 | 277.387 | 5.93 | 1615 |  |  |  | 60 | 277.273 | 5.84 | 1617 |  |  |  | 60.001 | 538.25 | 0.15 | 81
0.56 | 277.391 | 5.83 | 1614 |  |  |  | 60 | 277.543 | 5.96 | 1623 |  |  |  | 60.002 | 277.239 | 5.85 | 1619 |  |  |  | 60.001 | 533.44 | 0.154 | 82
1.06 | 277.391 | 5.83 | 1614 |  |  |  | 60 | 277.543 | 5.96 | 1623 |  |  |  | 60.002 | 277.239 | 5.85 | 1619 |  |  |  | 60.001 | 533.44 | 0.154 | 82
1.56 | 277.436 | 5.83 | 1615 |  |  |  | 60 | 277.404 | 5.95 | 1620 |  |  |  | 60 | 277.321 | 5.85 | 1619 |  |  |  | 60.003 | 533.47 | 0.148 | 79
2.06 | 277.436 | 5.83 | 1615 |  |  |  | 60 | 277.404 | 5.95 | 1620 |  |  |  | 60 | 277.321 | 5.85 | 1619 |  |  |  | 60.003 | 533.47 | 0.148 | 79
2.56 | 277.386 | 5.85 | 1618 |  |  |  | 60.001 | 277.339 | 5.98 | 1627 |  |  |  | 59.999 | 277.31 | 5.84 | 1617 |  |  |  | 60 | 533.45 | 0.155 | 83
3.06 | 277.386 | 5.85 | 1618 |  |  |  | 60.001 | 277.339 | 5.98 | 1627 |  |  |  | 59.999 | 277.31 | 5.84 | 1617 |  |  |  | 60 | 533.45 | 0.155 | 83
3.56 | 277.448 | 5.85 | 1620 |  |  |  | 60 | 277.445 | 5.95 | 1621 |  |  |  | 60 | 277.283 | 5.86 | 1624 |  |  |  | 59.999 | 533 | 0.154 | 82
4.06 | 277.448 | 5.85 | 1620 |  |  |  | 60 | 277.445 | 5.95 | 1621 |  |  |  | 60 | 277.283 | 5.86 | 1624 |  |  |  | 59.999 | 533 | 0.154 | 82
4.56 | 277.35 | 5.8 | 1605 |  |  |  | 60 | 277.361 | 5.91 | 1607 |  |  |  | 60.001 | 277.245 | 5.82 | 1610 |  |  |  | 60 | 527.01 | 0.153 | 81
4.64 | 277.35 | 5.8 | 1605 |  |  |  | 60 | 277.361 | 5.91 | 1607 |  |  |  | 60.001 | 277.245 | 5.82 | 1610 |  |  |  | 60 | 527.01 | 0.153 | 81 | 4.64
5.06 | 277.35 | 5.8 | 1605 |  |  |  | 60 | 277.361 | 5.91 | 1607 |  |  |  | 60.001 | 277.245 | 5.82 | 1610 |  |  |  | 60 | 527.01 | 0.153 | 81 | 4.64
5.56 | 277.676 | 6.02 | 1603 |  |  |  | 58.58 | 277.778 | 6.13 | 1608 |  |  |  | 58.58 | 277.473 | 6.04 | 1611 |  |  |  | 58.579 | 527.15 | 0.152 | 80 | 4.64
6.06 | 277.676 | 6.02 | 1603 |  |  |  | 58.58 | 277.778 | 6.13 | 1608 |  |  |  | 58.58 | 277.473 | 6.04 | 1611 |  |  |  | 58.579 | 527.15 | 0.152 | 80 | 4.64
6.56 | 277.449 | 5.93 | 1612 |  |  |  | 58.581 | 277.481 | 6.05 | 1621 |  |  |  | 58.579 | 277.427 | 5.98 | 1626 |  |  |  | 58.58 | 533.44 | 0.154 | 82 | 4.64
7.06 | 277.449 | 5.93 | 1612 |  |  |  | 58.581 | 277.481 | 6.05 | 1621 |  |  |  | 58.579 | 277.427 | 5.98 | 1626 |  |  |  | 58.58 | 533.44 | 0.154 | 82 | 4.64
7.56 | 277.442 | 5.88 | 1614 |  |  |  | 58.581 | 277.563 | 6.01 | 1624 |  |  |  | 58.583 | 277.342 | 5.92 | 1624 |  |  |  | 58.581 | 533.47 | 0.152 | 81 | 4.64
8.06 | 277.442 | 5.88 | 1614 |  |  |  | 58.581 | 277.563 | 6.01 | 1624 |  |  |  | 58.583 | 277.342 | 5.92 | 1624 |  |  |  | 58.581 | 533.47 | 0.152 | 81 | 4.64
8.56 | 277.353 | 5.86 | 1616 |  |  |  | 58.579 | 277.394 | 5.97 | 1618 |  |  |  | 58.58 | 277.261 | 5.88 | 1622 |  |  |  | 58.58 | 533.43 | 0.152 | 81 | 4.64
9.06 | 277.353 | 5.86 | 1616 |  |  |  | 58.579 | 277.394 | 5.97 | 1618 |  |  |  | 58.58 | 277.261 | 5.88 | 1622 |  |  |  | 58.58 | 533.43 | 0.152 | 81 | 4.64
9.56 | 277.384 | 5.85 | 1616 |  |  |  | 58.58 | 277.264 | 5.96 | 1619 |  |  |  | 58.581 | 277.233 | 5.87 | 1623 |  |  |  | 58.581 | 533.4 | 0.151 | 81 | 4.64
10.06 | 277.384 | 5.85 | 1616 |  |  |  | 58.58 | 277.264 | 5.96 | 1619 |  |  |  | 58.581 | 277.233 | 5.87 | 1623 |  |  |  | 58.581 | 533.4 | 0.151 | 81 | 4.64
10.56 | 277.415 | 5.79 | 1600 |  |  |  | 58.58 | 277.417 | 5.9 | 1604 |  |  |  | 58.58 | 277.339 | 5.82 | 1609 |  |  |  | 58.58 | 538.79 | 0.146 | 79 | 4.64
11.06 | 277.415 | 5.79 | 1600 |  |  |  | 58.58 | 277.417 | 5.9 | 1604 |  |  |  | 58.58 | 277.339 | 5.82 | 1609 |  |  |  | 58.58 | 538.79 | 0.146 | 79 | 4.64
11.56 | 277.372 | 5.63 | 1556 |  |  |  | 58.581 | 277.312 | 5.76 | 1566 |  |  |  | 58.581 | 277.286 | 5.67 | 1568 |  |  |  | 58.58 | 539.89 | 0.151 | 82 | 4.64
12.06 | 277.372 | 5.63 | 1556 |  |  |  | 58.581 | 277.312 | 5.76 | 1566 |  |  |  | 58.581 | 277.286 | 5.67 | 1568 |  |  |  | 58.58 | 539.89 | 0.151 | 82 | 4.64
12.56 | 277.431 | 5.84 | 1615 |  |  |  | 58.58 | 277.487 | 5.97 | 1625 |  |  |  | 58.581 | 277.28 | 5.86 | 1622 |  |  |  | 58.58 | 535.06 | 0.147 | 78 | 4.64
13.06 | 277.431 | 5.84 | 1615 |  |  |  | 58.58 | 277.487 | 5.97 | 1625 |  |  |  | 58.581 | 277.28 | 5.86 | 1622 |  |  |  | 58.58 | 535.06 | 0.147 | 78 | 4.64
13.56 | 277.376 | 5.83 | 1613 |  |  |  | 58.58 | 277.375 | 5.95 | 1619 |  |  |  | 58.58 | 277.238 | 5.84 | 1617 |  |  |  | 58.581 | 533.43 | 0.149 | 80 | 4.64
14.06 | 277.376 | 5.83 | 1613 |  |  |  | 58.58 | 277.375 | 5.95 | 1619 |  |  |  | 58.58 | 277.238 | 5.84 | 1617 |  |  |  | 58.581 | 533.43 | 0.149 | 80 | 4.64
14.56 | 277.457 | 5.83 | 1614 |  |  |  | 58.58 | 277.49 | 5.95 | 1619 |  |  |  | 58.58 | 277.213 | 5.86 | 1623 |  |  |  | 58.58 | 533.46 | 0.152 | 81 | 4.64
15.08 | 277.457 | 5.83 | 1614 |  |  |  | 58.58 | 277.49 | 5.95 | 1619 |  |  |  | 58.58 | 277.213 | 5.86 | 1623 |  |  |  | 58.58 | 533.46 | 0.152 | 81 | 4.64
15.56 | 275.525 | 6.42 | 1615 |  |  |  | 59.645 | 275.596 | 6.52 | 1620 |  |  |  | 59.8 | 275.562 | 6.43 | 1618 |  |  |  | 59.958 | 533.43 | 0.15 | 80 | 4.64
16.06 | 275.525 | 6.42 | 1615 |  |  |  | 59.645 | 275.596 | 6.52 | 1620 |  |  |  | 59.8 | 275.562 | 6.43 | 1618 |  |  |  | 59.958 | 533.43 | 0.15 | 80 | 4.64
16.56 | 275.778 | 6.45 | 1606 |  |  |  | 61.92 | 275.588 | 6.57 | 1612 |  |  |  | 61.92 | 275.738 | 6.47 | 1612 |  |  |  | 61.919 | 530.1 | 0.147 | 78 | 4.64
17.06 | 275.778 | 6.45 | 1606 |  |  |  | 61.92 | 275.588 | 6.57 | 1612 |  |  |  | 61.92 | 275.738 | 6.47 | 1612 |  |  |  | 61.919 | 530.1 | 0.147 | 78 | 4.64
17.56 | 276.498 | 6.23 | 1601 |  |  |  | 61.92 | 276.619 | 6.33 | 1604 |  |  |  | 61.92 | 276.467 | 6.24 | 1602 |  |  |  | 61.921 | 527 | 0.15 | 79 | 4.64
18.06 | 276.498 | 6.23 | 1601 |  |  |  | 61.92 | 276.619 | 6.33 | 1604 |  |  |  | 61.92 | 276.467 | 6.24 | 1602 |  |  |  | 61.921 | 527 | 0.15 | 79 | 4.64
18.56 | 277.082 | 5.99 | 1606 |  |  |  | 61.92 | 276.941 | 6.09 | 1606 |  |  |  | 61.919 | 276.913 | 6.02 | 1612 |  |  |  | 61.919 | 530.51 | 0.146 | 77 | 4.64
19.06 | 277.082 | 5.99 | 1606 |  |  |  | 61.92 | 276.941 | 6.09 | 1606 |  |  |  | 61.919 | 276.913 | 6.02 | 1612 |  |  |  | 61.919 | 530.51 | 0.146 | 77 | 4.64
19.56 | 277.342 | 5.9 | 1611 |  |  |  | 61.921 | 277.39 | 6.02 | 1618 |  |  |  | 61.923 | 277.257 | 5.93 | 1620 |  |  |  | 61.92 | 533.43 | 0.15 | 80 | 4.64
20.06 | 277.342 | 5.9 | 1611 |  |  |  | 61.921 | 277.39 | 6.02 | 1618 |  |  |  | 61.923 | 277.257 | 5.93 | 1620 |  |  |  | 61.92 | 533.43 | 0.15 | 80 | 4.64
20.56 | 277.372 | 5.85 | 1609 |  |  |  | 61.92 | 277.355 | 5.98 | 1621 |  |  |  | 61.921 | 277.295 | 5.88 | 1619 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
21.06 | 277.372 | 5.85 | 1609 |  |  |  | 61.92 | 277.355 | 5.98 | 1621 |  |  |  | 61.921 | 277.295 | 5.88 | 1619 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
21.56 | 277.478 | 5.83 | 1611 |  |  |  | 61.921 | 277.293 | 5.96 | 1619 |  |  |  | 61.919 | 277.317 | 5.87 | 1620 |  |  |  | 61.92 | 533.41 | 0.149 | 79 | 4.64
22.06 | 277.478 | 5.83 | 1611 |  |  |  | 61.921 | 277.293 | 5.96 | 1619 |  |  |  | 61.919 | 277.317 | 5.87 | 1620 |  |  |  | 61.92 | 533.41 | 0.149 | 79 | 4.64
22.56 | 277.416 | 5.82 | 1609 |  |  |  | 61.92 | 277.452 | 5.94 | 1616 |  |  |  | 61.92 | 277.306 | 5.86 | 1621 |  |  |  | 61.921 | 536.72 | 0.151 | 81 | 4.64
23.1 | 277.416 | 5.82 | 1609 |  |  |  | 61.92 | 277.452 | 5.94 | 1616 |  |  |  | 61.92 | 277.306 | 5.86 | 1621 |  |  |  | 61.921 | 536.72 | 0.151 | 81 | 4.64
23.6 | 277.5 | 5.65 | 1563 |  |  |  | 61.92 | 277.282 | 5.79 | 1574 |  |  |  | 61.919 | 277.284 | 5.67 | 1570 |  |  |  | 61.92 | 539.82 | 0.15 | 81 | 4.64
24.08 | 277.5 | 5.65 | 1563 |  |  |  | 61.92 | 277.282 | 5.79 | 1574 |  |  |  | 61.919 | 277.284 | 5.67 | 1570 |  |  |  | 61.92 | 539.82 | 0.15 | 81 | 4.64
24.58 | 277.404 | 5.83 | 1612 |  |  |  | 61.919 | 277.534 | 5.98 | 1628 |  |  |  | 61.921 | 277.421 | 5.85 | 1621 |  |  |  | 61.919 | 536.39 | 0.153 | 82 | 4.64
25.06 | 277.404 | 5.83 | 1612 |  |  |  | 61.919 | 277.534 | 5.98 | 1628 |  |  |  | 61.921 | 277.421 | 5.85 | 1621 |  |  |  | 61.919 | 536.39 | 0.153 | 82 | 4.64
25.56 | 277.481 | 5.83 | 1613 |  |  |  | 61.921 | 277.351 | 5.93 | 1614 |  |  |  | 61.921 | 277.401 | 5.86 | 1624 |  |  |  | 61.921 | 533.38 | 0.151 | 81 | 4.64
26.1 | 277.389 | 5.83 | 1614 |  |  |  | 61.919 | 277.506 | 5.93 | 1616 |  |  |  | 61.923 | 277.383 | 5.84 | 1618 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 4.64
26.6 | 277.389 | 5.83 | 1614 |  |  |  | 61.919 | 277.506 | 5.93 | 1616 |  |  |  | 61.923 | 277.383 | 5.84 | 1618 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 4.64
27.09 | 277.451 | 5.84 | 1616 |  |  |  | 61.92 | 277.433 | 5.94 | 1618 |  |  |  | 61.92 | 277.336 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.15 | 80 | 4.64
27.59 | 277.451 | 5.84 | 1616 |  |  |  | 61.92 | 277.433 | 5.94 | 1618 |  |  |  | 61.92 | 277.336 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.15 | 80 | 4.64
28.07 | 277.475 | 5.81 | 1609 |  |  |  | 61.919 | 277.3 | 5.94 | 1616 |  |  |  | 61.919 | 277.408 | 5.83 | 1615 |  |  |  | 61.919 | 530.11 | 0.152 | 81 | 4.64
28.57 | 277.475 | 5.81 | 1609 |  |  |  | 61.919 | 277.3 | 5.94 | 1616 |  |  |  | 61.919 | 277.408 | 5.83 | 1615 |  |  |  | 61.919 | 530.11 | 0.152 | 81 | 4.64
29.06 | 277.408 | 5.79 | 1604 |  |  |  | 61.921 | 277.461 | 5.9 | 1606 |  |  |  | 61.921 | 277.382 | 5.81 | 1610 |  |  |  | 61.92 | 527 | 0.155 | 82 | 4.64
29.56 | 277.408 | 5.79 | 1604 |  |  |  | 61.921 | 277.461 | 5.9 | 1606 |  |  |  | 61.921 | 277.382 | 5.81 | 1610 |  |  |  | 61.92 | 527 | 0.155 | 82 | 4.64
30.06 | 277.479 | 5.8 | 1607 |  |  |  | 61.921 | 277.316 | 5.91 | 1606 |  |  |  | 61.919 | 277.358 | 5.84 | 1618 |  |  |  | 61.92 | 530.46 | 0.151 | 80 | 4.64
30.56 | 277.479 | 5.8 | 1607 |  |  |  | 61.921 | 277.316 | 5.91 | 1606 |  |  |  | 61.919 | 277.358 | 5.84 | 1618 |  |  |  | 61.92 | 530.46 | 0.151 | 80 | 4.64
31.06 | 277.35 | 5.82 | 1611 |  |  |  | 61.919 | 277.508 | 5.94 | 1617 |  |  |  | 61.922 | 277.324 | 5.84 | 1618 |  |  |  | 61.92 | 533.45 | 0.15 | 80 | 4.64
31.56 | 277.35 | 5.82 | 1611 |  |  |  | 61.919 | 277.508 | 5.94 | 1617 |  |  |  | 61.922 | 277.324 | 5.84 | 1618 |  |  |  | 61.92 | 533.45 | 0.15 | 80 | 4.64
32.06 | 277.426 | 5.82 | 1611 |  |  |  | 61.92 | 277.37 | 5.95 | 1620 |  |  |  | 61.92 | 277.412 | 5.86 | 1623 |  |  |  | 61.923 | 533.43 | 0.15 | 80 | 4.64
32.56 | 277.426 | 5.82 | 1611 |  |  |  | 61.92 | 277.37 | 5.95 | 1620 |  |  |  | 61.92 | 277.412 | 5.86 | 1623 |  |  |  | 61.923 | 533.43 | 0.15 | 80 | 4.64
33.06 | 277.345 | 5.83 | 1612 |  |  |  | 61.921 | 277.365 | 5.95 | 1622 |  |  |  | 61.919 | 277.367 | 5.86 | 1623 |  |  |  | 61.919 | 533.44 | 0.147 | 78 | 4.64
33.56 | 277.345 | 5.83 | 1612 |  |  |  | 61.921 | 277.365 | 5.95 | 1622 |  |  |  | 61.919 | 277.367 | 5.86 | 1623 |  |  |  | 61.919 | 533.44 | 0.147 | 78 | 4.64
34.06 | 277.4 | 5.82 | 1611 |  |  |  | 61.921 | 277.425 | 5.93 | 1617 |  |  |  | 61.918 | 277.346 | 5.85 | 1620 |  |  |  | 61.92 | 536.64 | 0.152 | 82 | 4.64
34.56 | 277.4 | 5.82 | 1611 |  |  |  | 61.921 | 277.425 | 5.93 | 1617 |  |  |  | 61.918 | 277.346 | 5.85 | 1620 |  |  |  | 61.92 | 536.64 | 0.152 | 82 | 4.64
35.06 | 277.326 | 5.64 | 1560 |  |  |  | 61.918 | 277.303 | 5.75 | 1564 |  |  |  | 61.921 | 277.313 | 5.65 | 1565 |  |  |  | 61.92 | 539.88 | 0.155 | 83 | 4.64
35.56 | 277.326 | 5.64 | 1560 |  |  |  | 61.918 | 277.303 | 5.75 | 1564 |  |  |  | 61.921 | 277.313 | 5.65 | 1565 |  |  |  | 61.92 | 539.88 | 0.155 | 83 | 4.64
36.06 | 277.395 | 5.83 | 1614 |  |  |  | 61.921 | 277.484 | 5.96 | 1623 |  |  |  | 61.92 | 277.285 | 5.87 | 1625 |  |  |  | 61.921 | 536.39 | 0.145 | 78 | 4.64
36.56 | 277.395 | 5.83 | 1614 |  |  |  | 61.921 | 277.484 | 5.96 | 1623 |  |  |  | 61.92 | 277.285 | 5.87 | 1625 |  |  |  | 61.921 | 536.39 | 0.145 | 78 | 4.64
37.06 | 277.449 | 5.82 | 1610 |  |  |  | 61.921 | 277.374 | 5.95 | 1619 |  |  |  | 61.921 | 277.368 | 5.85 | 1620 |  |  |  | 61.921 | 533.46 | 0.153 | 82 | 4.64
37.56 | 277.449 | 5.82 | 1610 |  |  |  | 61.921 | 277.374 | 5.95 | 1619 |  |  |  | 61.921 | 277.368 | 5.85 | 1620 |  |  |  | 61.921 | 533.46 | 0.153 | 82 | 4.64
38.06 | 277.386 | 5.83 | 1612 |  |  |  | 61.919 | 277.545 | 5.94 | 1618 |  |  |  | 61.922 | 277.336 | 5.86 | 1624 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 4.64
38.56 | 277.386 | 5.83 | 1612 |  |  |  | 61.919 | 277.545 | 5.94 | 1618 |  |  |  | 61.922 | 277.336 | 5.86 | 1624 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 4.64
39.06 | 277.45 | 5.83 | 1613 |  |  |  | 61.921 | 277.421 | 5.94 | 1618 |  |  |  | 61.921 | 277.315 | 5.85 | 1620 |  |  |  | 61.919 | 533.43 | 0.152 | 81 | 4.64
39.56 | 277.45 | 5.83 | 1613 |  |  |  | 61.921 | 277.421 | 5.94 | 1618 |  |  |  | 61.921 | 277.315 | 5.85 | 1620 |  |  |  | 61.919 | 533.43 | 0.152 | 81 | 4.64
40.06 | 277.362 | 5.82 | 1610 |  |  |  | 61.921 | 277.289 | 5.93 | 1616 |  |  |  | 61.92 | 277.295 | 5.84 | 1618 |  |  |  | 61.919 | 530.22 | 0.149 | 79 | 4.64
40.56 | 277.362 | 5.82 | 1610 |  |  |  | 61.921 | 277.289 | 5.93 | 1616 |  |  |  | 61.92 | 277.295 | 5.84 | 1618 |  |  |  | 61.919 | 530.22 | 0.149 | 79 | 4.64
41.06 | 277.42 | 5.78 | 1599 |  |  |  | 61.921 | 277.488 | 5.9 | 1608 |  |  |  | 61.92 | 277.366 | 5.8 | 1606 |  |  |  | 61.919 | 526.95 | 0.152 | 80 | 4.64
41.56 | 277.42 | 5.78 | 1599 |  |  |  | 61.921 | 277.488 | 5.9 | 1608 |  |  |  | 61.92 | 277.366 | 5.8 | 1606 |  |  |  | 61.919 | 526.95 | 0.152 | 80 | 4.64
42.06 | 277.345 | 5.8 | 1604 |  |  |  | 61.921 | 277.38 | 5.93 | 1614 |  |  |  | 61.92 | 277.331 | 5.83 | 1615 |  |  |  | 61.92 | 530.36 | 0.153 | 81 | 4.64
42.56 | 277.345 | 5.8 | 1604 |  |  |  | 61.921 | 277.38 | 5.93 | 1614 |  |  |  | 61.92 | 277.331 | 5.83 | 1615 |  |  |  | 61.92 | 530.36 | 0.153 | 81 | 4.64
43.06 | 277.407 | 5.84 | 1616 |  |  |  | 61.921 | 277.536 | 5.95 | 1622 |  |  |  | 61.923 | 277.302 | 5.86 | 1621 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 4.64
43.56 | 277.407 | 5.84 | 1616 |  |  |  | 61.921 | 277.536 | 5.95 | 1622 |  |  |  | 61.923 | 277.302 | 5.86 | 1621 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 4.64
44.06 | 277.317 | 5.84 | 1615 |  |  |  | 61.919 | 277.41 | 5.94 | 1617 |  |  |  | 61.92 | 277.281 | 5.85 | 1620 |  |  |  | 61.92 | 533.48 | 0.149 | 79 | 4.64
44.56 | 277.317 | 5.84 | 1615 |  |  |  | 61.919 | 277.41 | 5.94 | 1617 |  |  |  | 61.92 | 277.281 | 5.85 | 1620 |  |  |  | 61.92 | 533.48 | 0.149 | 79 | 4.64
45.06 | 277.395 | 5.83 | 1613 |  |  |  | 61.919 | 277.561 | 5.95 | 1622 |  |  |  | 61.923 | 277.252 | 5.86 | 1623 |  |  |  | 61.92 | 533.46 | 0.15 | 80 | 4.64
45.56 | 277.395 | 5.83 | 1613 |  |  |  | 61.919 | 277.561 | 5.95 | 1622 |  |  |  | 61.923 | 277.252 | 5.86 | 1623 |  |  |  | 61.92 | 533.46 | 0.15 | 80 | 4.64
46.06 | 277.443 | 5.83 | 1614 |  |  |  | 61.92 | 277.482 | 5.94 | 1617 |  |  |  | 61.919 | 277.349 | 5.85 | 1620 |  |  |  | 61.92 | 536.72 | 0.147 | 79 | 4.64
46.56 | 277.443 | 5.83 | 1614 |  |  |  | 61.92 | 277.482 | 5.94 | 1617 |  |  |  | 61.919 | 277.349 | 5.85 | 1620 |  |  |  | 61.92 | 536.72 | 0.147 | 79 | 4.64
47.06 | 277.369 | 5.63 | 1557 |  |  |  | 61.92 | 277.306 | 5.77 | 1567 |  |  |  | 61.92 | 277.304 | 5.67 | 1569 |  |  |  | 61.921 | 539.85 | 0.144 | 78 | 4.64
47.56 | 277.369 | 5.63 | 1557 |  |  |  | 61.92 | 277.306 | 5.77 | 1567 |  |  |  | 61.92 | 277.304 | 5.67 | 1569 |  |  |  | 61.921 | 539.85 | 0.144 | 78 | 4.64
48.06 | 277.459 | 5.83 | 1615 |  |  |  | 61.921 | 277.52 | 5.97 | 1625 |  |  |  | 61.919 | 277.278 | 5.87 | 1625 |  |  |  | 61.919 | 536.34 | 0.151 | 81 | 4.64
48.56 | 277.459 | 5.83 | 1615 |  |  |  | 61.921 | 277.52 | 5.97 | 1625 |  |  |  | 61.919 | 277.278 | 5.87 | 1625 |  |  |  | 61.919 | 536.34 | 0.151 | 81 | 4.64
49.06 | 277.353 | 5.83 | 1613 |  |  |  | 61.92 | 277.319 | 5.95 | 1618 |  |  |  | 61.92 | 277.258 | 5.86 | 1622 |  |  |  | 61.921 | 533.46 | 0.148 | 79 | 4.64
49.56 | 277.353 | 5.83 | 1613 |  |  |  | 61.92 | 277.319 | 5.95 | 1618 |  |  |  | 61.92 | 277.258 | 5.86 | 1622 |  |  |  | 61.921 | 533.46 | 0.148 | 79 | 4.64
50.06 | 277.434 | 5.83 | 1613 |  |  |  | 61.92 | 277.538 | 5.94 | 1618 |  |  |  | 61.924 | 277.362 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.149 | 79 | 4.64
50.56 | 277.434 | 5.83 | 1613 |  |  |  | 61.92 | 277.538 | 5.94 | 1618 |  |  |  | 61.924 | 277.362 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.149 | 79 | 4.64
51.06 | 277.348 | 5.84 | 1615 |  |  |  | 61.92 | 277.42 | 5.94 | 1618 |  |  |  | 61.92 | 277.335 | 5.84 | 1618 |  |  |  | 61.92 | 533.42 | 0.147 | 79 | 4.64
51.56 | 277.348 | 5.84 | 1615 |  |  |  | 61.92 | 277.42 | 5.94 | 1618 |  |  |  | 61.92 | 277.335 | 5.84 | 1618 |  |  |  | 61.92 | 533.42 | 0.147 | 79 | 4.64
52.06 | 277.403 | 5.8 | 1606 |  |  |  | 61.921 | 277.48 | 5.93 | 1615 |  |  |  | 61.921 | 277.303 | 5.84 | 1617 |  |  |  | 61.92 | 530.15 | 0.151 | 80 | 4.64
52.56 | 277.403 | 5.8 | 1606 |  |  |  | 61.921 | 277.48 | 5.93 | 1615 |  |  |  | 61.921 | 277.303 | 5.84 | 1617 |  |  |  | 61.92 | 530.15 | 0.151 | 80 | 4.64
53.06 | 277.313 | 5.79 | 1601 |  |  |  | 61.918 | 277.419 | 5.9 | 1608 |  |  |  | 61.92 | 277.276 | 5.81 | 1608 |  |  |  | 61.92 | 526.97 | 0.15 | 79 | 4.64
53.56 | 277.313 | 5.79 | 1601 |  |  |  | 61.918 | 277.419 | 5.9 | 1608 |  |  |  | 61.92 | 277.276 | 5.81 | 1608 |  |  |  | 61.92 | 526.97 | 0.15 | 79 | 4.64
54.06 | 277.391 | 5.81 | 1607 |  |  |  | 61.92 | 277.279 | 5.91 | 1609 |  |  |  | 61.919 | 277.268 | 5.85 | 1618 |  |  |  | 61.92 | 530.43 | 0.151 | 80 | 4.64
54.56 | 277.391 | 5.81 | 1607 |  |  |  | 61.92 | 277.279 | 5.91 | 1609 |  |  |  | 61.919 | 277.268 | 5.85 | 1618 |  |  |  | 61.92 | 530.43 | 0.151 | 80 | 4.64
55.06 | 277.461 | 5.85 | 1620 |  |  |  | 61.921 | 277.528 | 5.95 | 1621 |  |  |  | 61.921 | 277.343 | 5.86 | 1622 |  |  |  | 61.92 | 533.43 | 0.146 | 78 | 4.64
55.59 | 277.461 | 5.85 | 1620 |  |  |  | 61.921 | 277.528 | 5.95 | 1621 |  |  |  | 61.921 | 277.343 | 5.86 | 1622 |  |  |  | 61.92 | 533.43 | 0.146 | 78 | 4.64
56.09 | 277.361 | 5.84 | 1616 |  |  |  | 61.921 | 277.361 | 5.95 | 1620 |  |  |  | 61.92 | 277.31 | 5.84 | 1617 |  |  |  | 61.92 | 533.38 | 0.145 | 77 | 4.64
56.58 | 277.361 | 5.84 | 1616 |  |  |  | 61.921 | 277.361 | 5.95 | 1620 |  |  |  | 61.92 | 277.31 | 5.84 | 1617 |  |  |  | 61.92 | 533.38 | 0.145 | 77 | 4.64
57.08 | 277.445 | 5.83 | 1614 |  |  |  | 61.921 | 277.507 | 5.97 | 1624 |  |  |  | 61.922 | 277.282 | 5.83 | 1615 |  |  |  | 61.92 | 533.4 | 0.151 | 81 | 4.64
57.56 | 277.445 | 5.83 | 1614 |  |  |  | 61.921 | 277.507 | 5.97 | 1624 |  |  |  | 61.922 | 277.282 | 5.83 | 1615 |  |  |  | 61.92 | 533.4 | 0.151 | 81 | 4.64
58.06 | 277.35 | 5.82 | 1611 |  |  |  | 61.921 | 277.375 | 5.94 | 1618 |  |  |  | 61.919 | 277.258 | 5.86 | 1622 |  |  |  | 61.92 | 536.62 | 0.146 | 78 | 4.64
58.6 | 277.35 | 5.82 | 1611 |  |  |  | 61.921 | 277.375 | 5.94 | 1618 |  |  |  | 61.919 | 277.258 | 5.86 | 1622 |  |  |  | 61.92 | 536.62 | 0.146 | 78 | 4.64
59.1 | 277.401 | 5.65 | 1563 |  |  |  | 61.921 | 277.265 | 5.78 | 1569 |  |  |  | 61.921 | 277.344 | 5.69 | 1577 |  |  |  | 61.921 | 539.79 | 0.151 | 81 | 4.64
59.59 | 277.335 | 5.83 | 1614 |  |  |  | 61.921 | 277.443 | 5.94 | 1619 |  |  |  | 61.921 | 277.325 | 5.86 | 1622 |  |  |  | 61.921 | 536.39 | 0.148 | 80 | 4.64
60.09 | 277.335 | 5.83 | 1614 |  |  |  | 61.921 | 277.443 | 5.94 | 1619 |  |  |  | 61.921 | 277.325 | 5.86 | 1622 |  |  |  | 61.921 | 536.39 | 0.148 | 80 | 4.64
60.57 | 277.398 | 5.84 | 1617 |  |  |  | 61.92 | 277.315 | 5.94 | 1616 |  |  |  | 61.919 | 277.295 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
61.07 | 277.398 | 5.84 | 1617 |  |  |  | 61.92 | 277.315 | 5.94 | 1616 |  |  |  | 61.919 | 277.295 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
61.56 | 277.316 | 5.85 | 1617 |  |  |  | 61.918 | 277.476 | 5.95 | 1619 |  |  |  | 61.919 | 277.269 | 5.85 | 1618 |  |  |  | 61.921 | 533.45 | 0.145 | 77 | 4.64
62.06 | 277.316 | 5.85 | 1617 |  |  |  | 61.918 | 277.476 | 5.95 | 1619 |  |  |  | 61.919 | 277.269 | 5.85 | 1618 |  |  |  | 61.921 | 533.45 | 0.145 | 77 | 4.64
62.56 | 277.389 | 5.84 | 1616 |  |  |  | 61.921 | 277.324 | 5.96 | 1621 |  |  |  | 61.92 | 277.36 | 5.85 | 1621 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 4.64
63.06 | 277.389 | 5.84 | 1616 |  |  |  | 61.921 | 277.324 | 5.96 | 1621 |  |  |  | 61.92 | 277.36 | 5.85 | 1621 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 4.64
63.56 | 277.449 | 5.81 | 1607 |  |  |  | 61.921 | 277.524 | 5.96 | 1622 |  |  |  | 61.922 | 277.342 | 5.83 | 1613 |  |  |  | 61.92 | 530.21 | 0.147 | 78 | 4.64
64.06 | 277.449 | 5.81 | 1607 |  |  |  | 61.921 | 277.524 | 5.96 | 1622 |  |  |  | 61.922 | 277.342 | 5.83 | 1613 |  |  |  | 61.92 | 530.21 | 0.147 | 78 | 4.64
64.56 | 277.368 | 5.79 | 1602 |  |  |  | 61.921 | 277.384 | 5.91 | 1607 |  |  |  | 61.92 | 277.303 | 5.82 | 1610 |  |  |  | 61.92 | 526.99 | 0.153 | 81 | 4.64
65.06 | 277.368 | 5.79 | 1602 |  |  |  | 61.921 | 277.384 | 5.91 | 1607 |  |  |  | 61.92 | 277.303 | 5.82 | 1610 |  |  |  | 61.92 | 526.99 | 0.153 | 81 | 4.64
65.56 | 277.454 | 5.81 | 1608 |  |  |  | 61.921 | 277.27 | 5.92 | 1612 |  |  |  | 61.92 | 277.268 | 5.83 | 1613 |  |  |  | 61.919 | 530.45 | 0.15 | 80 | 4.64
66.06 | 277.454 | 5.81 | 1608 |  |  |  | 61.921 | 277.27 | 5.92 | 1612 |  |  |  | 61.92 | 277.268 | 5.83 | 1613 |  |  |  | 61.919 | 530.45 | 0.15 | 80 | 4.64
66.56 | 277.361 | 5.84 | 1614 |  |  |  | 61.921 | 277.455 | 5.95 | 1620 |  |  |  | 61.92 | 277.246 | 5.86 | 1621 |  |  |  | 61.92 | 533.4 | 0.147 | 78 | 4.64
67.06 | 277.361 | 5.84 | 1614 |  |  |  | 61.921 | 277.455 | 5.95 | 1620 |  |  |  | 61.92 | 277.246 | 5.86 | 1621 |  |  |  | 61.92 | 533.4 | 0.147 | 78 | 4.64
67.56 | 277.42 | 5.84 | 1616 |  |  |  | 61.92 | 277.309 | 5.95 | 1620 |  |  |  | 61.919 | 277.355 | 5.84 | 1618 |  |  |  | 61.919 | 533.46 | 0.153 | 82 | 4.64
68.06 | 277.42 | 5.84 | 1616 |  |  |  | 61.92 | 277.309 | 5.95 | 1620 |  |  |  | 61.919 | 277.355 | 5.84 | 1618 |  |  |  | 61.919 | 533.46 | 0.153 | 82 | 4.64
68.56 | 277.34 | 5.83 | 1612 |  |  |  | 61.921 | 277.499 | 5.96 | 1622 |  |  |  | 61.923 | 277.332 | 5.85 | 1621 |  |  |  | 61.921 | 533.4 | 0.153 | 81 | 4.64
69.06 | 277.34 | 5.83 | 1612 |  |  |  | 61.921 | 277.499 | 5.96 | 1622 |  |  |  | 61.923 | 277.332 | 5.85 | 1621 |  |  |  | 61.921 | 533.4 | 0.153 | 81 | 4.64
69.56 | 277.406 | 5.82 | 1610 |  |  |  | 61.92 | 277.371 | 5.94 | 1617 |  |  |  | 61.92 | 277.298 | 5.85 | 1619 |  |  |  | 61.92 | 536.56 | 0.149 | 80 | 4.64
70.06 | 277.406 | 5.82 | 1610 |  |  |  | 61.92 | 277.371 | 5.94 | 1617 |  |  |  | 61.92 | 277.298 | 5.85 | 1619 |  |  |  | 61.92 | 536.56 | 0.149 | 80 | 4.64
70.56 | 277.33 | 5.62 | 1554 |  |  |  | 61.919 | 277.37 | 5.75 | 1563 |  |  |  | 61.919 | 277.26 | 5.66 | 1567 |  |  |  | 61.921 | 539.88 | 0.152 | 82 | 4.64
71.06 | 277.33 | 5.62 | 1554 |  |  |  | 61.919 | 277.37 | 5.75 | 1563 |  |  |  | 61.919 | 277.26 | 5.66 | 1567 |  |  |  | 61.921 | 539.88 | 0.152 | 82 | 4.64
71.56 | 277.376 | 5.86 | 1620 |  |  |  | 61.921 | 277.421 | 5.95 | 1620 |  |  |  | 61.921 | 277.351 | 5.86 | 1621 |  |  |  | 61.921 | 536.46 | 0.153 | 82 | 4.64
72.06 | 277.376 | 5.86 | 1620 |  |  |  | 61.921 | 277.421 | 5.95 | 1620 |  |  |  | 61.921 | 277.351 | 5.86 | 1621 |  |  |  | 61.921 | 536.46 | 0.153 | 82 | 4.64
72.56 | 277.439 | 5.83 | 1613 |  |  |  | 61.921 | 277.317 | 5.94 | 1617 |  |  |  | 61.919 | 277.332 | 5.84 | 1618 |  |  |  | 61.92 | 533.43 | 0.144 | 77 | 4.64
73.06 | 277.439 | 5.83 | 1613 |  |  |  | 61.921 | 277.317 | 5.94 | 1617 |  |  |  | 61.919 | 277.332 | 5.84 | 1618 |  |  |  | 61.92 | 533.43 | 0.144 | 77 | 4.64
73.56 | 277.357 | 5.82 | 1609 |  |  |  | 61.92 | 277.492 | 5.96 | 1625 |  |  |  | 61.921 | 277.303 | 5.85 | 1620 |  |  |  | 61.92 | 533.46 | 0.147 | 78 | 4.64
74.06 | 277.357 | 5.82 | 1609 |  |  |  | 61.92 | 277.492 | 5.96 | 1625 |  |  |  | 61.921 | 277.303 | 5.85 | 1620 |  |  |  | 61.92 | 533.46 | 0.147 | 78 | 4.64
74.56 | 277.439 | 5.81 | 1609 |  |  |  | 61.92 | 277.361 | 5.94 | 1617 |  |  |  | 61.921 | 277.271 | 5.86 | 1623 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
75.06 | 277.439 | 5.81 | 1609 |  |  |  | 61.92 | 277.361 | 5.94 | 1617 |  |  |  | 61.921 | 277.271 | 5.86 | 1623 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
75.56 | 277.361 | 5.81 | 1607 |  |  |  | 61.921 | 277.542 | 5.92 | 1614 |  |  |  | 61.922 | 277.245 | 5.84 | 1616 |  |  |  | 61.919 | 530.31 | 0.147 | 78 | 4.64
76.06 | 277.361 | 5.81 | 1607 |  |  |  | 61.921 | 277.542 | 5.92 | 1614 |  |  |  | 61.922 | 277.245 | 5.84 | 1616 |  |  |  | 61.919 | 530.31 | 0.147 | 78 | 4.64
76.56 | 277.414 | 5.8 | 1604 |  |  |  | 61.92 | 277.426 | 5.92 | 1610 |  |  |  | 61.921 | 277.348 | 5.81 | 1609 |  |  |  | 61.921 | 526.98 | 0.145 | 76 | 4.64
77.06 | 277.414 | 5.8 | 1604 |  |  |  | 61.92 | 277.426 | 5.92 | 1610 |  |  |  | 61.921 | 277.348 | 5.81 | 1609 |  |  |  | 61.921 | 526.98 | 0.145 | 76 | 4.64
77.56 | 277.339 | 5.81 | 1607 |  |  |  | 61.921 | 277.276 | 5.94 | 1614 |  |  |  | 61.919 | 277.328 | 5.82 | 1613 |  |  |  | 61.92 | 530.3 | 0.148 | 79 | 4.64
78.06 | 277.339 | 5.81 | 1607 |  |  |  | 61.921 | 277.276 | 5.94 | 1614 |  |  |  | 61.919 | 277.328 | 5.82 | 1613 |  |  |  | 61.92 | 530.3 | 0.148 | 79 | 4.64
78.56 | 277.406 | 5.84 | 1614 |  |  |  | 61.92 | 277.489 | 5.95 | 1620 |  |  |  | 61.92 | 277.293 | 5.86 | 1623 |  |  |  | 61.92 | 533.43 | 0.148 | 79 | 4.64
79.06 | 277.406 | 5.84 | 1614 |  |  |  | 61.92 | 277.489 | 5.95 | 1620 |  |  |  | 61.92 | 277.293 | 5.86 | 1623 |  |  |  | 61.92 | 533.43 | 0.148 | 79 | 4.64
79.56 | 277.373 | 5.83 | 1612 |  |  |  | 61.921 | 277.312 | 5.96 | 1621 |  |  |  | 61.921 | 277.257 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.151 | 80 | 4.64
80.06 | 277.373 | 5.83 | 1612 |  |  |  | 61.921 | 277.312 | 5.96 | 1621 |  |  |  | 61.921 | 277.257 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.151 | 80 | 4.64
80.56 | 277.379 | 5.84 | 1617 |  |  |  | 61.921 | 277.505 | 5.94 | 1618 |  |  |  | 61.919 | 277.344 | 5.85 | 1620 |  |  |  | 61.92 | 533.39 | 0.147 | 79 | 4.64
81.06 | 277.379 | 5.84 | 1617 |  |  |  | 61.921 | 277.505 | 5.94 | 1618 |  |  |  | 61.919 | 277.344 | 5.85 | 1620 |  |  |  | 61.92 | 533.39 | 0.147 | 79 | 4.64
81.56 | 277.454 | 5.85 | 1618 |  |  |  | 61.921 | 277.396 | 5.94 | 1616 |  |  |  | 61.92 | 277.33 | 5.84 | 1617 |  |  |  | 61.921 | 536.48 | 0.145 | 78 | 4.64
82.06 | 277.454 | 5.85 | 1618 |  |  |  | 61.921 | 277.396 | 5.94 | 1616 |  |  |  | 61.92 | 277.33 | 5.84 | 1617 |  |  |  | 61.921 | 536.48 | 0.145 | 78 | 4.64
82.56 | 277.348 | 5.65 | 1563 |  |  |  | 61.921 | 277.559 | 5.77 | 1572 |  |  |  | 61.923 | 277.293 | 5.68 | 1572 |  |  |  | 61.921 | 539.8 | 0.149 | 81 | 4.64
83.06 | 277.348 | 5.65 | 1563 |  |  |  | 61.921 | 277.559 | 5.77 | 1572 |  |  |  | 61.923 | 277.293 | 5.68 | 1572 |  |  |  | 61.921 | 539.8 | 0.149 | 81 | 4.64
83.56 | 277.427 | 5.83 | 1613 |  |  |  | 61.92 | 277.474 | 5.95 | 1620 |  |  |  | 61.92 | 277.255 | 5.87 | 1624 |  |  |  | 61.92 | 536.52 | 0.149 | 80 | 4.64
84.06 | 277.427 | 5.83 | 1613 |  |  |  | 61.92 | 277.474 | 5.95 | 1620 |  |  |  | 61.92 | 277.255 | 5.87 | 1624 |  |  |  | 61.92 | 536.52 | 0.149 | 80 | 4.64
84.56 | 277.348 | 5.82 | 1610 |  |  |  | 61.921 | 277.299 | 5.95 | 1619 |  |  |  | 61.919 | 277.368 | 5.85 | 1621 |  |  |  | 61.92 | 533.46 | 0.145 | 77 | 4.64
85.06 | 277.348 | 5.82 | 1610 |  |  |  | 61.921 | 277.299 | 5.95 | 1619 |  |  |  | 61.919 | 277.368 | 5.85 | 1621 |  |  |  | 61.92 | 533.46 | 0.145 | 77 | 4.64
85.56 | 277.402 | 5.83 | 1612 |  |  |  | 61.921 | 277.49 | 5.95 | 1619 |  |  |  | 61.918 | 277.339 | 5.85 | 1621 |  |  |  | 61.921 | 533.47 | 0.147 | 78 | 4.64
86.06 | 277.402 | 5.83 | 1612 |  |  |  | 61.921 | 277.49 | 5.95 | 1619 |  |  |  | 61.918 | 277.339 | 5.85 | 1621 |  |  |  | 61.921 | 533.47 | 0.147 | 78 | 4.64
86.56 | 277.334 | 5.83 | 1613 |  |  |  | 61.921 | 277.351 | 5.94 | 1619 |  |  |  | 61.921 | 277.322 | 5.85 | 1620 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
87.09 | 277.334 | 5.83 | 1613 |  |  |  | 61.921 | 277.351 | 5.94 | 1619 |  |  |  | 61.921 | 277.322 | 5.85 | 1620 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
87.59 | 277.4 | 5.8 | 1604 |  |  |  | 61.92 | 277.565 | 5.93 | 1616 |  |  |  | 61.922 | 277.277 | 5.85 | 1619 |  |  |  | 61.92 | 530.46 | 0.148 | 79 | 4.64
88.08 | 277.4 | 5.8 | 1604 |  |  |  | 61.92 | 277.565 | 5.93 | 1616 |  |  |  | 61.922 | 277.277 | 5.85 | 1619 |  |  |  | 61.92 | 530.46 | 0.148 | 79 | 4.64
88.58 | 277.42 | 5.79 | 1601 |  |  |  | 61.921 | 277.402 | 5.92 | 1610 |  |  |  | 61.919 | 277.232 | 5.82 | 1612 |  |  |  | 61.92 | 526.97 | 0.144 | 76 | 4.64
89.06 | 277.42 | 5.79 | 1601 |  |  |  | 61.921 | 277.402 | 5.92 | 1610 |  |  |  | 61.919 | 277.232 | 5.82 | 1612 |  |  |  | 61.92 | 526.97 | 0.144 | 76 | 4.64
89.56 | 277.381 | 5.81 | 1607 |  |  |  | 61.92 | 277.411 | 5.9 | 1608 |  |  |  | 61.92 | 277.34 | 5.83 | 1614 |  |  |  | 61.92 | 530.23 | 0.151 | 80 | 4.64
90.1 | 277.381 | 5.81 | 1607 |  |  |  | 61.92 | 277.411 | 5.9 | 1608 |  |  |  | 61.92 | 277.34 | 5.83 | 1614 |  |  |  | 61.92 | 530.23 | 0.151 | 80 | 4.64
90.6 | 277.446 | 5.83 | 1612 |  |  |  | 61.921 | 277.466 | 5.95 | 1621 |  |  |  | 61.921 | 277.318 | 5.84 | 1617 |  |  |  | 61.92 | 533.4 | 0.147 | 79 | 4.64
91.09 | 277.363 | 5.82 | 1610 |  |  |  | 61.92 | 277.334 | 5.96 | 1623 |  |  |  | 61.92 | 277.293 | 5.84 | 1618 |  |  |  | 61.919 | 533.4 | 0.145 | 77 | 4.64
91.59 | 277.363 | 5.82 | 1610 |  |  |  | 61.92 | 277.334 | 5.96 | 1623 |  |  |  | 61.92 | 277.293 | 5.84 | 1618 |  |  |  | 61.919 | 533.4 | 0.145 | 77 | 4.64
92.08 | 277.421 | 5.82 | 1611 |  |  |  | 61.92 | 277.516 | 5.94 | 1617 |  |  |  | 61.919 | 277.249 | 5.86 | 1623 |  |  |  | 61.92 | 533.36 | 0.144 | 77 | 4.64
92.58 | 277.421 | 5.82 | 1611 |  |  |  | 61.92 | 277.516 | 5.94 | 1617 |  |  |  | 61.919 | 277.249 | 5.86 | 1623 |  |  |  | 61.92 | 533.36 | 0.144 | 77 | 4.64
93.06 | 277.357 | 5.83 | 1611 |  |  |  | 61.921 | 277.34 | 5.95 | 1618 |  |  |  | 61.92 | 277.326 | 5.86 | 1624 |  |  |  | 61.921 | 536.39 | 0.147 | 79 | 4.64
93.56 | 277.357 | 5.83 | 1611 |  |  |  | 61.921 | 277.34 | 5.95 | 1618 |  |  |  | 61.92 | 277.326 | 5.86 | 1624 |  |  |  | 61.921 | 536.39 | 0.147 | 79 | 4.64
94.06 | 277.397 | 5.65 | 1563 |  |  |  | 61.92 | 277.553 | 5.78 | 1572 |  |  |  | 61.922 | 277.294 | 5.66 | 1567 |  |  |  | 61.92 | 539.83 | 0.146 | 79 | 4.64
94.56 | 277.397 | 5.65 | 1563 |  |  |  | 61.92 | 277.553 | 5.78 | 1572 |  |  |  | 61.922 | 277.294 | 5.66 | 1567 |  |  |  | 61.92 | 539.83 | 0.146 | 79 | 4.64
95.06 | 277.331 | 5.84 | 1615 |  |  |  | 61.921 | 277.382 | 5.96 | 1623 |  |  |  | 61.92 | 277.292 | 5.85 | 1619 |  |  |  | 61.921 | 536.59 | 0.15 | 80 | 4.64
95.56 | 277.331 | 5.84 | 1615 |  |  |  | 61.921 | 277.382 | 5.96 | 1623 |  |  |  | 61.92 | 277.292 | 5.85 | 1619 |  |  |  | 61.921 | 536.59 | 0.15 | 80 | 4.64
96.06 | 277.411 | 5.81 | 1609 |  |  |  | 61.92 | 277.311 | 5.95 | 1621 |  |  |  | 61.92 | 277.259 | 5.86 | 1621 |  |  |  | 61.92 | 533.41 | 0.151 | 80 | 4.64
96.56 | 277.411 | 5.81 | 1609 |  |  |  | 61.92 | 277.311 | 5.95 | 1621 |  |  |  | 61.92 | 277.259 | 5.86 | 1621 |  |  |  | 61.92 | 533.41 | 0.151 | 80 | 4.64
97.06 | 277.442 | 5.83 | 1613 |  |  |  | 61.921 | 277.435 | 5.94 | 1618 |  |  |  | 61.921 | 277.325 | 5.87 | 1625 |  |  |  | 61.923 | 533.45 | 0.148 | 79 | 4.64
97.56 | 277.442 | 5.83 | 1613 |  |  |  | 61.921 | 277.435 | 5.94 | 1618 |  |  |  | 61.921 | 277.325 | 5.87 | 1625 |  |  |  | 61.923 | 533.45 | 0.148 | 79 | 4.64
98.06 | 277.422 | 5.83 | 1614 |  |  |  | 61.921 | 277.305 | 5.93 | 1617 |  |  |  | 61.919 | 277.306 | 5.86 | 1621 |  |  |  | 61.92 | 533.42 | 0.151 | 80 | 4.64
98.56 | 277.422 | 5.83 | 1614 |  |  |  | 61.921 | 277.305 | 5.93 | 1617 |  |  |  | 61.919 | 277.306 | 5.86 | 1621 |  |  |  | 61.92 | 533.42 | 0.151 | 80 | 4.64
99.06 | 277.477 | 5.81 | 1606 |  |  |  | 61.921 | 277.516 | 5.93 | 1616 |  |  |  | 61.919 | 277.283 | 5.82 | 1612 |  |  |  | 61.92 | 530.49 | 0.151 | 80 | 4.64
99.56 | 277.477 | 5.81 | 1606 |  |  |  | 61.921 | 277.516 | 5.93 | 1616 |  |  |  | 61.919 | 277.283 | 5.82 | 1612 |  |  |  | 61.92 | 530.49 | 0.151 | 80 | 4.64
100.06 | 277.382 | 5.77 | 1597 |  |  |  | 61.92 | 277.374 | 5.9 | 1607 |  |  |  | 61.92 | 277.265 | 5.81 | 1608 |  |  |  | 61.921 | 526.98 | 0.151 | 80 | 4.64
100.56 | 277.382 | 5.77 | 1597 |  |  |  | 61.92 | 277.374 | 5.9 | 1607 |  |  |  | 61.92 | 277.265 | 5.81 | 1608 |  |  |  | 61.921 | 526.98 | 0.151 | 80 | 4.64
101.06 | 277.449 | 5.8 | 1604 |  |  |  | 61.921 | 277.521 | 5.9 | 1609 |  |  |  | 61.922 | 277.228 | 5.85 | 1618 |  |  |  | 61.92 | 530.24 | 0.151 | 80 | 4.64
101.56 | 277.449 | 5.8 | 1604 |  |  |  | 61.921 | 277.521 | 5.9 | 1609 |  |  |  | 61.922 | 277.228 | 5.85 | 1618 |  |  |  | 61.92 | 530.24 | 0.151 | 80 | 4.64
102.06 | 277.364 | 5.84 | 1616 |  |  |  | 61.921 | 277.389 | 5.95 | 1619 |  |  |  | 61.92 | 277.326 | 5.87 | 1626 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
102.56 | 277.364 | 5.84 | 1616 |  |  |  | 61.921 | 277.389 | 5.95 | 1619 |  |  |  | 61.92 | 277.326 | 5.87 | 1626 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
103.06 | 277.436 | 5.84 | 1615 |  |  |  | 61.92 | 277.272 | 5.94 | 1617 |  |  |  | 61.92 | 277.299 | 5.84 | 1617 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 4.64
103.56 | 277.436 | 5.84 | 1615 |  |  |  | 61.92 | 277.272 | 5.94 | 1617 |  |  |  | 61.92 | 277.299 | 5.84 | 1617 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 4.64
104.06 | 277.339 | 5.83 | 1612 |  |  |  | 61.921 | 277.407 | 5.94 | 1617 |  |  |  | 61.92 | 277.276 | 5.86 | 1622 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 4.64
104.56 | 277.339 | 5.83 | 1612 |  |  |  | 61.921 | 277.407 | 5.94 | 1617 |  |  |  | 61.92 | 277.276 | 5.86 | 1622 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 4.64
105.06 | 277.424 | 5.81 | 1608 |  |  |  | 61.919 | 277.281 | 5.95 | 1622 |  |  |  | 61.919 | 277.247 | 5.86 | 1623 |  |  |  | 61.919 | 536.36 | 0.153 | 82 | 4.64
105.56 | 277.424 | 5.81 | 1608 |  |  |  | 61.919 | 277.281 | 5.95 | 1622 |  |  |  | 61.919 | 277.247 | 5.86 | 1623 |  |  |  | 61.919 | 536.36 | 0.153 | 82 | 4.64
106.06 | 277.471 | 5.66 | 1566 |  |  |  | 61.921 | 277.465 | 5.78 | 1573 |  |  |  | 61.92 | 277.338 | 5.69 | 1575 |  |  |  | 61.921 | 539.8 | 0.148 | 80 | 4.64
106.56 | 277.471 | 5.66 | 1566 |  |  |  | 61.921 | 277.465 | 5.78 | 1573 |  |  |  | 61.92 | 277.338 | 5.69 | 1575 |  |  |  | 61.921 | 539.8 | 0.148 | 80 | 4.64
107.06 | 277.399 | 5.84 | 1616 |  |  |  | 61.92 | 277.368 | 5.95 | 1622 |  |  |  | 61.92 | 277.307 | 5.86 | 1623 |  |  |  | 61.92 | 536.66 | 0.15 | 81 | 4.64
107.56 | 277.399 | 5.84 | 1616 |  |  |  | 61.92 | 277.368 | 5.95 | 1622 |  |  |  | 61.92 | 277.307 | 5.86 | 1623 |  |  |  | 61.92 | 536.66 | 0.15 | 81 | 4.64
108.06 | 277.473 | 5.82 | 1612 |  |  |  | 61.92 | 277.461 | 5.95 | 1622 |  |  |  | 61.92 | 277.27 | 5.86 | 1623 |  |  |  | 61.92 | 533.45 | 0.15 | 80 | 4.64
108.56 | 277.473 | 5.82 | 1612 |  |  |  | 61.92 | 277.461 | 5.95 | 1622 |  |  |  | 61.92 | 277.27 | 5.86 | 1623 |  |  |  | 61.92 | 533.45 | 0.15 | 80 | 4.64
109.06 | 277.383 | 5.83 | 1614 |  |  |  | 61.921 | 277.397 | 5.95 | 1618 |  |  |  | 61.92 | 277.242 | 5.86 | 1622 |  |  |  | 61.921 | 533.43 | 0.152 | 81 | 4.64
109.56 | 277.383 | 5.83 | 1614 |  |  |  | 61.921 | 277.397 | 5.95 | 1618 |  |  |  | 61.92 | 277.242 | 5.86 | 1622 |  |  |  | 61.921 | 533.43 | 0.152 | 81 | 4.64
110.06 | 277.446 | 5.83 | 1614 |  |  |  | 61.92 | 277.244 | 5.96 | 1621 |  |  |  | 61.92 | 277.351 | 5.85 | 1619 |  |  |  | 61.923 | 533.46 | 0.152 | 81 | 4.64
110.56 | 277.446 | 5.83 | 1614 |  |  |  | 61.92 | 277.244 | 5.96 | 1621 |  |  |  | 61.92 | 277.351 | 5.85 | 1619 |  |  |  | 61.923 | 533.46 | 0.152 | 81 | 4.64
111.06 | 277.377 | 5.82 | 1609 |  |  |  | 61.921 | 277.464 | 5.92 | 1613 |  |  |  | 61.921 | 277.326 | 5.85 | 1621 |  |  |  | 61.921 | 530.54 | 0.152 | 81 | 4.64
111.56 | 277.377 | 5.82 | 1609 |  |  |  | 61.921 | 277.464 | 5.92 | 1613 |  |  |  | 61.921 | 277.326 | 5.85 | 1621 |  |  |  | 61.921 | 530.54 | 0.152 | 81 | 4.64
112.06 | 277.438 | 5.79 | 1602 |  |  |  | 61.921 | 277.291 | 5.92 | 1611 |  |  |  | 61.919 | 277.29 | 5.82 | 1612 |  |  |  | 61.921 | 526.98 | 0.15 | 79 | 4.64
112.56 | 277.438 | 5.79 | 1602 |  |  |  | 61.921 | 277.291 | 5.92 | 1611 |  |  |  | 61.919 | 277.29 | 5.82 | 1612 |  |  |  | 61.921 | 526.98 | 0.15 | 79 | 4.64
113.06 | 277.351 | 5.81 | 1609 |  |  |  | 61.921 | 277.492 | 5.91 | 1610 |  |  |  | 61.922 | 277.259 | 5.83 | 1613 |  |  |  | 61.92 | 530.18 | 0.15 | 80 | 4.64
113.56 | 277.351 | 5.81 | 1609 |  |  |  | 61.921 | 277.492 | 5.91 | 1610 |  |  |  | 61.922 | 277.259 | 5.83 | 1613 |  |  |  | 61.92 | 530.18 | 0.15 | 80 | 4.64
114.06 | 277.428 | 5.82 | 1612 |  |  |  | 61.92 | 277.378 | 5.93 | 1615 |  |  |  | 61.92 | 277.233 | 5.85 | 1620 |  |  |  | 61.921 | 533.44 | 0.152 | 81 | 4.64
114.56 | 277.428 | 5.82 | 1612 |  |  |  | 61.92 | 277.378 | 5.93 | 1615 |  |  |  | 61.92 | 277.233 | 5.85 | 1620 |  |  |  | 61.921 | 533.44 | 0.152 | 81 | 4.64
115.06 | 277.486 | 5.83 | 1615 |  |  |  | 61.92 | 277.494 | 5.94 | 1617 |  |  |  | 61.92 | 277.327 | 5.85 | 1619 |  |  |  | 61.92 | 533.47 | 0.154 | 82 | 4.64
115.56 | 277.486 | 5.83 | 1615 |  |  |  | 61.92 | 277.494 | 5.94 | 1617 |  |  |  | 61.92 | 277.327 | 5.85 | 1619 |  |  |  | 61.92 | 533.47 | 0.154 | 82 | 4.64
116.06 | 277.393 | 5.82 | 1609 |  |  |  | 61.92 | 277.443 | 5.96 | 1621 |  |  |  | 61.92 | 277.297 | 5.85 | 1620 |  |  |  | 61.921 | 533.44 | 0.152 | 81 | 4.64
116.56 | 277.393 | 5.82 | 1609 |  |  |  | 61.92 | 277.443 | 5.96 | 1621 |  |  |  | 61.92 | 277.297 | 5.85 | 1620 |  |  |  | 61.921 | 533.44 | 0.152 | 81 | 4.64
117.06 | 277.467 | 5.81 | 1609 |  |  |  | 61.921 | 277.302 | 5.96 | 1621 |  |  |  | 61.92 | 277.264 | 5.85 | 1620 |  |  |  | 61.919 | 536.31 | 0.15 | 80 | 4.64
117.56 | 277.467 | 5.81 | 1609 |  |  |  | 61.921 | 277.302 | 5.96 | 1621 |  |  |  | 61.92 | 277.264 | 5.85 | 1620 |  |  |  | 61.919 | 536.31 | 0.15 | 80 | 4.64
118.06 | 277.353 | 5.65 | 1562 |  |  |  | 61.921 | 277.52 | 5.76 | 1567 |  |  |  | 61.919 | 277.231 | 5.67 | 1570 |  |  |  | 61.92 | 539.83 | 0.152 | 82 | 4.64
118.56 | 277.353 | 5.65 | 1562 |  |  |  | 61.921 | 277.52 | 5.76 | 1567 |  |  |  | 61.919 | 277.231 | 5.67 | 1570 |  |  |  | 61.92 | 539.83 | 0.152 | 82 | 4.64
119.06 | 277.415 | 5.84 | 1617 |  |  |  | 61.92 | 277.35 | 5.96 | 1624 |  |  |  | 61.919 | 277.341 | 5.87 | 1626 |  |  |  | 61.92 | 536.6 | 0.148 | 80 | 4.64
119.6 | 277.415 | 5.84 | 1617 |  |  |  | 61.92 | 277.35 | 5.96 | 1624 |  |  |  | 61.919 | 277.341 | 5.87 | 1626 |  |  |  | 61.92 | 536.6 | 0.148 | 80 | 4.64
120.1 | 277.344 | 5.84 | 1615 |  |  |  | 61.92 | 277.58 | 5.94 | 1618 |  |  |  | 61.922 | 277.309 | 5.84 | 1618 |  |  |  | 61.92 | 533.45 | 0.149 | 80 | 4.64
120.58 | 277.344 | 5.84 | 1615 |  |  |  | 61.92 | 277.58 | 5.94 | 1618 |  |  |  | 61.922 | 277.309 | 5.84 | 1618 |  |  |  | 61.92 | 533.45 | 0.149 | 80 | 4.64
121.08 | 277.41 | 5.83 | 1613 |  |  |  | 61.92 | 277.416 | 5.98 | 1628 |  |  |  | 61.92 | 277.268 | 5.86 | 1622 |  |  |  | 61.921 | 533.42 | 0.15 | 80 | 4.64
121.57 | 277.41 | 5.83 | 1613 |  |  |  | 61.92 | 277.416 | 5.98 | 1628 |  |  |  | 61.92 | 277.268 | 5.86 | 1622 |  |  |  | 61.921 | 533.42 | 0.15 | 80 | 4.64
122.07 | 277.322 | 5.82 | 1610 |  |  |  | 61.921 | 277.394 | 5.96 | 1621 |  |  |  | 61.919 | 277.242 | 5.86 | 1623 |  |  |  | 61.921 | 533.37 | 0.148 | 79 | 4.64
122.56 | 277.322 | 5.82 | 1610 |  |  |  | 61.921 | 277.394 | 5.96 | 1621 |  |  |  | 61.919 | 277.242 | 5.86 | 1623 |  |  |  | 61.921 | 533.37 | 0.148 | 79 | 4.64
123.06 | 277.4 | 5.81 | 1607 |  |  |  | 61.921 | 277.491 | 5.94 | 1617 |  |  |  | 61.92 | 277.339 | 5.83 | 1615 |  |  |  | 61.921 | 530.47 | 0.154 | 82 | 4.64
123.59 | 277.456 | 5.79 | 1603 |  |  |  | 61.92 | 277.359 | 5.91 | 1609 |  |  |  | 61.92 | 277.316 | 5.82 | 1611 |  |  |  | 61.92 | 526.97 | 0.15 | 79 | 4.64
124.09 | 277.456 | 5.79 | 1603 |  |  |  | 61.92 | 277.359 | 5.91 | 1609 |  |  |  | 61.92 | 277.316 | 5.82 | 1611 |  |  |  | 61.92 | 526.97 | 0.15 | 79 | 4.64
124.57 | 277.371 | 5.81 | 1607 |  |  |  | 61.921 | 277.56 | 5.92 | 1612 |  |  |  | 61.921 | 277.282 | 5.82 | 1612 |  |  |  | 61.92 | 530.12 | 0.146 | 77 | 4.64
125.07 | 277.371 | 5.81 | 1607 |  |  |  | 61.921 | 277.56 | 5.92 | 1612 |  |  |  | 61.921 | 277.282 | 5.82 | 1612 |  |  |  | 61.92 | 530.12 | 0.146 | 77 | 4.64
125.56 | 277.436 | 5.84 | 1616 |  |  |  | 61.92 | 277.379 | 5.95 | 1618 |  |  |  | 61.919 | 277.237 | 5.84 | 1617 |  |  |  | 61.921 | 533.39 | 0.151 | 81 | 4.64
126.06 | 277.436 | 5.84 | 1616 |  |  |  | 61.92 | 277.379 | 5.95 | 1618 |  |  |  | 61.919 | 277.237 | 5.84 | 1617 |  |  |  | 61.921 | 533.39 | 0.151 | 81 | 4.64
126.56 | 277.363 | 5.83 | 1614 |  |  |  | 61.921 | 277.573 | 5.94 | 1618 |  |  |  | 61.922 | 277.215 | 5.85 | 1620 |  |  |  | 61.919 | 533.47 | 0.154 | 82 | 4.64
127.06 | 277.363 | 5.83 | 1614 |  |  |  | 61.921 | 277.573 | 5.94 | 1618 |  |  |  | 61.922 | 277.215 | 5.85 | 1620 |  |  |  | 61.919 | 533.47 | 0.154 | 82 | 4.64
127.56 | 277.421 | 5.81 | 1608 |  |  |  | 61.921 | 277.425 | 5.95 | 1621 |  |  |  | 61.92 | 277.32 | 5.85 | 1621 |  |  |  | 61.921 | 533.47 | 0.146 | 78 | 4.64
128.06 | 277.421 | 5.81 | 1608 |  |  |  | 61.921 | 277.425 | 5.95 | 1621 |  |  |  | 61.92 | 277.32 | 5.85 | 1621 |  |  |  | 61.921 | 533.47 | 0.146 | 78 | 4.64
128.56 | 277.343 | 5.83 | 1613 |  |  |  | 61.921 | 277.322 | 5.94 | 1618 |  |  |  | 61.92 | 277.301 | 5.86 | 1623 |  |  |  | 61.919 | 536.28 | 0.15 | 81 | 4.64
129.06 | 277.343 | 5.83 | 1613 |  |  |  | 61.921 | 277.322 | 5.94 | 1618 |  |  |  | 61.92 | 277.301 | 5.86 | 1623 |  |  |  | 61.919 | 536.28 | 0.15 | 81 | 4.64
129.56 | 277.408 | 5.63 | 1557 |  |  |  | 61.921 | 277.503 | 5.74 | 1564 |  |  |  | 61.919 | 277.255 | 5.66 | 1565 |  |  |  | 61.92 | 539.89 | 0.15 | 81 | 4.64
130.06 | 277.408 | 5.63 | 1557 |  |  |  | 61.921 | 277.503 | 5.74 | 1564 |  |  |  | 61.919 | 277.255 | 5.66 | 1565 |  |  |  | 61.92 | 539.89 | 0.15 | 81 | 4.64
130.56 | 277.317 | 5.84 | 1616 |  |  |  | 61.92 | 277.376 | 5.95 | 1620 |  |  |  | 61.919 | 277.231 | 5.86 | 1623 |  |  |  | 61.92 | 536.69 | 0.152 | 81 | 4.64
131.06 | 277.317 | 5.84 | 1616 |  |  |  | 61.92 | 277.376 | 5.95 | 1620 |  |  |  | 61.919 | 277.231 | 5.86 | 1623 |  |  |  | 61.92 | 536.69 | 0.152 | 81 | 4.64
131.56 | 277.39 | 5.82 | 1610 |  |  |  | 61.92 | 277.551 | 5.94 | 1619 |  |  |  | 61.922 | 277.313 | 5.86 | 1623 |  |  |  | 61.92 | 533.44 | 0.15 | 80 | 4.64
132.06 | 277.39 | 5.82 | 1610 |  |  |  | 61.92 | 277.551 | 5.94 | 1619 |  |  |  | 61.922 | 277.313 | 5.86 | 1623 |  |  |  | 61.92 | 533.44 | 0.15 | 80 | 4.64
132.56 | 277.458 | 5.82 | 1610 |  |  |  | 61.921 | 277.404 | 5.95 | 1620 |  |  |  | 61.92 | 277.296 | 5.86 | 1624 |  |  |  | 61.92 | 533.42 | 0.151 | 81 | 4.64
133.06 | 277.458 | 5.82 | 1610 |  |  |  | 61.921 | 277.404 | 5.95 | 1620 |  |  |  | 61.92 | 277.296 | 5.86 | 1624 |  |  |  | 61.92 | 533.42 | 0.151 | 81 | 4.64
133.56 | 277.366 | 5.81 | 1608 |  |  |  | 61.921 | 277.523 | 5.95 | 1620 |  |  |  | 61.922 | 277.259 | 5.86 | 1621 |  |  |  | 61.92 | 533.39 | 0.154 | 82 | 4.64
134.06 | 277.366 | 5.81 | 1608 |  |  |  | 61.921 | 277.523 | 5.95 | 1620 |  |  |  | 61.922 | 277.259 | 5.86 | 1621 |  |  |  | 61.92 | 533.39 | 0.154 | 82 | 4.64
134.56 | 277.44 | 5.82 | 1612 |  |  |  | 61.921 | 277.445 | 5.93 | 1616 |  |  |  | 61.918 | 277.222 | 5.83 | 1614 |  |  |  | 61.921 | 530.54 | 0.153 | 81 | 4.64
135.06 | 277.44 | 5.82 | 1612 |  |  |  | 61.921 | 277.445 | 5.93 | 1616 |  |  |  | 61.918 | 277.222 | 5.83 | 1614 |  |  |  | 61.921 | 530.54 | 0.153 | 81 | 4.64
135.56 | 277.356 | 5.8 | 1604 |  |  |  | 61.921 | 277.299 | 5.91 | 1609 |  |  |  | 61.92 | 277.332 | 5.8 | 1607 |  |  |  | 61.921 | 526.93 | 0.149 | 79 | 4.64
136.06 | 277.356 | 5.8 | 1604 |  |  |  | 61.921 | 277.299 | 5.91 | 1609 |  |  |  | 61.92 | 277.332 | 5.8 | 1607 |  |  |  | 61.921 | 526.93 | 0.149 | 79 | 4.64
136.56 | 277.42 | 5.8 | 1605 |  |  |  | 61.921 | 277.431 | 5.93 | 1614 |  |  |  | 61.92 | 277.311 | 5.82 | 1611 |  |  |  | 61.92 | 530.1 | 0.153 | 81 | 4.64
137.06 | 277.42 | 5.8 | 1605 |  |  |  | 61.921 | 277.431 | 5.93 | 1614 |  |  |  | 61.92 | 277.311 | 5.82 | 1611 |  |  |  | 61.92 | 530.1 | 0.153 | 81 | 4.64
137.56 | 277.346 | 5.82 | 1611 |  |  |  | 61.92 | 277.329 | 5.95 | 1620 |  |  |  | 61.92 | 277.289 | 5.86 | 1623 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
138.06 | 277.346 | 5.82 | 1611 |  |  |  | 61.92 | 277.329 | 5.95 | 1620 |  |  |  | 61.92 | 277.289 | 5.86 | 1623 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
138.56 | 277.416 | 5.84 | 1616 |  |  |  | 61.92 | 277.498 | 5.95 | 1620 |  |  |  | 61.923 | 277.243 | 5.86 | 1621 |  |  |  | 61.92 | 533.38 | 0.149 | 79 | 4.64
139.06 | 277.416 | 5.84 | 1616 |  |  |  | 61.92 | 277.498 | 5.95 | 1620 |  |  |  | 61.923 | 277.243 | 5.86 | 1621 |  |  |  | 61.92 | 533.38 | 0.149 | 79 | 4.64
139.56 | 277.341 | 5.84 | 1616 |  |  |  | 61.917 | 277.36 | 5.94 | 1617 |  |  |  | 61.92 | 277.243 | 5.85 | 1619 |  |  |  | 61.92 | 533.44 | 0.149 | 79 | 4.64
140.06 | 277.341 | 5.84 | 1616 |  |  |  | 61.917 | 277.36 | 5.94 | 1617 |  |  |  | 61.92 | 277.243 | 5.85 | 1619 |  |  |  | 61.92 | 533.44 | 0.149 | 79 | 4.64
140.56 | 277.411 | 5.82 | 1610 |  |  |  | 61.92 | 277.35 | 5.95 | 1621 |  |  |  | 61.92 | 277.311 | 5.84 | 1618 |  |  |  | 61.92 | 536.16 | 0.149 | 80 | 4.64
141.06 | 277.411 | 5.82 | 1610 |  |  |  | 61.92 | 277.35 | 5.95 | 1621 |  |  |  | 61.92 | 277.311 | 5.84 | 1618 |  |  |  | 61.92 | 536.16 | 0.149 | 80 | 4.64
141.56 | 277.47 | 5.63 | 1557 |  |  |  | 61.921 | 277.432 | 5.76 | 1567 |  |  |  | 61.92 | 277.285 | 5.68 | 1573 |  |  |  | 61.921 | 539.86 | 0.15 | 81 | 4.64
142.06 | 277.47 | 5.63 | 1557 |  |  |  | 61.921 | 277.432 | 5.76 | 1567 |  |  |  | 61.92 | 277.285 | 5.68 | 1573 |  |  |  | 61.921 | 539.86 | 0.15 | 81 | 4.64
142.56 | 277.396 | 5.84 | 1617 |  |  |  | 61.92 | 277.267 | 5.94 | 1616 |  |  |  | 61.92 | 277.259 | 5.87 | 1625 |  |  |  | 61.919 | 536.7 | 0.15 | 81 | 4.64
143.06 | 277.396 | 5.84 | 1617 |  |  |  | 61.92 | 277.267 | 5.94 | 1616 |  |  |  | 61.92 | 277.259 | 5.87 | 1625 |  |  |  | 61.919 | 536.7 | 0.15 | 81 | 4.64
143.56 | 277.45 | 5.82 | 1610 |  |  |  | 61.921 | 277.489 | 5.96 | 1624 |  |  |  | 61.919 | 277.215 | 5.85 | 1618 |  |  |  | 61.921 | 533.39 | 0.154 | 82 | 4.64
144.06 | 277.45 | 5.82 | 1610 |  |  |  | 61.921 | 277.489 | 5.96 | 1624 |  |  |  | 61.919 | 277.215 | 5.85 | 1618 |  |  |  | 61.921 | 533.39 | 0.154 | 82 | 4.64
144.56 | 277.395 | 5.84 | 1615 |  |  |  | 61.921 | 277.315 | 5.96 | 1621 |  |  |  | 61.919 | 277.325 | 5.85 | 1619 |  |  |  | 61.92 | 533.41 | 0.15 | 80 | 4.64
145.06 | 277.395 | 5.84 | 1615 |  |  |  | 61.921 | 277.315 | 5.96 | 1621 |  |  |  | 61.919 | 277.325 | 5.85 | 1619 |  |  |  | 61.92 | 533.41 | 0.15 | 80 | 4.64
145.56 | 277.443 | 5.82 | 1611 |  |  |  | 61.921 | 277.504 | 5.97 | 1625 |  |  |  | 61.923 | 277.308 | 5.86 | 1623 |  |  |  | 61.92 | 533.42 | 0.151 | 80 | 4.64
146.06 | 277.443 | 5.82 | 1611 |  |  |  | 61.921 | 277.504 | 5.97 | 1625 |  |  |  | 61.923 | 277.308 | 5.86 | 1623 |  |  |  | 61.92 | 533.42 | 0.151 | 80 | 4.64
146.56 | 277.371 | 5.82 | 1610 |  |  |  | 61.921 | 277.366 | 5.95 | 1618 |  |  |  | 61.92 | 277.286 | 5.85 | 1619 |  |  |  | 61.919 | 530.6 | 0.151 | 80 | 4.64
147.06 | 277.371 | 5.82 | 1610 |  |  |  | 61.921 | 277.366 | 5.95 | 1618 |  |  |  | 61.92 | 277.286 | 5.85 | 1619 |  |  |  | 61.919 | 530.6 | 0.151 | 80 | 4.64
147.56 | 277.455 | 5.8 | 1606 |  |  |  | 61.921 | 277.248 | 5.91 | 1608 |  |  |  | 61.919 | 277.244 | 5.83 | 1614 |  |  |  | 61.921 | 527 | 0.151 | 79 | 4.64
148.06 | 277.455 | 5.8 | 1606 |  |  |  | 61.921 | 277.248 | 5.91 | 1608 |  |  |  | 61.919 | 277.244 | 5.83 | 1614 |  |  |  | 61.921 | 527 | 0.151 | 79 | 4.64
148.56 | 277.346 | 5.81 | 1607 |  |  |  | 61.918 | 277.457 | 5.94 | 1616 |  |  |  | 61.921 | 277.331 | 5.81 | 1610 |  |  |  | 61.92 | 529.97 | 0.151 | 80 | 4.64
149.06 | 277.346 | 5.81 | 1607 |  |  |  | 61.918 | 277.457 | 5.94 | 1616 |  |  |  | 61.921 | 277.331 | 5.81 | 1610 |  |  |  | 61.92 | 529.97 | 0.151 | 80 | 4.64
149.56 | 277.42 | 5.82 | 1611 |  |  |  | 61.92 | 277.301 | 5.96 | 1621 |  |  |  | 61.919 | 277.299 | 5.85 | 1618 |  |  |  | 61.921 | 533.44 | 0.152 | 81 | 4.64
150.06 | 277.42 | 5.82 | 1611 |  |  |  | 61.92 | 277.301 | 5.96 | 1621 |  |  |  | 61.919 | 277.299 | 5.85 | 1618 |  |  |  | 61.921 | 533.44 | 0.152 | 81 | 4.64
150.56 | 277.485 | 5.83 | 1613 |  |  |  | 61.92 | 277.494 | 5.93 | 1617 |  |  |  | 61.921 | 277.278 | 5.87 | 1626 |  |  |  | 61.92 | 533.43 | 0.148 | 79 | 4.64
151.06 | 277.485 | 5.83 | 1613 |  |  |  | 61.92 | 277.494 | 5.93 | 1617 |  |  |  | 61.921 | 277.278 | 5.87 | 1626 |  |  |  | 61.92 | 533.43 | 0.148 | 79 | 4.64
151.56 | 277.397 | 5.83 | 1614 |  |  |  | 61.92 | 277.329 | 5.94 | 1617 |  |  |  | 61.92 | 277.249 | 5.85 | 1618 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 4.64
152.08 | 277.397 | 5.83 | 1614 |  |  |  | 61.92 | 277.329 | 5.94 | 1617 |  |  |  | 61.92 | 277.249 | 5.85 | 1618 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 4.64
152.58 | 277.466 | 5.85 | 1617 |  |  |  | 61.921 | 277.517 | 5.94 | 1619 |  |  |  | 61.923 | 277.349 | 5.85 | 1619 |  |  |  | 61.923 | 536.2 | 0.151 | 81 | 4.64
153.07 | 277.466 | 5.85 | 1617 |  |  |  | 61.921 | 277.517 | 5.94 | 1619 |  |  |  | 61.923 | 277.349 | 5.85 | 1619 |  |  |  | 61.923 | 536.2 | 0.151 | 81 | 4.64
153.57 | 277.379 | 5.66 | 1564 |  |  |  | 61.921 | 277.447 | 5.77 | 1571 |  |  |  | 61.921 | 277.311 | 5.68 | 1572 |  |  |  | 61.92 | 539.82 | 0.155 | 84 | 4.64
154.06 | 277.379 | 5.66 | 1564 |  |  |  | 61.921 | 277.447 | 5.77 | 1571 |  |  |  | 61.921 | 277.311 | 5.68 | 1572 |  |  |  | 61.92 | 539.82 | 0.155 | 84 | 4.64
154.56 | 277.444 | 5.83 | 1612 |  |  |  | 61.921 | 277.321 | 5.96 | 1624 |  |  |  | 61.919 | 277.296 | 5.86 | 1622 |  |  |  | 61.92 | 536.84 | 0.155 | 83 | 4.64
155.09 | 277.36 | 5.84 | 1613 |  |  |  | 61.921 | 277.492 | 5.95 | 1620 |  |  |  | 61.92 | 277.264 | 5.85 | 1621 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 4.64
155.59 | 277.36 | 5.84 | 1613 |  |  |  | 61.921 | 277.492 | 5.95 | 1620 |  |  |  | 61.92 | 277.264 | 5.85 | 1621 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 4.64
156.07 | 277.432 | 5.84 | 1616 |  |  |  | 61.921 | 277.315 | 5.95 | 1623 |  |  |  | 61.921 | 277.231 | 5.87 | 1626 |  |  |  | 61.92 | 533.47 | 0.15 | 80 | 4.64
156.57 | 277.432 | 5.84 | 1616 |  |  |  | 61.921 | 277.315 | 5.95 | 1623 |  |  |  | 61.921 | 277.231 | 5.87 | 1626 |  |  |  | 61.92 | 533.47 | 0.15 | 80 | 4.64
157.06 | 277.309 | 5.84 | 1615 |  |  |  | 61.918 | 277.533 | 5.93 | 1616 |  |  |  | 61.922 | 277.324 | 5.84 | 1618 |  |  |  | 61.92 | 533.46 | 0.152 | 81 | 4.64
157.56 | 277.309 | 5.84 | 1615 |  |  |  | 61.918 | 277.533 | 5.93 | 1616 |  |  |  | 61.922 | 277.324 | 5.84 | 1618 |  |  |  | 61.92 | 533.46 | 0.152 | 81 | 4.64
158.06 | 277.375 | 5.83 | 1611 |  |  |  | 61.92 | 277.401 | 5.94 | 1619 |  |  |  | 61.919 | 277.283 | 5.84 | 1617 |  |  |  | 61.92 | 530.71 | 0.15 | 80 | 4.64
158.56 | 277.375 | 5.83 | 1611 |  |  |  | 61.92 | 277.401 | 5.94 | 1619 |  |  |  | 61.919 | 277.283 | 5.84 | 1617 |  |  |  | 61.92 | 530.71 | 0.15 | 80 | 4.64
159.06 | 277.45 | 5.79 | 1601 |  |  |  | 61.921 | 277.392 | 5.91 | 1609 |  |  |  | 61.92 | 277.256 | 5.8 | 1605 |  |  |  | 61.92 | 526.96 | 0.153 | 81 | 4.64
159.56 | 277.45 | 5.79 | 1601 |  |  |  | 61.921 | 277.392 | 5.91 | 1609 |  |  |  | 61.92 | 277.256 | 5.8 | 1605 |  |  |  | 61.92 | 526.96 | 0.153 | 81 | 4.64
160.06 | 277.381 | 5.82 | 1609 |  |  |  | 61.919 | 277.43 | 5.91 | 1610 |  |  |  | 61.92 | 277.227 | 5.82 | 1611 |  |  |  | 61.921 | 529.94 | 0.148 | 79 | 4.64
160.56 | 277.381 | 5.82 | 1609 |  |  |  | 61.919 | 277.43 | 5.91 | 1610 |  |  |  | 61.92 | 277.227 | 5.82 | 1611 |  |  |  | 61.921 | 529.94 | 0.148 | 79 | 4.64
161.06 | 277.439 | 5.84 | 1616 |  |  |  | 61.92 | 277.334 | 5.94 | 1617 |  |  |  | 61.919 | 277.338 | 5.87 | 1625 |  |  |  | 61.92 | 533.44 | 0.153 | 81 | 4.64
161.56 | 277.439 | 5.84 | 1616 |  |  |  | 61.92 | 277.334 | 5.94 | 1617 |  |  |  | 61.919 | 277.338 | 5.87 | 1625 |  |  |  | 61.92 | 533.44 | 0.153 | 81 | 4.64
162.06 | 277.363 | 5.83 | 1612 |  |  |  | 61.919 | 277.564 | 5.93 | 1617 |  |  |  | 61.921 | 277.314 | 5.84 | 1616 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 4.64
162.56 | 277.363 | 5.83 | 1612 |  |  |  | 61.919 | 277.564 | 5.93 | 1617 |  |  |  | 61.921 | 277.314 | 5.84 | 1616 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 4.64
163.06 | 277.418 | 5.82 | 1610 |  |  |  | 61.921 | 277.422 | 5.95 | 1621 |  |  |  | 61.92 | 277.272 | 5.83 | 1614 |  |  |  | 61.921 | 533.41 | 0.149 | 79 | 4.64
163.56 | 277.418 | 5.82 | 1610 |  |  |  | 61.921 | 277.422 | 5.95 | 1621 |  |  |  | 61.92 | 277.272 | 5.83 | 1614 |  |  |  | 61.921 | 533.41 | 0.149 | 79 | 4.64
164.06 | 277.33 | 5.82 | 1610 |  |  |  | 61.92 | 277.542 | 5.96 | 1622 |  |  |  | 61.922 | 277.246 | 5.87 | 1624 |  |  |  | 61.92 | 536.12 | 0.15 | 81 | 4.64
164.56 | 277.33 | 5.82 | 1610 |  |  |  | 61.92 | 277.542 | 5.96 | 1622 |  |  |  | 61.922 | 277.246 | 5.87 | 1624 |  |  |  | 61.92 | 536.12 | 0.15 | 81 | 4.64
165.06 | 277.397 | 5.63 | 1556 |  |  |  | 61.92 | 277.401 | 5.75 | 1562 |  |  |  | 61.919 | 277.325 | 5.66 | 1566 |  |  |  | 61.922 | 539.89 | 0.145 | 78 | 4.64
165.56 | 277.397 | 5.63 | 1556 |  |  |  | 61.92 | 277.401 | 5.75 | 1562 |  |  |  | 61.919 | 277.325 | 5.66 | 1566 |  |  |  | 61.922 | 539.89 | 0.145 | 78 | 4.64
166.06 | 277.304 | 5.85 | 1618 |  |  |  | 61.917 | 277.321 | 5.96 | 1620 |  |  |  | 61.92 | 277.314 | 5.86 | 1623 |  |  |  | 61.92 | 536.91 | 0.153 | 82 | 4.64
166.56 | 277.304 | 5.85 | 1618 |  |  |  | 61.917 | 277.321 | 5.96 | 1620 |  |  |  | 61.92 | 277.314 | 5.86 | 1623 |  |  |  | 61.92 | 536.91 | 0.153 | 82 | 4.64
167.06 | 277.369 | 5.83 | 1615 |  |  |  | 61.921 | 277.476 | 5.96 | 1622 |  |  |  | 61.921 | 277.283 | 5.84 | 1618 |  |  |  | 61.921 | 533.44 | 0.151 | 81 | 4.64
167.56 | 277.369 | 5.83 | 1615 |  |  |  | 61.921 | 277.476 | 5.96 | 1622 |  |  |  | 61.921 | 277.283 | 5.84 | 1618 |  |  |  | 61.921 | 533.44 | 0.151 | 81 | 4.64
168.06 | 277.448 | 5.83 | 1613 |  |  |  | 61.92 | 277.365 | 5.95 | 1619 |  |  |  | 61.919 | 277.246 | 5.86 | 1623 |  |  |  | 61.92 | 533.43 | 0.147 | 78 | 4.64
168.56 | 277.448 | 5.83 | 1613 |  |  |  | 61.92 | 277.365 | 5.95 | 1619 |  |  |  | 61.919 | 277.246 | 5.86 | 1623 |  |  |  | 61.92 | 533.43 | 0.147 | 78 | 4.64
169.06 | 277.377 | 5.83 | 1613 |  |  |  | 61.919 | 277.52 | 5.95 | 1622 |  |  |  | 61.919 | 277.22 | 5.86 | 1623 |  |  |  | 61.92 | 533.42 | 0.153 | 82 | 4.64
169.56 | 277.377 | 5.83 | 1613 |  |  |  | 61.919 | 277.52 | 5.95 | 1622 |  |  |  | 61.919 | 277.22 | 5.86 | 1623 |  |  |  | 61.92 | 533.42 | 0.153 | 82 | 4.64
170.06 | 277.429 | 5.82 | 1610 |  |  |  | 61.921 | 277.398 | 5.94 | 1617 |  |  |  | 61.921 | 277.328 | 5.84 | 1618 |  |  |  | 61.92 | 530.72 | 0.144 | 76 | 4.64
170.56 | 277.429 | 5.82 | 1610 |  |  |  | 61.921 | 277.398 | 5.94 | 1617 |  |  |  | 61.921 | 277.328 | 5.84 | 1618 |  |  |  | 61.92 | 530.72 | 0.144 | 76 | 4.64
171.06 | 277.365 | 5.78 | 1598 |  |  |  | 61.92 | 277.584 | 5.9 | 1608 |  |  |  | 61.922 | 277.298 | 5.8 | 1607 |  |  |  | 61.921 | 526.95 | 0.154 | 81 | 4.64
171.56 | 277.365 | 5.78 | 1598 |  |  |  | 61.92 | 277.584 | 5.9 | 1608 |  |  |  | 61.922 | 277.298 | 5.8 | 1607 |  |  |  | 61.921 | 526.95 | 0.154 | 81 | 4.64
172.06 | 277.427 | 5.78 | 1600 |  |  |  | 61.921 | 277.498 | 5.93 | 1614 |  |  |  | 61.92 | 277.264 | 5.82 | 1612 |  |  |  | 61.92 | 529.95 | 0.153 | 81 | 4.64
172.56 | 277.427 | 5.78 | 1600 |  |  |  | 61.921 | 277.498 | 5.93 | 1614 |  |  |  | 61.92 | 277.264 | 5.82 | 1612 |  |  |  | 61.92 | 529.95 | 0.153 | 81 | 4.64
173.06 | 277.327 | 5.82 | 1609 |  |  |  | 61.92 | 277.318 | 5.95 | 1620 |  |  |  | 61.919 | 277.242 | 5.86 | 1624 |  |  |  | 61.92 | 533.42 | 0.149 | 79 | 4.64
173.56 | 277.327 | 5.82 | 1609 |  |  |  | 61.92 | 277.318 | 5.95 | 1620 |  |  |  | 61.919 | 277.242 | 5.86 | 1624 |  |  |  | 61.92 | 533.42 | 0.149 | 79 | 4.64
174.06 | 277.395 | 5.83 | 1613 |  |  |  | 61.92 | 277.489 | 5.95 | 1620 |  |  |  | 61.919 | 277.325 | 5.86 | 1623 |  |  |  | 61.919 | 533.46 | 0.152 | 81 | 4.64
174.56 | 277.395 | 5.83 | 1613 |  |  |  | 61.92 | 277.489 | 5.95 | 1620 |  |  |  | 61.919 | 277.325 | 5.86 | 1623 |  |  |  | 61.919 | 533.46 | 0.152 | 81 | 4.64
175.06 | 277.308 | 5.84 | 1614 |  |  |  | 61.918 | 277.353 | 5.94 | 1618 |  |  |  | 61.919 | 277.305 | 5.86 | 1622 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
175.56 | 277.308 | 5.84 | 1614 |  |  |  | 61.918 | 277.353 | 5.94 | 1618 |  |  |  | 61.919 | 277.305 | 5.86 | 1622 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
176.06 | 277.401 | 5.83 | 1614 |  |  |  | 61.92 | 277.545 | 5.94 | 1619 |  |  |  | 61.923 | 277.268 | 5.85 | 1619 |  |  |  | 61.92 | 536.11 | 0.152 | 81 | 4.64
176.56 | 277.401 | 5.83 | 1614 |  |  |  | 61.92 | 277.545 | 5.94 | 1619 |  |  |  | 61.923 | 277.268 | 5.85 | 1619 |  |  |  | 61.92 | 536.11 | 0.152 | 81 | 4.64
177.06 | 277.465 | 5.64 | 1560 |  |  |  | 61.92 | 277.397 | 5.77 | 1568 |  |  |  | 61.92 | 277.233 | 5.65 | 1565 |  |  |  | 61.92 | 539.86 | 0.149 | 81 | 4.64
177.56 | 277.465 | 5.64 | 1560 |  |  |  | 61.92 | 277.397 | 5.77 | 1568 |  |  |  | 61.92 | 277.233 | 5.65 | 1565 |  |  |  | 61.92 | 539.86 | 0.149 | 81 | 4.64
178.06 | 277.408 | 5.82 | 1610 |  |  |  | 61.92 | 277.469 | 5.95 | 1621 |  |  |  | 61.92 | 277.327 | 5.87 | 1625 |  |  |  | 61.921 | 536.92 | 0.15 | 80 | 4.64
178.56 | 277.408 | 5.82 | 1610 |  |  |  | 61.92 | 277.469 | 5.95 | 1621 |  |  |  | 61.92 | 277.327 | 5.87 | 1625 |  |  |  | 61.921 | 536.92 | 0.15 | 80 | 4.64
179.06 | 277.451 | 5.84 | 1615 |  |  |  | 61.921 | 277.444 | 5.95 | 1619 |  |  |  | 61.92 | 277.319 | 5.86 | 1623 |  |  |  | 61.92 | 533.38 | 0.148 | 79 | 4.64
179.56 | 277.451 | 5.84 | 1615 |  |  |  | 61.921 | 277.444 | 5.95 | 1619 |  |  |  | 61.92 | 277.319 | 5.86 | 1623 |  |  |  | 61.92 | 533.38 | 0.148 | 79 | 4.64
180.06 | 277.392 | 5.84 | 1616 |  |  |  | 61.921 | 277.273 | 5.94 | 1616 |  |  |  | 61.92 | 277.293 | 5.85 | 1621 |  |  |  | 61.921 | 533.37 | 0.152 | 81 | 4.64
180.56 | 277.392 | 5.84 | 1616 |  |  |  | 61.921 | 277.273 | 5.94 | 1616 |  |  |  | 61.92 | 277.293 | 5.85 | 1621 |  |  |  | 61.921 | 533.37 | 0.152 | 81 | 4.64
181.06 | 277.448 | 5.82 | 1611 |  |  |  | 61.921 | 277.469 | 5.94 | 1619 |  |  |  | 61.919 | 277.253 | 5.84 | 1618 |  |  |  | 61.92 | 533.47 | 0.151 | 81 | 4.64
181.56 | 277.448 | 5.82 | 1611 |  |  |  | 61.921 | 277.469 | 5.94 | 1619 |  |  |  | 61.919 | 277.253 | 5.84 | 1618 |  |  |  | 61.92 | 533.47 | 0.151 | 81 | 4.64
182.06 | 277.355 | 5.81 | 1608 |  |  |  | 61.92 | 277.318 | 5.96 | 1622 |  |  |  | 61.921 | 277.234 | 5.84 | 1616 |  |  |  | 61.92 | 530.8 | 0.152 | 81 | 4.64
182.6 | 277.355 | 5.81 | 1608 |  |  |  | 61.92 | 277.318 | 5.96 | 1622 |  |  |  | 61.921 | 277.234 | 5.84 | 1616 |  |  |  | 61.92 | 530.8 | 0.152 | 81 | 4.64
183.1 | 277.435 | 5.78 | 1600 |  |  |  | 61.921 | 277.502 | 5.89 | 1605 |  |  |  | 61.922 | 277.321 | 5.82 | 1612 |  |  |  | 61.92 | 526.99 | 0.151 | 80 | 4.64
183.58 | 277.435 | 5.78 | 1600 |  |  |  | 61.921 | 277.502 | 5.89 | 1605 |  |  |  | 61.922 | 277.321 | 5.82 | 1612 |  |  |  | 61.92 | 526.99 | 0.151 | 80 | 4.64
184.08 | 277.366 | 5.8 | 1605 |  |  |  | 61.917 | 277.335 | 5.91 | 1611 |  |  |  | 61.92 | 277.302 | 5.83 | 1615 |  |  |  | 61.921 | 529.79 | 0.151 | 80 | 4.64
184.57 | 277.366 | 5.8 | 1605 |  |  |  | 61.917 | 277.335 | 5.91 | 1611 |  |  |  | 61.92 | 277.302 | 5.83 | 1615 |  |  |  | 61.921 | 529.79 | 0.151 | 80 | 4.64
185.07 | 277.417 | 5.84 | 1616 |  |  |  | 61.92 | 277.271 | 5.95 | 1619 |  |  |  | 61.919 | 277.262 | 5.84 | 1618 |  |  |  | 61.92 | 533.38 | 0.15 | 80 | 4.64
185.56 | 277.417 | 5.84 | 1616 |  |  |  | 61.92 | 277.271 | 5.95 | 1619 |  |  |  | 61.919 | 277.262 | 5.84 | 1618 |  |  |  | 61.92 | 533.38 | 0.15 | 80 | 4.64
186.06 | 277.477 | 5.83 | 1613 |  |  |  | 61.921 | 277.444 | 5.96 | 1625 |  |  |  | 61.921 | 277.22 | 5.85 | 1620 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
186.59 | 277.405 | 5.83 | 1612 |  |  |  | 61.92 | 277.301 | 5.94 | 1616 |  |  |  | 61.92 | 277.337 | 5.87 | 1624 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 4.64
187.09 | 277.405 | 5.83 | 1612 |  |  |  | 61.92 | 277.301 | 5.94 | 1616 |  |  |  | 61.92 | 277.337 | 5.87 | 1624 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 4.64
187.58 | 277.456 | 5.83 | 1613 |  |  |  | 61.921 | 277.476 | 5.96 | 1623 |  |  |  | 61.92 | 277.314 | 5.86 | 1622 |  |  |  | 61.92 | 536.01 | 0.147 | 79 | 4.64
188.08 | 277.456 | 5.83 | 1613 |  |  |  | 61.921 | 277.476 | 5.96 | 1623 |  |  |  | 61.92 | 277.314 | 5.86 | 1622 |  |  |  | 61.92 | 536.01 | 0.147 | 79 | 4.64
188.56 | 277.366 | 5.66 | 1566 |  |  |  | 61.92 | 277.339 | 5.76 | 1566 |  |  |  | 61.92 | 277.278 | 5.68 | 1573 |  |  |  | 61.92 | 539.82 | 0.15 | 81 | 4.64
189.06 | 277.366 | 5.66 | 1566 |  |  |  | 61.92 | 277.339 | 5.76 | 1566 |  |  |  | 61.92 | 277.278 | 5.68 | 1573 |  |  |  | 61.92 | 539.82 | 0.15 | 81 | 4.64
189.56 | 277.451 | 5.85 | 1618 |  |  |  | 61.92 | 277.556 | 5.94 | 1620 |  |  |  | 61.922 | 277.241 | 5.84 | 1616 |  |  |  | 61.92 | 537.03 | 0.151 | 81 | 4.64
190.06 | 277.451 | 5.85 | 1618 |  |  |  | 61.92 | 277.556 | 5.94 | 1620 |  |  |  | 61.922 | 277.241 | 5.84 | 1616 |  |  |  | 61.92 | 537.03 | 0.151 | 81 | 4.64
190.56 | 277.35 | 5.83 | 1612 |  |  |  | 61.92 | 277.397 | 5.96 | 1622 |  |  |  | 61.92 | 277.334 | 5.85 | 1621 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
191.06 | 277.35 | 5.83 | 1612 |  |  |  | 61.92 | 277.397 | 5.96 | 1622 |  |  |  | 61.92 | 277.334 | 5.85 | 1621 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
191.56 | 277.427 | 5.81 | 1609 |  |  |  | 61.921 | 277.297 | 5.94 | 1616 |  |  |  | 61.919 | 277.31 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.151 | 81 | 4.64
192.06 | 277.427 | 5.81 | 1609 |  |  |  | 61.921 | 277.297 | 5.94 | 1616 |  |  |  | 61.919 | 277.31 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.151 | 81 | 4.64
192.56 | 277.391 | 5.84 | 1615 |  |  |  | 61.919 | 277.435 | 5.95 | 1621 |  |  |  | 61.919 | 277.283 | 5.87 | 1624 |  |  |  | 61.921 | 533.43 | 0.155 | 83 | 4.64
193.06 | 277.391 | 5.84 | 1615 |  |  |  | 61.919 | 277.435 | 5.95 | 1621 |  |  |  | 61.919 | 277.283 | 5.87 | 1624 |  |  |  | 61.921 | 533.43 | 0.155 | 83 | 4.64
193.56 | 277.409 | 5.82 | 1609 |  |  |  | 61.92 | 277.332 | 5.95 | 1621 |  |  |  | 61.92 | 277.254 | 5.83 | 1613 |  |  |  | 61.921 | 530.85 | 0.152 | 81 | 4.64
194.06 | 277.409 | 5.82 | 1609 |  |  |  | 61.92 | 277.332 | 5.95 | 1621 |  |  |  | 61.92 | 277.254 | 5.83 | 1613 |  |  |  | 61.921 | 530.85 | 0.152 | 81 | 4.64
194.56 | 277.467 | 5.8 | 1604 |  |  |  | 61.921 | 277.533 | 5.92 | 1612 |  |  |  | 61.923 | 277.229 | 5.82 | 1611 |  |  |  | 61.921 | 527 | 0.155 | 82 | 4.64
195.06 | 277.467 | 5.8 | 1604 |  |  |  | 61.921 | 277.533 | 5.92 | 1612 |  |  |  | 61.923 | 277.229 | 5.82 | 1611 |  |  |  | 61.921 | 527 | 0.155 | 82 | 4.64
195.56 | 277.392 | 5.79 | 1603 |  |  |  | 61.92 | 277.39 | 5.92 | 1613 |  |  |  | 61.92 | 277.343 | 5.81 | 1610 |  |  |  | 61.92 | 529.74 | 0.153 | 81 | 4.64
196.06 | 277.392 | 5.79 | 1603 |  |  |  | 61.92 | 277.39 | 5.92 | 1613 |  |  |  | 61.92 | 277.343 | 5.81 | 1610 |  |  |  | 61.92 | 529.74 | 0.153 | 81 | 4.64
196.56 | 277.437 | 5.83 | 1612 |  |  |  | 61.92 | 277.473 | 5.95 | 1621 |  |  |  | 61.919 | 277.318 | 5.85 | 1619 |  |  |  | 61.92 | 533.4 | 0.151 | 80 | 4.64
197.06 | 277.437 | 5.83 | 1612 |  |  |  | 61.92 | 277.473 | 5.95 | 1621 |  |  |  | 61.919 | 277.318 | 5.85 | 1619 |  |  |  | 61.92 | 533.4 | 0.151 | 80 | 4.64
197.56 | 277.34 | 5.84 | 1616 |  |  |  | 61.919 | 277.436 | 5.96 | 1623 |  |  |  | 61.92 | 277.295 | 5.87 | 1624 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
198.06 | 277.34 | 5.84 | 1616 |  |  |  | 61.919 | 277.436 | 5.96 | 1623 |  |  |  | 61.92 | 277.295 | 5.87 | 1624 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
198.56 | 277.422 | 5.8 | 1605 |  |  |  | 61.921 | 277.335 | 5.95 | 1617 |  |  |  | 61.921 | 277.268 | 5.86 | 1623 |  |  |  | 61.92 | 533.44 | 0.151 | 80 | 4.64
199.06 | 277.422 | 5.8 | 1605 |  |  |  | 61.921 | 277.335 | 5.95 | 1617 |  |  |  | 61.921 | 277.268 | 5.86 | 1623 |  |  |  | 61.92 | 533.44 | 0.151 | 80 | 4.64
199.56 | 277.338 | 5.84 | 1614 |  |  |  | 61.921 | 277.511 | 5.95 | 1619 |  |  |  | 61.919 | 277.34 | 5.86 | 1622 |  |  |  | 61.92 | 535.94 | 0.151 | 81 | 4.64
200.06 | 277.338 | 5.84 | 1614 |  |  |  | 61.921 | 277.511 | 5.95 | 1619 |  |  |  | 61.919 | 277.34 | 5.86 | 1622 |  |  |  | 61.92 | 535.94 | 0.151 | 81 | 4.64
200.56 | 277.399 | 5.66 | 1565 |  |  |  | 61.921 | 277.381 | 5.76 | 1567 |  |  |  | 61.92 | 277.311 | 5.66 | 1568 |  |  |  | 61.92 | 539.86 | 0.149 | 80 | 4.64
201.06 | 277.399 | 5.66 | 1565 |  |  |  | 61.921 | 277.381 | 5.76 | 1567 |  |  |  | 61.92 | 277.311 | 5.66 | 1568 |  |  |  | 61.92 | 539.86 | 0.149 | 80 | 4.64
201.56 | 277.354 | 5.83 | 1612 |  |  |  | 61.919 | 277.555 | 5.96 | 1623 |  |  |  | 61.923 | 277.298 | 5.87 | 1624 |  |  |  | 61.92 | 537.02 | 0.15 | 81 | 4.64
202.06 | 277.354 | 5.83 | 1612 |  |  |  | 61.919 | 277.555 | 5.96 | 1623 |  |  |  | 61.923 | 277.298 | 5.87 | 1624 |  |  |  | 61.92 | 537.02 | 0.15 | 81 | 4.64
202.56 | 277.388 | 5.84 | 1615 |  |  |  | 61.921 | 277.435 | 5.97 | 1625 |  |  |  | 61.92 | 277.275 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.153 | 81 | 4.64
203.06 | 277.388 | 5.84 | 1615 |  |  |  | 61.921 | 277.435 | 5.97 | 1625 |  |  |  | 61.92 | 277.275 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.153 | 81 | 4.64
203.56 | 277.441 | 5.83 | 1613 |  |  |  | 61.92 | 277.4 | 5.96 | 1623 |  |  |  | 61.918 | 277.366 | 5.86 | 1623 |  |  |  | 61.92 | 533.41 | 0.149 | 79 | 4.64
204.06 | 277.441 | 5.83 | 1613 |  |  |  | 61.92 | 277.4 | 5.96 | 1623 |  |  |  | 61.918 | 277.366 | 5.86 | 1623 |  |  |  | 61.92 | 533.41 | 0.149 | 79 | 4.64
204.56 | 277.368 | 5.82 | 1611 |  |  |  | 61.921 | 277.499 | 5.95 | 1620 |  |  |  | 61.919 | 277.335 | 5.85 | 1621 |  |  |  | 61.919 | 533.43 | 0.152 | 81 | 4.64
205.06 | 277.368 | 5.82 | 1611 |  |  |  | 61.921 | 277.499 | 5.95 | 1620 |  |  |  | 61.919 | 277.335 | 5.85 | 1621 |  |  |  | 61.919 | 533.43 | 0.152 | 81 | 4.64
205.56 | 277.433 | 5.8 | 1605 |  |  |  | 61.921 | 277.323 | 5.95 | 1617 |  |  |  | 61.92 | 277.31 | 5.84 | 1616 |  |  |  | 61.92 | 530.83 | 0.149 | 79 | 4.64
206.06 | 277.433 | 5.8 | 1605 |  |  |  | 61.921 | 277.323 | 5.95 | 1617 |  |  |  | 61.92 | 277.31 | 5.84 | 1616 |  |  |  | 61.92 | 530.83 | 0.149 | 79 | 4.64
206.56 | 277.336 | 5.78 | 1598 |  |  |  | 61.92 | 277.514 | 5.91 | 1608 |  |  |  | 61.92 | 277.292 | 5.8 | 1606 |  |  |  | 61.919 | 526.98 | 0.155 | 81 | 4.64
207.06 | 277.336 | 5.78 | 1598 |  |  |  | 61.92 | 277.514 | 5.91 | 1608 |  |  |  | 61.92 | 277.292 | 5.8 | 1606 |  |  |  | 61.919 | 526.98 | 0.155 | 81 | 4.64
207.56 | 277.42 | 5.8 | 1605 |  |  |  | 61.92 | 277.409 | 5.92 | 1610 |  |  |  | 61.919 | 277.249 | 5.82 | 1612 |  |  |  | 61.92 | 529.79 | 0.158 | 83 | 4.64
208.06 | 277.42 | 5.8 | 1605 |  |  |  | 61.92 | 277.409 | 5.92 | 1610 |  |  |  | 61.919 | 277.249 | 5.82 | 1612 |  |  |  | 61.92 | 529.79 | 0.158 | 83 | 4.64
208.56 | 277.322 | 5.84 | 1615 |  |  |  | 61.92 | 277.609 | 5.96 | 1622 |  |  |  | 61.923 | 277.347 | 5.84 | 1617 |  |  |  | 61.921 | 533.43 | 0.149 | 79 | 4.64
209.06 | 277.322 | 5.84 | 1615 |  |  |  | 61.92 | 277.609 | 5.96 | 1622 |  |  |  | 61.923 | 277.347 | 5.84 | 1617 |  |  |  | 61.921 | 533.43 | 0.149 | 79 | 4.64
209.56 | 277.39 | 5.83 | 1614 |  |  |  | 61.921 | 277.461 | 5.95 | 1619 |  |  |  | 61.92 | 277.311 | 5.84 | 1618 |  |  |  | 61.92 | 533.46 | 0.152 | 81 | 4.64
210.06 | 277.39 | 5.83 | 1614 |  |  |  | 61.921 | 277.461 | 5.95 | 1619 |  |  |  | 61.92 | 277.311 | 5.84 | 1618 |  |  |  | 61.92 | 533.46 | 0.152 | 81 | 4.64
210.56 | 277.339 | 5.83 | 1611 |  |  |  | 61.918 | 277.319 | 5.96 | 1621 |  |  |  | 61.919 | 277.281 | 5.86 | 1621 |  |  |  | 61.92 | 533.46 | 0.151 | 80 | 4.64
211.06 | 277.339 | 5.83 | 1611 |  |  |  | 61.918 | 277.319 | 5.96 | 1621 |  |  |  | 61.919 | 277.281 | 5.86 | 1621 |  |  |  | 61.92 | 533.46 | 0.151 | 80 | 4.64
211.56 | 277.382 | 5.83 | 1612 |  |  |  | 61.921 | 277.51 | 5.95 | 1617 |  |  |  | 61.92 | 277.252 | 5.87 | 1626 |  |  |  | 61.92 | 536.05 | 0.152 | 81 | 4.64
212.06 | 277.382 | 5.83 | 1612 |  |  |  | 61.921 | 277.51 | 5.95 | 1617 |  |  |  | 61.92 | 277.252 | 5.87 | 1626 |  |  |  | 61.92 | 536.05 | 0.152 | 81 | 4.64
212.56 | 277.435 | 5.65 | 1563 |  |  |  | 61.92 | 277.323 | 5.76 | 1566 |  |  |  | 61.919 | 277.329 | 5.66 | 1568 |  |  |  | 61.92 | 539.86 | 0.154 | 83 | 4.64
213.06 | 277.435 | 5.65 | 1563 |  |  |  | 61.92 | 277.323 | 5.76 | 1566 |  |  |  | 61.919 | 277.329 | 5.66 | 1568 |  |  |  | 61.92 | 539.86 | 0.154 | 83 | 4.64
213.56 | 277.378 | 5.84 | 1614 |  |  |  | 61.921 | 277.552 | 5.94 | 1618 |  |  |  | 61.922 | 277.298 | 5.85 | 1620 |  |  |  | 61.92 | 537.06 | 0.155 | 83 | 4.64
214.06 | 277.378 | 5.84 | 1614 |  |  |  | 61.921 | 277.552 | 5.94 | 1618 |  |  |  | 61.922 | 277.298 | 5.85 | 1620 |  |  |  | 61.92 | 537.06 | 0.155 | 83 | 4.64
214.56 | 277.432 | 5.83 | 1613 |  |  |  | 61.921 | 277.388 | 5.96 | 1621 |  |  |  | 61.92 | 277.262 | 5.86 | 1623 |  |  |  | 61.92 | 533.47 | 0.156 | 83 | 4.64
215.1 | 277.432 | 5.83 | 1613 |  |  |  | 61.921 | 277.388 | 5.96 | 1621 |  |  |  | 61.92 | 277.262 | 5.86 | 1623 |  |  |  | 61.92 | 533.47 | 0.156 | 83 | 4.64
215.6 | 277.363 | 5.8 | 1606 |  |  |  | 61.92 | 277.454 | 5.94 | 1616 |  |  |  | 61.919 | 277.243 | 5.85 | 1621 |  |  |  | 61.919 | 533.48 | 0.149 | 80 | 4.64
216.08 | 277.363 | 5.8 | 1606 |  |  |  | 61.92 | 277.454 | 5.94 | 1616 |  |  |  | 61.919 | 277.243 | 5.85 | 1621 |  |  |  | 61.919 | 533.48 | 0.149 | 80 | 4.64
216.58 | 277.432 | 5.83 | 1613 |  |  |  | 61.92 | 277.455 | 5.95 | 1618 |  |  |  | 61.92 | 277.332 | 5.86 | 1622 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
217.07 | 277.432 | 5.83 | 1613 |  |  |  | 61.92 | 277.455 | 5.95 | 1618 |  |  |  | 61.92 | 277.332 | 5.86 | 1622 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
217.57 | 277.355 | 5.83 | 1613 |  |  |  | 61.92 | 277.324 | 5.94 | 1617 |  |  |  | 61.919 | 277.316 | 5.84 | 1617 |  |  |  | 61.92 | 530.88 | 0.157 | 83 | 4.64
218.06 | 277.355 | 5.83 | 1613 |  |  |  | 61.92 | 277.324 | 5.94 | 1617 |  |  |  | 61.919 | 277.316 | 5.84 | 1617 |  |  |  | 61.92 | 530.88 | 0.157 | 83 | 4.64
218.56 | 277.414 | 5.77 | 1596 |  |  |  | 61.921 | 277.516 | 5.91 | 1611 |  |  |  | 61.919 | 277.274 | 5.81 | 1608 |  |  |  | 61.92 | 527.02 | 0.152 | 80 | 4.64
219.09 | 277.363 | 5.8 | 1605 |  |  |  | 61.917 | 277.364 | 5.9 | 1607 |  |  |  | 61.919 | 277.245 | 5.83 | 1613 |  |  |  | 61.919 | 529.76 | 0.15 | 80 | 4.64
219.59 | 277.363 | 5.8 | 1605 |  |  |  | 61.917 | 277.364 | 5.9 | 1607 |  |  |  | 61.919 | 277.245 | 5.83 | 1613 |  |  |  | 61.919 | 529.76 | 0.15 | 80 | 4.64
220.08 | 277.42 | 5.83 | 1613 |  |  |  | 61.921 | 277.549 | 5.95 | 1620 |  |  |  | 61.923 | 277.22 | 5.84 | 1618 |  |  |  | 61.921 | 533.46 | 0.149 | 79 | 4.64
220.58 | 277.42 | 5.83 | 1613 |  |  |  | 61.921 | 277.549 | 5.95 | 1620 |  |  |  | 61.923 | 277.22 | 5.84 | 1618 |  |  |  | 61.921 | 533.46 | 0.149 | 79 | 4.64
221.06 | 277.469 | 5.83 | 1614 |  |  |  | 61.921 | 277.38 | 5.95 | 1620 |  |  |  | 61.92 | 277.327 | 5.85 | 1620 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
221.56 | 277.469 | 5.83 | 1614 |  |  |  | 61.921 | 277.38 | 5.95 | 1620 |  |  |  | 61.92 | 277.327 | 5.85 | 1620 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
222.06 | 277.394 | 5.83 | 1611 |  |  |  | 61.921 | 277.276 | 5.95 | 1621 |  |  |  | 61.918 | 277.306 | 5.86 | 1623 |  |  |  | 61.92 | 533.49 | 0.149 | 79 | 4.64
222.56 | 277.394 | 5.83 | 1611 |  |  |  | 61.921 | 277.276 | 5.95 | 1621 |  |  |  | 61.918 | 277.306 | 5.86 | 1623 |  |  |  | 61.92 | 533.49 | 0.149 | 79 | 4.64
223.06 | 277.457 | 5.84 | 1615 |  |  |  | 61.921 | 277.44 | 5.94 | 1616 |  |  |  | 61.92 | 277.265 | 5.85 | 1621 |  |  |  | 61.92 | 535.94 | 0.151 | 81 | 4.64
223.56 | 277.457 | 5.84 | 1615 |  |  |  | 61.921 | 277.44 | 5.94 | 1616 |  |  |  | 61.92 | 277.265 | 5.85 | 1621 |  |  |  | 61.92 | 535.94 | 0.151 | 81 | 4.64
224.06 | 277.345 | 5.63 | 1557 |  |  |  | 61.921 | 277.312 | 5.75 | 1562 |  |  |  | 61.919 | 277.235 | 5.66 | 1567 |  |  |  | 61.92 | 539.91 | 0.151 | 82 | 4.64
224.56 | 277.345 | 5.63 | 1557 |  |  |  | 61.921 | 277.312 | 5.75 | 1562 |  |  |  | 61.919 | 277.235 | 5.66 | 1567 |  |  |  | 61.92 | 539.91 | 0.151 | 82 | 4.64
225.06 | 277.429 | 5.85 | 1618 |  |  |  | 61.921 | 277.476 | 5.96 | 1623 |  |  |  | 61.921 | 277.328 | 5.84 | 1618 |  |  |  | 61.921 | 537.19 | 0.147 | 79 | 4.64
225.56 | 277.429 | 5.85 | 1618 |  |  |  | 61.921 | 277.476 | 5.96 | 1623 |  |  |  | 61.921 | 277.328 | 5.84 | 1618 |  |  |  | 61.921 | 537.19 | 0.147 | 79 | 4.64
226.06 | 277.35 | 5.82 | 1610 |  |  |  | 61.921 | 277.346 | 5.96 | 1622 |  |  |  | 61.92 | 277.318 | 5.85 | 1619 |  |  |  | 61.92 | 533.46 | 0.152 | 81 | 4.64
226.56 | 277.35 | 5.82 | 1610 |  |  |  | 61.921 | 277.346 | 5.96 | 1622 |  |  |  | 61.92 | 277.318 | 5.85 | 1619 |  |  |  | 61.92 | 533.46 | 0.152 | 81 | 4.64
227.06 | 277.42 | 5.83 | 1612 |  |  |  | 61.921 | 277.478 | 5.94 | 1617 |  |  |  | 61.921 | 277.281 | 5.87 | 1624 |  |  |  | 61.921 | 533.5 | 0.147 | 79 | 4.64
227.56 | 277.42 | 5.83 | 1612 |  |  |  | 61.921 | 277.478 | 5.94 | 1617 |  |  |  | 61.921 | 277.281 | 5.87 | 1624 |  |  |  | 61.921 | 533.5 | 0.147 | 79 | 4.64
228.06 | 277.365 | 5.85 | 1617 |  |  |  | 61.918 | 277.397 | 5.95 | 1620 |  |  |  | 61.921 | 277.24 | 5.88 | 1626 |  |  |  | 61.921 | 533.47 | 0.15 | 80 | 4.64
228.56 | 277.365 | 5.85 | 1617 |  |  |  | 61.918 | 277.397 | 5.95 | 1620 |  |  |  | 61.921 | 277.24 | 5.88 | 1626 |  |  |  | 61.921 | 533.47 | 0.15 | 80 | 4.64
229.06 | 277.43 | 5.83 | 1612 |  |  |  | 61.921 | 277.286 | 5.93 | 1614 |  |  |  | 61.92 | 277.361 | 5.83 | 1615 |  |  |  | 61.923 | 530.87 | 0.144 | 77 | 4.64
229.56 | 277.43 | 5.83 | 1612 |  |  |  | 61.921 | 277.286 | 5.93 | 1614 |  |  |  | 61.92 | 277.361 | 5.83 | 1615 |  |  |  | 61.923 | 530.87 | 0.144 | 77 | 4.64
230.06 | 277.466 | 5.78 | 1600 |  |  |  | 61.92 | 277.458 | 5.93 | 1614 |  |  |  | 61.92 | 277.343 | 5.8 | 1607 |  |  |  | 61.921 | 526.94 | 0.149 | 79 | 4.64
230.56 | 277.466 | 5.78 | 1600 |  |  |  | 61.92 | 277.458 | 5.93 | 1614 |  |  |  | 61.92 | 277.343 | 5.8 | 1607 |  |  |  | 61.921 | 526.94 | 0.149 | 79 | 4.64
231.06 | 277.399 | 5.79 | 1602 |  |  |  | 61.921 | 277.343 | 5.94 | 1616 |  |  |  | 61.92 | 277.32 | 5.81 | 1610 |  |  |  | 61.92 | 529.82 | 0.149 | 79 | 4.64
231.56 | 277.399 | 5.79 | 1602 |  |  |  | 61.921 | 277.343 | 5.94 | 1616 |  |  |  | 61.92 | 277.32 | 5.81 | 1610 |  |  |  | 61.92 | 529.82 | 0.149 | 79 | 4.64
232.06 | 277.467 | 5.83 | 1612 |  |  |  | 61.921 | 277.539 | 5.93 | 1616 |  |  |  | 61.921 | 277.277 | 5.87 | 1626 |  |  |  | 61.92 | 533.47 | 0.149 | 79 | 4.64
232.56 | 277.467 | 5.83 | 1612 |  |  |  | 61.921 | 277.539 | 5.93 | 1616 |  |  |  | 61.921 | 277.277 | 5.87 | 1626 |  |  |  | 61.92 | 533.47 | 0.149 | 79 | 4.64
233.06 | 277.336 | 5.83 | 1613 |  |  |  | 61.92 | 277.412 | 5.94 | 1616 |  |  |  | 61.921 | 277.255 | 5.85 | 1619 |  |  |  | 61.921 | 533.5 | 0.147 | 78 | 4.64
233.56 | 277.336 | 5.83 | 1613 |  |  |  | 61.92 | 277.412 | 5.94 | 1616 |  |  |  | 61.921 | 277.255 | 5.85 | 1619 |  |  |  | 61.921 | 533.5 | 0.147 | 78 | 4.64
234.06 | 277.418 | 5.84 | 1616 |  |  |  | 61.92 | 277.351 | 5.94 | 1616 |  |  |  | 61.919 | 277.349 | 5.85 | 1621 |  |  |  | 61.921 | 533.47 | 0.149 | 80 | 4.64
234.56 | 277.418 | 5.84 | 1616 |  |  |  | 61.92 | 277.351 | 5.94 | 1616 |  |  |  | 61.919 | 277.349 | 5.85 | 1621 |  |  |  | 61.921 | 533.47 | 0.149 | 80 | 4.64
235.06 | 277.334 | 5.83 | 1612 |  |  |  | 61.92 | 277.455 | 5.96 | 1623 |  |  |  | 61.92 | 277.328 | 5.86 | 1622 |  |  |  | 61.921 | 535.96 | 0.153 | 82 | 4.64
235.56 | 277.334 | 5.83 | 1612 |  |  |  | 61.92 | 277.455 | 5.96 | 1623 |  |  |  | 61.92 | 277.328 | 5.86 | 1622 |  |  |  | 61.921 | 535.96 | 0.153 | 82 | 4.64
236.06 | 277.388 | 5.64 | 1559 |  |  |  | 61.921 | 277.293 | 5.77 | 1567 |  |  |  | 61.92 | 277.282 | 5.67 | 1570 |  |  |  | 61.921 | 539.88 | 0.152 | 82 | 4.64
236.56 | 277.388 | 5.64 | 1559 |  |  |  | 61.921 | 277.293 | 5.77 | 1567 |  |  |  | 61.92 | 277.282 | 5.67 | 1570 |  |  |  | 61.921 | 539.88 | 0.152 | 82 | 4.64
237.06 | 277.334 | 5.85 | 1617 |  |  |  | 61.918 | 277.493 | 5.95 | 1620 |  |  |  | 61.92 | 277.244 | 5.87 | 1625 |  |  |  | 61.92 | 537.13 | 0.147 | 79 | 4.64
237.56 | 277.334 | 5.85 | 1617 |  |  |  | 61.918 | 277.493 | 5.95 | 1620 |  |  |  | 61.92 | 277.244 | 5.87 | 1625 |  |  |  | 61.92 | 537.13 | 0.147 | 79 | 4.64
238.06 | 277.396 | 5.83 | 1613 |  |  |  | 61.921 | 277.367 | 5.95 | 1618 |  |  |  | 61.921 | 277.361 | 5.86 | 1622 |  |  |  | 61.92 | 533.45 | 0.147 | 79 | 4.64
238.56 | 277.396 | 5.83 | 1613 |  |  |  | 61.921 | 277.367 | 5.95 | 1618 |  |  |  | 61.921 | 277.361 | 5.86 | 1622 |  |  |  | 61.92 | 533.45 | 0.147 | 79 | 4.64
239.06 | 277.457 | 5.84 | 1617 |  |  |  | 61.92 | 277.534 | 5.95 | 1620 |  |  |  | 61.923 | 277.341 | 5.85 | 1619 |  |  |  | 61.92 | 533.49 | 0.148 | 79 | 4.64
239.56 | 277.457 | 5.84 | 1617 |  |  |  | 61.92 | 277.534 | 5.95 | 1620 |  |  |  | 61.923 | 277.341 | 5.85 | 1619 |  |  |  | 61.92 | 533.49 | 0.148 | 79 | 4.64
240.06 | 277.365 | 5.82 | 1609 |  |  |  | 61.921 | 277.409 | 5.96 | 1621 |  |  |  | 61.918 | 277.316 | 5.85 | 1620 |  |  |  | 61.919 | 533.48 | 0.147 | 78 | 4.64
240.56 | 277.365 | 5.82 | 1609 |  |  |  | 61.921 | 277.409 | 5.96 | 1621 |  |  |  | 61.918 | 277.316 | 5.85 | 1620 |  |  |  | 61.919 | 533.48 | 0.147 | 78 | 4.64
241.06 | 277.441 | 5.82 | 1609 |  |  |  | 61.921 | 277.281 | 5.95 | 1618 |  |  |  | 61.92 | 277.271 | 5.84 | 1617 |  |  |  | 61.921 | 530.66 | 0.146 | 77 | 4.64
241.56 | 277.441 | 5.82 | 1609 |  |  |  | 61.921 | 277.281 | 5.95 | 1618 |  |  |  | 61.92 | 277.271 | 5.84 | 1617 |  |  |  | 61.921 | 530.66 | 0.146 | 77 | 4.64
242.06 | 277.339 | 5.78 | 1597 |  |  |  | 61.92 | 277.533 | 5.91 | 1609 |  |  |  | 61.92 | 277.292 | 5.81 | 1609 |  |  |  | 61.92 | 527 | 0.148 | 78 | 4.64
242.56 | 277.339 | 5.78 | 1597 |  |  |  | 61.92 | 277.533 | 5.91 | 1609 |  |  |  | 61.92 | 277.292 | 5.81 | 1609 |  |  |  | 61.92 | 527 | 0.148 | 78 | 4.64
243.06 | 277.41 | 5.79 | 1602 |  |  |  | 61.92 | 277.351 | 5.94 | 1615 |  |  |  | 61.919 | 277.334 | 5.84 | 1616 |  |  |  | 61.921 | 529.91 | 0.152 | 81 | 4.64
243.56 | 277.41 | 5.79 | 1602 |  |  |  | 61.92 | 277.351 | 5.94 | 1615 |  |  |  | 61.919 | 277.334 | 5.84 | 1616 |  |  |  | 61.921 | 529.91 | 0.152 | 81 | 4.64
244.06 | 277.34 | 5.85 | 1617 |  |  |  | 61.92 | 277.557 | 5.95 | 1621 |  |  |  | 61.921 | 277.312 | 5.84 | 1618 |  |  |  | 61.919 | 533.44 | 0.15 | 80 | 4.64
244.56 | 277.34 | 5.85 | 1617 |  |  |  | 61.92 | 277.557 | 5.95 | 1621 |  |  |  | 61.921 | 277.312 | 5.84 | 1618 |  |  |  | 61.919 | 533.44 | 0.15 | 80 | 4.64
245.06 | 277.395 | 5.83 | 1613 |  |  |  | 61.92 | 277.434 | 5.96 | 1620 |  |  |  | 61.918 | 277.281 | 5.85 | 1621 |  |  |  | 61.921 | 533.43 | 0.15 | 80 | 4.64
245.56 | 277.395 | 5.83 | 1613 |  |  |  | 61.92 | 277.434 | 5.96 | 1620 |  |  |  | 61.918 | 277.281 | 5.85 | 1621 |  |  |  | 61.921 | 533.43 | 0.15 | 80 | 4.64
246.06 | 277.322 | 5.82 | 1610 |  |  |  | 61.917 | 277.539 | 5.96 | 1623 |  |  |  | 61.922 | 277.249 | 5.85 | 1619 |  |  |  | 61.919 | 533.41 | 0.153 | 82 | 4.64
246.56 | 277.322 | 5.82 | 1610 |  |  |  | 61.917 | 277.539 | 5.96 | 1623 |  |  |  | 61.922 | 277.249 | 5.85 | 1619 |  |  |  | 61.919 | 533.41 | 0.153 | 82 | 4.64
247.06 | 277.394 | 5.82 | 1609 |  |  |  | 61.921 | 277.467 | 5.96 | 1621 |  |  |  | 61.919 | 277.342 | 5.85 | 1621 |  |  |  | 61.921 | 536.1 | 0.152 | 81 | 4.64
247.56 | 277.394 | 5.82 | 1609 |  |  |  | 61.921 | 277.467 | 5.96 | 1621 |  |  |  | 61.919 | 277.342 | 5.85 | 1621 |  |  |  | 61.921 | 536.1 | 0.152 | 81 | 4.64
248.06 | 277.438 | 5.65 | 1562 |  |  |  | 61.92 | 277.332 | 5.77 | 1569 |  |  |  | 61.92 | 277.317 | 5.68 | 1573 |  |  |  | 61.92 | 539.84 | 0.15 | 81 | 4.64
248.56 | 277.438 | 5.65 | 1562 |  |  |  | 61.92 | 277.332 | 5.77 | 1569 |  |  |  | 61.92 | 277.317 | 5.68 | 1573 |  |  |  | 61.92 | 539.84 | 0.15 | 81 | 4.64
249.06 | 277.352 | 5.85 | 1618 |  |  |  | 61.921 | 277.516 | 5.94 | 1617 |  |  |  | 61.92 | 277.299 | 5.87 | 1624 |  |  |  | 61.921 | 536.95 | 0.147 | 79 | 4.64
249.59 | 277.352 | 5.85 | 1618 |  |  |  | 61.921 | 277.516 | 5.94 | 1617 |  |  |  | 61.92 | 277.299 | 5.87 | 1624 |  |  |  | 61.921 | 536.95 | 0.147 | 79 | 4.64
250.09 | 277.423 | 5.84 | 1615 |  |  |  | 61.921 | 277.336 | 5.94 | 1618 |  |  |  | 61.919 | 277.269 | 5.86 | 1622 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 4.64
250.58 | 277.423 | 5.84 | 1615 |  |  |  | 61.921 | 277.336 | 5.94 | 1618 |  |  |  | 61.919 | 277.269 | 5.86 | 1622 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 4.64
251.08 | 277.333 | 5.84 | 1615 |  |  |  | 61.921 | 277.574 | 5.96 | 1624 |  |  |  | 61.922 | 277.36 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.153 | 81 | 4.64
251.56 | 277.333 | 5.84 | 1615 |  |  |  | 61.921 | 277.574 | 5.96 | 1624 |  |  |  | 61.922 | 277.36 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.153 | 81 | 4.64
252.06 | 277.402 | 5.82 | 1611 |  |  |  | 61.921 | 277.409 | 5.95 | 1621 |  |  |  | 61.921 | 277.328 | 5.84 | 1617 |  |  |  | 61.921 | 533.47 | 0.15 | 80 | 4.64
252.6 | 277.402 | 5.82 | 1611 |  |  |  | 61.921 | 277.409 | 5.95 | 1621 |  |  |  | 61.921 | 277.328 | 5.84 | 1617 |  |  |  | 61.921 | 533.47 | 0.15 | 80 | 4.64
253.1 | 277.348 | 5.8 | 1604 |  |  |  | 61.92 | 277.32 | 5.92 | 1613 |  |  |  | 61.919 | 277.308 | 5.86 | 1622 |  |  |  | 61.92 | 530.82 | 0.149 | 79 | 4.64
253.59 | 277.397 | 5.79 | 1602 |  |  |  | 61.921 | 277.488 | 5.9 | 1606 |  |  |  | 61.92 | 277.276 | 5.82 | 1612 |  |  |  | 61.921 | 526.99 | 0.147 | 77 | 4.64
254.09 | 277.397 | 5.79 | 1602 |  |  |  | 61.921 | 277.488 | 5.9 | 1606 |  |  |  | 61.92 | 277.276 | 5.82 | 1612 |  |  |  | 61.921 | 526.99 | 0.147 | 77 | 4.64
254.57 | 277.332 | 5.8 | 1605 |  |  |  | 61.918 | 277.348 | 5.92 | 1612 |  |  |  | 61.92 | 277.239 | 5.83 | 1613 |  |  |  | 61.921 | 529.87 | 0.15 | 79 | 4.64
255.07 | 277.332 | 5.8 | 1605 |  |  |  | 61.918 | 277.348 | 5.92 | 1612 |  |  |  | 61.92 | 277.239 | 5.83 | 1613 |  |  |  | 61.921 | 529.87 | 0.15 | 79 | 4.64
255.57 | 277.39 | 5.83 | 1612 |  |  |  | 61.921 | 277.537 | 5.95 | 1621 |  |  |  | 61.92 | 277.348 | 5.84 | 1618 |  |  |  | 61.921 | 533.41 | 0.148 | 79 | 4.64
256.07 | 277.39 | 5.83 | 1612 |  |  |  | 61.921 | 277.537 | 5.95 | 1621 |  |  |  | 61.92 | 277.348 | 5.84 | 1618 |  |  |  | 61.921 | 533.41 | 0.148 | 79 | 4.64
256.56 | 277.45 | 5.83 | 1612 |  |  |  | 61.92 | 277.402 | 5.94 | 1617 |  |  |  | 61.92 | 277.326 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.149 | 79 | 4.64
257.06 | 277.45 | 5.83 | 1612 |  |  |  | 61.92 | 277.402 | 5.94 | 1617 |  |  |  | 61.92 | 277.326 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.149 | 79 | 4.64
257.56 | 277.392 | 5.81 | 1608 |  |  |  | 61.92 | 277.542 | 5.95 | 1621 |  |  |  | 61.922 | 277.297 | 5.87 | 1624 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
258.06 | 277.392 | 5.81 | 1608 |  |  |  | 61.92 | 277.542 | 5.95 | 1621 |  |  |  | 61.922 | 277.297 | 5.87 | 1624 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
258.56 | 277.463 | 5.86 | 1620 |  |  |  | 61.92 | 277.413 | 5.94 | 1617 |  |  |  | 61.92 | 277.262 | 5.86 | 1621 |  |  |  | 61.921 | 536.07 | 0.152 | 82 | 4.64
259.06 | 277.463 | 5.86 | 1620 |  |  |  | 61.92 | 277.413 | 5.94 | 1617 |  |  |  | 61.92 | 277.262 | 5.86 | 1621 |  |  |  | 61.921 | 536.07 | 0.152 | 82 | 4.64
259.56 | 277.375 | 5.68 | 1570 |  |  |  | 61.921 | 277.315 | 5.78 | 1569 |  |  |  | 61.919 | 277.351 | 5.69 | 1576 |  |  |  | 61.921 | 539.8 | 0.153 | 83 | 4.64
260.06 | 277.375 | 5.68 | 1570 |  |  |  | 61.921 | 277.315 | 5.78 | 1569 |  |  |  | 61.919 | 277.351 | 5.69 | 1576 |  |  |  | 61.921 | 539.8 | 0.153 | 83 | 4.64
260.56 | 277.436 | 5.82 | 1612 |  |  |  | 61.921 | 277.435 | 5.96 | 1624 |  |  |  | 61.92 | 277.327 | 5.86 | 1623 |  |  |  | 61.921 | 537.02 | 0.15 | 81 | 4.64
261.06 | 277.436 | 5.82 | 1612 |  |  |  | 61.921 | 277.435 | 5.96 | 1624 |  |  |  | 61.92 | 277.327 | 5.86 | 1623 |  |  |  | 61.921 | 537.02 | 0.15 | 81 | 4.64
261.56 | 277.367 | 5.84 | 1615 |  |  |  | 61.92 | 277.318 | 5.97 | 1624 |  |  |  | 61.92 | 277.307 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 4.64
262.06 | 277.367 | 5.84 | 1615 |  |  |  | 61.92 | 277.318 | 5.97 | 1624 |  |  |  | 61.92 | 277.307 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 4.64
262.56 | 277.434 | 5.83 | 1612 |  |  |  | 61.921 | 277.536 | 5.95 | 1621 |  |  |  | 61.923 | 277.282 | 5.86 | 1622 |  |  |  | 61.921 | 533.43 | 0.154 | 82 | 4.64
263.06 | 277.434 | 5.83 | 1612 |  |  |  | 61.921 | 277.536 | 5.95 | 1621 |  |  |  | 61.923 | 277.282 | 5.86 | 1622 |  |  |  | 61.921 | 533.43 | 0.154 | 82 | 4.64
263.56 | 277.347 | 5.84 | 1616 |  |  |  | 61.917 | 277.401 | 5.96 | 1622 |  |  |  | 61.92 | 277.366 | 5.83 | 1615 |  |  |  | 61.921 | 533.47 | 0.152 | 81 | 4.64
264.06 | 277.347 | 5.84 | 1616 |  |  |  | 61.917 | 277.401 | 5.96 | 1622 |  |  |  | 61.92 | 277.366 | 5.83 | 1615 |  |  |  | 61.921 | 533.47 | 0.152 | 81 | 4.64
264.56 | 277.422 | 5.84 | 1615 |  |  |  | 61.921 | 277.388 | 5.94 | 1617 |  |  |  | 61.92 | 277.338 | 5.84 | 1617 |  |  |  | 61.921 | 530.81 | 0.146 | 78 | 4.64
265.06 | 277.422 | 5.84 | 1615 |  |  |  | 61.921 | 277.388 | 5.94 | 1617 |  |  |  | 61.92 | 277.338 | 5.84 | 1617 |  |  |  | 61.921 | 530.81 | 0.146 | 78 | 4.64
265.56 | 277.482 | 5.79 | 1602 |  |  |  | 61.921 | 277.424 | 5.91 | 1607 |  |  |  | 61.921 | 277.312 | 5.81 | 1610 |  |  |  | 61.919 | 526.99 | 0.149 | 78 | 4.64
266.06 | 277.482 | 5.79 | 1602 |  |  |  | 61.921 | 277.424 | 5.91 | 1607 |  |  |  | 61.921 | 277.312 | 5.81 | 1610 |  |  |  | 61.919 | 526.99 | 0.149 | 78 | 4.64
266.56 | 277.388 | 5.8 | 1605 |  |  |  | 61.921 | 277.291 | 5.91 | 1610 |  |  |  | 61.919 | 277.286 | 5.83 | 1613 |  |  |  | 61.92 | 529.79 | 0.15 | 80 | 4.64
267.06 | 277.388 | 5.8 | 1605 |  |  |  | 61.921 | 277.291 | 5.91 | 1610 |  |  |  | 61.919 | 277.286 | 5.83 | 1613 |  |  |  | 61.92 | 529.79 | 0.15 | 80 | 4.64
267.56 | 277.462 | 5.84 | 1615 |  |  |  | 61.92 | 277.465 | 5.94 | 1617 |  |  |  | 61.92 | 277.251 | 5.86 | 1622 |  |  |  | 61.919 | 533.41 | 0.149 | 79 | 4.64
268.06 | 277.462 | 5.84 | 1615 |  |  |  | 61.92 | 277.465 | 5.94 | 1617 |  |  |  | 61.92 | 277.251 | 5.86 | 1622 |  |  |  | 61.919 | 533.41 | 0.149 | 79 | 4.64
268.56 | 277.378 | 5.84 | 1614 |  |  |  | 61.921 | 277.363 | 5.95 | 1618 |  |  |  | 61.919 | 277.348 | 5.85 | 1621 |  |  |  | 61.921 | 533.38 | 0.154 | 82 | 4.64
269.06 | 277.378 | 5.84 | 1614 |  |  |  | 61.921 | 277.363 | 5.95 | 1618 |  |  |  | 61.919 | 277.348 | 5.85 | 1621 |  |  |  | 61.921 | 533.38 | 0.154 | 82 | 4.64
269.56 | 277.432 | 5.82 | 1612 |  |  |  | 61.921 | 277.527 | 5.96 | 1623 |  |  |  | 61.922 | 277.317 | 5.85 | 1620 |  |  |  | 61.919 | 533.38 | 0.152 | 81 | 4.64
270.06 | 277.432 | 5.82 | 1612 |  |  |  | 61.921 | 277.527 | 5.96 | 1623 |  |  |  | 61.922 | 277.317 | 5.85 | 1620 |  |  |  | 61.919 | 533.38 | 0.152 | 81 | 4.64
270.56 | 277.366 | 5.82 | 1609 |  |  |  | 61.92 | 277.344 | 5.95 | 1620 |  |  |  | 61.92 | 277.287 | 5.85 | 1621 |  |  |  | 61.92 | 536 | 0.15 | 81 | 4.64
271.06 | 277.366 | 5.82 | 1609 |  |  |  | 61.92 | 277.344 | 5.95 | 1620 |  |  |  | 61.92 | 277.287 | 5.85 | 1621 |  |  |  | 61.92 | 536 | 0.15 | 81 | 4.64
271.56 | 277.425 | 5.65 | 1563 |  |  |  | 61.921 | 277.223 | 5.78 | 1571 |  |  |  | 61.921 | 277.258 | 5.68 | 1572 |  |  |  | 61.92 | 539.83 | 0.153 | 82 | 4.64
272.06 | 277.425 | 5.65 | 1563 |  |  |  | 61.921 | 277.223 | 5.78 | 1571 |  |  |  | 61.921 | 277.258 | 5.68 | 1572 |  |  |  | 61.92 | 539.83 | 0.153 | 82 | 4.64
272.56 | 277.365 | 5.86 | 1620 |  |  |  | 61.919 | 277.47 | 5.95 | 1623 |  |  |  | 61.92 | 277.365 | 5.85 | 1620 |  |  |  | 61.921 | 537.03 | 0.153 | 82 | 4.64
273.06 | 277.365 | 5.86 | 1620 |  |  |  | 61.919 | 277.47 | 5.95 | 1623 |  |  |  | 61.92 | 277.365 | 5.85 | 1620 |  |  |  | 61.921 | 537.03 | 0.153 | 82 | 4.64
273.56 | 277.411 | 5.82 | 1610 |  |  |  | 61.921 | 277.291 | 5.95 | 1621 |  |  |  | 61.92 | 277.336 | 5.85 | 1620 |  |  |  | 61.92 | 533.43 | 0.15 | 80 | 4.64
274.06 | 277.411 | 5.82 | 1610 |  |  |  | 61.921 | 277.291 | 5.95 | 1621 |  |  |  | 61.92 | 277.336 | 5.85 | 1620 |  |  |  | 61.92 | 533.43 | 0.15 | 80 | 4.64
274.56 | 277.484 | 5.81 | 1608 |  |  |  | 61.92 | 277.496 | 5.94 | 1618 |  |  |  | 61.922 | 277.298 | 5.86 | 1624 |  |  |  | 61.92 | 533.42 | 0.153 | 82 | 4.64
275.06 | 277.484 | 5.81 | 1608 |  |  |  | 61.92 | 277.496 | 5.94 | 1618 |  |  |  | 61.922 | 277.298 | 5.86 | 1624 |  |  |  | 61.92 | 533.42 | 0.153 | 82 | 4.64
275.56 | 277.361 | 5.83 | 1613 |  |  |  | 61.92 | 277.396 | 5.96 | 1624 |  |  |  | 61.92 | 277.272 | 5.85 | 1620 |  |  |  | 61.921 | 533.42 | 0.155 | 83 | 4.64
276.06 | 277.361 | 5.83 | 1613 |  |  |  | 61.92 | 277.396 | 5.96 | 1624 |  |  |  | 61.92 | 277.272 | 5.85 | 1620 |  |  |  | 61.921 | 533.42 | 0.155 | 83 | 4.64
276.56 | 277.429 | 5.83 | 1613 |  |  |  | 61.921 | 277.513 | 5.93 | 1616 |  |  |  | 61.921 | 277.358 | 5.84 | 1618 |  |  |  | 61.923 | 530.83 | 0.15 | 80 | 4.64
277.06 | 277.429 | 5.83 | 1613 |  |  |  | 61.921 | 277.513 | 5.93 | 1616 |  |  |  | 61.921 | 277.358 | 5.84 | 1618 |  |  |  | 61.923 | 530.83 | 0.15 | 80 | 4.64
277.56 | 277.353 | 5.79 | 1600 |  |  |  | 61.92 | 277.445 | 5.92 | 1612 |  |  |  | 61.92 | 277.348 | 5.8 | 1607 |  |  |  | 61.92 | 526.99 | 0.151 | 79 | 4.64
278.06 | 277.353 | 5.79 | 1600 |  |  |  | 61.92 | 277.445 | 5.92 | 1612 |  |  |  | 61.92 | 277.348 | 5.8 | 1607 |  |  |  | 61.92 | 526.99 | 0.151 | 79 | 4.64
278.56 | 277.409 | 5.79 | 1601 |  |  |  | 61.921 | 277.306 | 5.94 | 1616 |  |  |  | 61.92 | 277.311 | 5.84 | 1617 |  |  |  | 61.92 | 529.71 | 0.151 | 80 | 4.64
279.06 | 277.409 | 5.79 | 1601 |  |  |  | 61.921 | 277.306 | 5.94 | 1616 |  |  |  | 61.92 | 277.311 | 5.84 | 1617 |  |  |  | 61.92 | 529.71 | 0.151 | 80 | 4.64
279.56 | 277.343 | 5.82 | 1610 |  |  |  | 61.921 | 277.465 | 5.95 | 1620 |  |  |  | 61.919 | 277.274 | 5.85 | 1621 |  |  |  | 61.92 | 533.45 | 0.155 | 82 | 4.64
280.06 | 277.343 | 5.82 | 1610 |  |  |  | 61.921 | 277.465 | 5.95 | 1620 |  |  |  | 61.919 | 277.274 | 5.85 | 1621 |  |  |  | 61.92 | 533.45 | 0.155 | 82 | 4.64
280.56 | 277.415 | 5.82 | 1609 |  |  |  | 61.921 | 277.315 | 5.95 | 1620 |  |  |  | 61.921 | 277.247 | 5.86 | 1622 |  |  |  | 61.92 | 533.45 | 0.154 | 82 | 4.64
281.06 | 277.415 | 5.82 | 1609 |  |  |  | 61.921 | 277.315 | 5.95 | 1620 |  |  |  | 61.921 | 277.247 | 5.86 | 1622 |  |  |  | 61.92 | 533.45 | 0.154 | 82 | 4.64
281.56 | 277.379 | 5.84 | 1616 |  |  |  | 61.921 | 277.547 | 5.95 | 1621 |  |  |  | 61.922 | 277.351 | 5.84 | 1617 |  |  |  | 61.92 | 533.39 | 0.152 | 81 | 4.64
282.08 | 277.379 | 5.84 | 1616 |  |  |  | 61.921 | 277.547 | 5.95 | 1621 |  |  |  | 61.922 | 277.351 | 5.84 | 1617 |  |  |  | 61.92 | 533.39 | 0.152 | 81 | 4.64
282.58 | 277.381 | 5.82 | 1611 |  |  |  | 61.921 | 277.394 | 5.95 | 1620 |  |  |  | 61.92 | 277.333 | 5.84 | 1619 |  |  |  | 61.92 | 535.85 | 0.149 | 80 | 4.64
283.06 | 277.381 | 5.82 | 1611 |  |  |  | 61.921 | 277.394 | 5.95 | 1620 |  |  |  | 61.92 | 277.333 | 5.84 | 1619 |  |  |  | 61.92 | 535.85 | 0.149 | 80 | 4.64
283.56 | 277.441 | 5.63 | 1557 |  |  |  | 61.92 | 277.376 | 5.76 | 1564 |  |  |  | 61.919 | 277.288 | 5.67 | 1569 |  |  |  | 61.92 | 539.85 | 0.15 | 81 | 4.64
284.1 | 277.351 | 5.82 | 1610 |  |  |  | 61.921 | 277.508 | 5.93 | 1615 |  |  |  | 61.92 | 277.269 | 5.86 | 1624 |  |  |  | 61.92 | 537.15 | 0.153 | 82 | 4.64
284.6 | 277.351 | 5.82 | 1610 |  |  |  | 61.921 | 277.508 | 5.93 | 1615 |  |  |  | 61.92 | 277.269 | 5.86 | 1624 |  |  |  | 61.92 | 537.15 | 0.153 | 82 | 4.64
285.09 | 277.416 | 5.83 | 1614 |  |  |  | 61.92 | 277.372 | 5.95 | 1621 |  |  |  | 61.92 | 277.357 | 5.87 | 1625 |  |  |  | 61.921 | 533.46 | 0.151 | 81 | 4.64
285.59 | 277.416 | 5.83 | 1614 |  |  |  | 61.92 | 277.372 | 5.95 | 1621 |  |  |  | 61.92 | 277.357 | 5.87 | 1625 |  |  |  | 61.921 | 533.46 | 0.151 | 81 | 4.64
286.08 | 277.351 | 5.83 | 1613 |  |  |  | 61.92 | 277.561 | 5.95 | 1621 |  |  |  | 61.92 | 277.342 | 5.84 | 1616 |  |  |  | 61.92 | 533.43 | 0.153 | 82 | 4.64
286.58 | 277.351 | 5.83 | 1613 |  |  |  | 61.92 | 277.561 | 5.95 | 1621 |  |  |  | 61.92 | 277.342 | 5.84 | 1616 |  |  |  | 61.92 | 533.43 | 0.153 | 82 | 4.64
287.06 | 277.405 | 5.83 | 1614 |  |  |  | 61.921 | 277.403 | 5.95 | 1622 |  |  |  | 61.92 | 277.307 | 5.85 | 1621 |  |  |  | 61.919 | 533.43 | 0.15 | 80 | 4.64
287.56 | 277.405 | 5.83 | 1614 |  |  |  | 61.921 | 277.403 | 5.95 | 1622 |  |  |  | 61.92 | 277.307 | 5.85 | 1621 |  |  |  | 61.919 | 533.43 | 0.15 | 80 | 4.64
288.06 | 277.342 | 5.82 | 1611 |  |  |  | 61.919 | 277.564 | 5.93 | 1617 |  |  |  | 61.922 | 277.273 | 5.86 | 1622 |  |  |  | 61.921 | 530.93 | 0.153 | 81 | 4.64
288.56 | 277.342 | 5.82 | 1611 |  |  |  | 61.919 | 277.564 | 5.93 | 1617 |  |  |  | 61.922 | 277.273 | 5.86 | 1622 |  |  |  | 61.921 | 530.93 | 0.153 | 81 | 4.64
289.06 | 277.42 | 5.79 | 1603 |  |  |  | 61.921 | 277.402 | 5.91 | 1609 |  |  |  | 61.918 | 277.26 | 5.82 | 1611 |  |  |  | 61.919 | 526.97 | 0.156 | 82 | 4.64
289.56 | 277.42 | 5.79 | 1603 |  |  |  | 61.921 | 277.402 | 5.91 | 1609 |  |  |  | 61.918 | 277.26 | 5.82 | 1611 |  |  |  | 61.919 | 526.97 | 0.156 | 82 | 4.64
290.06 | 277.46 | 5.81 | 1608 |  |  |  | 61.919 | 277.319 | 5.9 | 1608 |  |  |  | 61.92 | 277.344 | 5.83 | 1615 |  |  |  | 61.92 | 529.66 | 0.151 | 80 | 4.64
290.56 | 277.46 | 5.81 | 1608 |  |  |  | 61.919 | 277.319 | 5.9 | 1608 |  |  |  | 61.92 | 277.344 | 5.83 | 1615 |  |  |  | 61.92 | 529.66 | 0.151 | 80 | 4.64
291.06 | 277.387 | 5.86 | 1620 |  |  |  | 61.92 | 277.462 | 5.95 | 1622 |  |  |  | 61.919 | 277.324 | 5.85 | 1619 |  |  |  | 61.92 | 533.41 | 0.151 | 81 | 4.64
291.56 | 277.387 | 5.86 | 1620 |  |  |  | 61.92 | 277.462 | 5.95 | 1622 |  |  |  | 61.919 | 277.324 | 5.85 | 1619 |  |  |  | 61.92 | 533.41 | 0.151 | 81 | 4.64
292.06 | 277.451 | 5.83 | 1614 |  |  |  | 61.92 | 277.349 | 5.95 | 1619 |  |  |  | 61.92 | 277.29 | 5.83 | 1615 |  |  |  | 61.921 | 533.42 | 0.153 | 82 | 4.64
292.56 | 277.451 | 5.83 | 1614 |  |  |  | 61.92 | 277.349 | 5.95 | 1619 |  |  |  | 61.92 | 277.29 | 5.83 | 1615 |  |  |  | 61.921 | 533.42 | 0.153 | 82 | 4.64
293.06 | 277.356 | 5.82 | 1611 |  |  |  | 61.92 | 277.561 | 5.94 | 1619 |  |  |  | 61.92 | 277.262 | 5.85 | 1621 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 4.64
293.56 | 277.356 | 5.82 | 1611 |  |  |  | 61.92 | 277.561 | 5.94 | 1619 |  |  |  | 61.92 | 277.262 | 5.85 | 1621 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 4.64
294.06 | 277.417 | 5.83 | 1612 |  |  |  | 61.92 | 277.401 | 5.93 | 1616 |  |  |  | 61.92 | 277.351 | 5.86 | 1622 |  |  |  | 61.919 | 535.9 | 0.153 | 82 | 4.64
294.56 | 277.417 | 5.83 | 1612 |  |  |  | 61.92 | 277.401 | 5.93 | 1616 |  |  |  | 61.92 | 277.351 | 5.86 | 1622 |  |  |  | 61.919 | 535.9 | 0.153 | 82 | 4.64
295.06 | 277.345 | 5.65 | 1563 |  |  |  | 61.92 | 277.547 | 5.76 | 1569 |  |  |  | 61.922 | 277.332 | 5.69 | 1575 |  |  |  | 61.92 | 539.83 | 0.15 | 81 | 4.64
295.56 | 277.345 | 5.65 | 1563 |  |  |  | 61.92 | 277.547 | 5.76 | 1569 |  |  |  | 61.922 | 277.332 | 5.69 | 1575 |  |  |  | 61.92 | 539.83 | 0.15 | 81 | 4.64
296.06 | 277.402 | 5.85 | 1618 |  |  |  | 61.921 | 277.447 | 5.94 | 1617 |  |  |  | 61.92 | 277.299 | 5.85 | 1619 |  |  |  | 61.92 | 537.15 | 0.155 | 83 | 4.64
296.56 | 277.402 | 5.85 | 1618 |  |  |  | 61.921 | 277.447 | 5.94 | 1617 |  |  |  | 61.92 | 277.299 | 5.85 | 1619 |  |  |  | 61.92 | 537.15 | 0.155 | 83 | 4.64
297.06 | 277.331 | 5.83 | 1613 |  |  |  | 61.92 | 277.317 | 5.96 | 1623 |  |  |  | 61.919 | 277.263 | 5.84 | 1617 |  |  |  | 61.921 | 533.42 | 0.147 | 78 | 4.64
297.56 | 277.331 | 5.83 | 1613 |  |  |  | 61.92 | 277.317 | 5.96 | 1623 |  |  |  | 61.919 | 277.263 | 5.84 | 1617 |  |  |  | 61.921 | 533.42 | 0.147 | 78 | 4.64
298.06 | 277.417 | 5.81 | 1607 |  |  |  | 61.921 | 277.449 | 5.95 | 1620 |  |  |  | 61.919 | 277.362 | 5.85 | 1620 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 4.64
298.56 | 277.417 | 5.81 | 1607 |  |  |  | 61.921 | 277.449 | 5.95 | 1620 |  |  |  | 61.919 | 277.362 | 5.85 | 1620 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 4.64
299.06 | 277.471 | 5.83 | 1614 |  |  |  | 61.92 | 277.341 | 5.95 | 1618 |  |  |  | 61.92 | 277.344 | 5.86 | 1623 |  |  |  | 61.921 | 533.47 | 0.149 | 80 | 4.64
299.56 | 277.471 | 5.83 | 1614 |  |  |  | 61.92 | 277.341 | 5.95 | 1618 |  |  |  | 61.92 | 277.344 | 5.86 | 1623 |  |  |  | 61.921 | 533.47 | 0.149 | 80 | 4.64
300.06 | 277.389 | 5.85 | 1617 |  |  |  | 61.921 | 277.505 | 5.93 | 1614 |  |  |  | 61.923 | 277.322 | 5.84 | 1616 |  |  |  | 61.919 | 531.01 | 0.145 | 77 | 4.64
300.56 | 277.389 | 5.85 | 1617 |  |  |  | 61.921 | 277.505 | 5.93 | 1614 |  |  |  | 61.923 | 277.322 | 5.84 | 1616 |  |  |  | 61.919 | 531.01 | 0.145 | 77 | 4.64
301.06 | 277.452 | 5.8 | 1603 |  |  |  | 61.92 | 277.385 | 5.91 | 1606 |  |  |  | 61.921 | 277.278 | 5.8 | 1605 |  |  |  | 61.921 | 526.99 | 0.151 | 80 | 4.64
301.56 | 277.452 | 5.8 | 1603 |  |  |  | 61.92 | 277.385 | 5.91 | 1606 |  |  |  | 61.921 | 277.278 | 5.8 | 1605 |  |  |  | 61.921 | 526.99 | 0.151 | 80 | 4.64
302.06 | 277.384 | 5.8 | 1605 |  |  |  | 61.92 | 277.438 | 5.92 | 1612 |  |  |  | 61.919 | 277.244 | 5.82 | 1612 |  |  |  | 61.919 | 529.63 | 0.153 | 81 | 4.64
302.56 | 277.384 | 5.8 | 1605 |  |  |  | 61.92 | 277.438 | 5.92 | 1612 |  |  |  | 61.919 | 277.244 | 5.82 | 1612 |  |  |  | 61.919 | 529.63 | 0.153 | 81 | 4.64
303.06 | 277.448 | 5.83 | 1614 |  |  |  | 61.921 | 277.417 | 5.95 | 1619 |  |  |  | 61.92 | 277.349 | 5.85 | 1619 |  |  |  | 61.92 | 533.46 | 0.149 | 79 | 4.64
303.56 | 277.448 | 5.83 | 1614 |  |  |  | 61.921 | 277.417 | 5.95 | 1619 |  |  |  | 61.92 | 277.349 | 5.85 | 1619 |  |  |  | 61.92 | 533.46 | 0.149 | 79 | 4.64
304.06 | 277.373 | 5.85 | 1617 |  |  |  | 61.92 | 277.257 | 5.95 | 1618 |  |  |  | 61.921 | 277.327 | 5.86 | 1624 |  |  |  | 61.919 | 533.42 | 0.156 | 83 | 4.64
304.56 | 277.373 | 5.85 | 1617 |  |  |  | 61.92 | 277.257 | 5.95 | 1618 |  |  |  | 61.921 | 277.327 | 5.86 | 1624 |  |  |  | 61.919 | 533.42 | 0.156 | 83 | 4.64
305.06 | 277.447 | 5.84 | 1615 |  |  |  | 61.92 | 277.476 | 5.95 | 1621 |  |  |  | 61.92 | 277.291 | 5.86 | 1622 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 4.64
305.56 | 277.447 | 5.84 | 1615 |  |  |  | 61.92 | 277.476 | 5.95 | 1621 |  |  |  | 61.92 | 277.291 | 5.86 | 1622 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 4.64
306.06 | 277.347 | 5.84 | 1616 |  |  |  | 61.92 | 277.299 | 5.95 | 1620 |  |  |  | 61.919 | 277.249 | 5.84 | 1617 |  |  |  | 61.921 | 536.14 | 0.152 | 82 | 4.64
306.56 | 277.347 | 5.84 | 1616 |  |  |  | 61.92 | 277.299 | 5.95 | 1620 |  |  |  | 61.919 | 277.249 | 5.84 | 1617 |  |  |  | 61.921 | 536.14 | 0.152 | 82 | 4.64
307.06 | 277.427 | 5.63 | 1558 |  |  |  | 61.92 | 277.478 | 5.76 | 1566 |  |  |  | 61.922 | 277.349 | 5.66 | 1568 |  |  |  | 61.919 | 539.86 | 0.151 | 81 | 4.64
307.56 | 277.427 | 5.63 | 1558 |  |  |  | 61.92 | 277.478 | 5.76 | 1566 |  |  |  | 61.922 | 277.349 | 5.66 | 1568 |  |  |  | 61.919 | 539.86 | 0.151 | 81 | 4.64
308.06 | 277.461 | 5.83 | 1614 |  |  |  | 61.92 | 277.37 | 5.94 | 1617 |  |  |  | 61.921 | 277.329 | 5.86 | 1622 |  |  |  | 61.921 | 536.91 | 0.148 | 79 | 4.64
308.56 | 277.461 | 5.83 | 1614 |  |  |  | 61.92 | 277.37 | 5.94 | 1617 |  |  |  | 61.921 | 277.329 | 5.86 | 1622 |  |  |  | 61.921 | 536.91 | 0.148 | 79 | 4.64
309.06 | 277.388 | 5.85 | 1618 |  |  |  | 61.921 | 277.472 | 5.95 | 1620 |  |  |  | 61.92 | 277.307 | 5.83 | 1614 |  |  |  | 61.919 | 533.45 | 0.15 | 80 | 4.64
309.56 | 277.388 | 5.85 | 1618 |  |  |  | 61.921 | 277.472 | 5.95 | 1620 |  |  |  | 61.92 | 277.307 | 5.83 | 1614 |  |  |  | 61.919 | 533.45 | 0.15 | 80 | 4.64
310.06 | 277.47 | 5.82 | 1611 |  |  |  | 61.92 | 277.414 | 5.95 | 1621 |  |  |  | 61.919 | 277.273 | 5.84 | 1618 |  |  |  | 61.92 | 533.45 | 0.154 | 82 | 4.64
310.56 | 277.47 | 5.82 | 1611 |  |  |  | 61.92 | 277.414 | 5.95 | 1621 |  |  |  | 61.919 | 277.273 | 5.84 | 1618 |  |  |  | 61.92 | 533.45 | 0.154 | 82 | 4.64
311.06 | 277.391 | 5.82 | 1609 |  |  |  | 61.921 | 277.283 | 5.95 | 1620 |  |  |  | 61.919 | 277.367 | 5.86 | 1623 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 4.64
311.56 | 277.391 | 5.82 | 1609 |  |  |  | 61.921 | 277.283 | 5.95 | 1620 |  |  |  | 61.919 | 277.367 | 5.86 | 1623 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 4.64
312.06 | 277.451 | 5.84 | 1615 |  |  |  | 61.92 | 277.511 | 5.91 | 1611 |  |  |  | 61.921 | 277.338 | 5.85 | 1620 |  |  |  | 61.921 | 530.81 | 0.151 | 80 | 4.64
312.56 | 277.451 | 5.84 | 1615 |  |  |  | 61.92 | 277.511 | 5.91 | 1611 |  |  |  | 61.921 | 277.338 | 5.85 | 1620 |  |  |  | 61.921 | 530.81 | 0.151 | 80 | 4.64
313.06 | 277.381 | 5.79 | 1600 |  |  |  | 61.921 | 277.333 | 5.91 | 1609 |  |  |  | 61.92 | 277.314 | 5.81 | 1610 |  |  |  | 61.921 | 526.98 | 0.153 | 80 | 4.64
313.56 | 277.381 | 5.79 | 1600 |  |  |  | 61.921 | 277.333 | 5.91 | 1609 |  |  |  | 61.92 | 277.314 | 5.81 | 1610 |  |  |  | 61.921 | 526.98 | 0.153 | 80 | 4.64
314.37 | 277.445 | 5.8 | 1604 |  |  |  | 61.919 | 277.545 | 5.93 | 1615 |  |  |  | 61.922 | 277.293 | 5.83 | 1613 |  |  |  | 61.921 | 529.87 | 0.155 | 82 | 4.64
314.56 | 277.445 | 5.8 | 1604 |  |  |  | 61.919 | 277.545 | 5.93 | 1615 |  |  |  | 61.922 | 277.293 | 5.83 | 1613 |  |  |  | 61.921 | 529.87 | 0.155 | 82 | 4.64
315.06 | 278.019 | 6.39 | 1613 |  |  |  | 58.579 | 278.117 | 6.49 | 1618 |  |  |  | 58.577 | 277.87 | 6.42 | 1626 |  |  |  | 58.58 | 533.44 | 0.148 | 79 | 4.64
315.56 | 278.019 | 6.39 | 1613 |  |  |  | 58.579 | 278.117 | 6.49 | 1618 |  |  |  | 58.577 | 277.87 | 6.42 | 1626 |  |  |  | 58.58 | 533.44 | 0.148 | 79 | 4.64
316.06 | 279.315 | 6.36 | 1614 |  |  |  | 58.58 | 279.357 | 6.47 | 1621 |  |  |  | 58.58 | 279.158 | 6.4 | 1626 |  |  |  | 58.579 | 533.42 | 0.152 | 81 | 4.64
316.59 | 279.315 | 6.36 | 1614 |  |  |  | 58.58 | 279.357 | 6.47 | 1621 |  |  |  | 58.58 | 279.158 | 6.4 | 1626 |  |  |  | 58.579 | 533.42 | 0.152 | 81 | 4.64
317.09 | 278.471 | 6.2 | 1613 |  |  |  | 58.58 | 278.475 | 6.3 | 1623 |  |  |  | 58.58 | 278.286 | 6.23 | 1626 |  |  |  | 58.579 | 533.44 | 0.153 | 82 | 4.64
317.57 | 278.471 | 6.2 | 1613 |  |  |  | 58.58 | 278.475 | 6.3 | 1623 |  |  |  | 58.58 | 278.286 | 6.23 | 1626 |  |  |  | 58.579 | 533.44 | 0.153 | 82 | 4.64
318.07 | 277.891 | 5.99 | 1614 |  |  |  | 58.581 | 277.819 | 6.1 | 1620 |  |  |  | 58.58 | 277.751 | 6.02 | 1620 |  |  |  | 58.581 | 534.82 | 0.16 | 85 | 4.64
318.56 | 277.891 | 5.99 | 1614 |  |  |  | 58.581 | 277.819 | 6.1 | 1620 |  |  |  | 58.58 | 277.751 | 6.02 | 1620 |  |  |  | 58.581 | 534.82 | 0.16 | 85 | 4.64
319.06 | 277.667 | 5.73 | 1564 |  |  |  | 58.579 | 277.719 | 5.84 | 1571 |  |  |  | 58.58 | 277.482 | 5.73 | 1567 |  |  |  | 58.581 | 539.83 | 0.152 | 82 | 4.64
319.59 | 277.505 | 5.83 | 1603 |  |  |  | 58.581 | 277.428 | 5.93 | 1605 |  |  |  | 58.58 | 277.456 | 5.85 | 1611 |  |  |  | 58.58 | 538.93 | 0.151 | 82 | 4.64
320.09 | 277.505 | 5.83 | 1603 |  |  |  | 58.581 | 277.428 | 5.93 | 1605 |  |  |  | 58.58 | 277.456 | 5.85 | 1611 |  |  |  | 58.58 | 538.93 | 0.151 | 82 | 4.64
320.58 | 277.511 | 5.87 | 1618 |  |  |  | 58.581 | 277.6 | 5.94 | 1615 |  |  |  | 58.583 | 277.361 | 5.88 | 1625 |  |  |  | 58.58 | 533.48 | 0.148 | 79 | 4.64
321.08 | 277.511 | 5.87 | 1618 |  |  |  | 58.581 | 277.6 | 5.94 | 1615 |  |  |  | 58.583 | 277.361 | 5.88 | 1625 |  |  |  | 58.58 | 533.48 | 0.148 | 79 | 4.64
321.57 | 277.44 | 5.83 | 1611 |  |  |  | 58.58 | 277.406 | 5.95 | 1617 |  |  |  | 58.58 | 277.309 | 5.87 | 1622 |  |  |  | 58.579 | 533.41 | 0.154 | 82 | 4.64
322.07 | 277.44 | 5.83 | 1611 |  |  |  | 58.58 | 277.406 | 5.95 | 1617 |  |  |  | 58.58 | 277.309 | 5.87 | 1622 |  |  |  | 58.579 | 533.41 | 0.154 | 82 | 4.64
322.56 | 277.48 | 5.84 | 1614 |  |  |  | 58.58 | 277.318 | 5.95 | 1621 |  |  |  | 58.58 | 277.272 | 5.87 | 1625 |  |  |  | 58.58 | 533.43 | 0.158 | 84 | 4.64
323.06 | 277.48 | 5.84 | 1614 |  |  |  | 58.58 | 277.318 | 5.95 | 1621 |  |  |  | 58.58 | 277.272 | 5.87 | 1625 |  |  |  | 58.58 | 533.43 | 0.158 | 84 | 4.64
323.56 | 277.365 | 5.82 | 1610 |  |  |  | 58.58 | 277.48 | 5.97 | 1624 |  |  |  | 58.581 | 277.372 | 5.86 | 1623 |  |  |  | 58.582 | 533.47 | 0.149 | 80 | 4.64
324.06 | 277.365 | 5.82 | 1610 |  |  |  | 58.58 | 277.48 | 5.97 | 1624 |  |  |  | 58.581 | 277.372 | 5.86 | 1623 |  |  |  | 58.582 | 533.47 | 0.149 | 80 | 4.64
324.58 | 277.452 | 5.79 | 1603 |  |  |  | 58.58 | 277.328 | 5.93 | 1615 |  |  |  | 58.58 | 277.337 | 5.83 | 1614 |  |  |  | 58.58 | 527.44 | 0.154 | 81 | 4.64
325.06 | 277.452 | 5.79 | 1603 |  |  |  | 58.58 | 277.328 | 5.93 | 1615 |  |  |  | 58.58 | 277.337 | 5.83 | 1614 |  |  |  | 58.58 | 527.44 | 0.154 | 81 | 4.64
325.56 | 275.837 | 6.42 | 1598 |  |  |  | 61.92 | 275.834 | 6.55 | 1609 |  |  |  | 61.92 | 275.718 | 6.45 | 1607 |  |  |  | 61.921 | 526.98 | 0.151 | 79 | 4.64
326.06 | 275.837 | 6.42 | 1598 |  |  |  | 61.92 | 275.834 | 6.55 | 1609 |  |  |  | 61.92 | 275.718 | 6.45 | 1607 |  |  |  | 61.921 | 526.98 | 0.151 | 79 | 4.64
326.56 | 276.516 | 6.37 | 1609 |  |  |  | 61.92 | 276.446 | 6.47 | 1612 |  |  |  | 61.92 | 276.418 | 6.4 | 1614 |  |  |  | 61.92 | 533.02 | 0.152 | 81 | 4.64
327.06 | 276.516 | 6.37 | 1609 |  |  |  | 61.92 | 276.446 | 6.47 | 1612 |  |  |  | 61.92 | 276.418 | 6.4 | 1614 |  |  |  | 61.92 | 533.02 | 0.152 | 81 | 4.64
327.56 | 277.07 | 6.05 | 1609 |  |  |  | 61.92 | 277.128 | 6.17 | 1619 |  |  |  | 61.922 | 276.906 | 6.07 | 1614 |  |  |  | 61.921 | 533.44 | 0.151 | 80 | 4.64
328.06 | 277.07 | 6.05 | 1609 |  |  |  | 61.92 | 277.128 | 6.17 | 1619 |  |  |  | 61.922 | 276.906 | 6.07 | 1614 |  |  |  | 61.921 | 533.44 | 0.151 | 80 | 4.64
328.56 | 277.234 | 5.92 | 1608 |  |  |  | 61.92 | 277.252 | 6.06 | 1623 |  |  |  | 61.919 | 277.214 | 5.95 | 1619 |  |  |  | 61.921 | 533.38 | 0.149 | 80 | 4.64
329.06 | 277.234 | 5.92 | 1608 |  |  |  | 61.92 | 277.252 | 6.06 | 1623 |  |  |  | 61.919 | 277.214 | 5.95 | 1619 |  |  |  | 61.921 | 533.38 | 0.149 | 80 | 4.64
329.56 | 277.394 | 5.85 | 1608 |  |  |  | 61.921 | 277.239 | 6 | 1621 |  |  |  | 61.92 | 277.242 | 5.89 | 1620 |  |  |  | 61.921 | 533.45 | 0.15 | 80 | 4.64
330.06 | 277.394 | 5.85 | 1608 |  |  |  | 61.921 | 277.239 | 6 | 1621 |  |  |  | 61.92 | 277.242 | 5.89 | 1620 |  |  |  | 61.921 | 533.45 | 0.15 | 80 | 4.64
330.56 | 277.362 | 5.77 | 1592 |  |  |  | 61.92 | 277.437 | 5.89 | 1601 |  |  |  | 61.92 | 277.253 | 5.78 | 1596 |  |  |  | 61.919 | 539.15 | 0.151 | 81 | 4.64
331.06 | 277.362 | 5.77 | 1592 |  |  |  | 61.92 | 277.437 | 5.89 | 1601 |  |  |  | 61.92 | 277.253 | 5.78 | 1596 |  |  |  | 61.919 | 539.15 | 0.151 | 81 | 4.64
331.56 | 277.46 | 5.66 | 1565 |  |  |  | 61.921 | 277.353 | 5.75 | 1563 |  |  |  | 61.921 | 277.259 | 5.68 | 1570 |  |  |  | 61.921 | 539.82 | 0.15 | 81 | 4.64
332.06 | 277.46 | 5.66 | 1565 |  |  |  | 61.921 | 277.353 | 5.75 | 1563 |  |  |  | 61.921 | 277.259 | 5.68 | 1570 |  |  |  | 61.921 | 539.82 | 0.15 | 81 | 4.64
332.56 | 277.348 | 5.85 | 1618 |  |  |  | 61.92 | 277.52 | 5.98 | 1627 |  |  |  | 61.922 | 277.382 | 5.84 | 1618 |  |  |  | 61.92 | 533.83 | 0.149 | 79 | 4.64
333.06 | 277.348 | 5.85 | 1618 |  |  |  | 61.92 | 277.52 | 5.98 | 1627 |  |  |  | 61.922 | 277.382 | 5.84 | 1618 |  |  |  | 61.92 | 533.83 | 0.149 | 79 | 4.64
333.56 | 277.447 | 5.82 | 1609 |  |  |  | 61.92 | 277.411 | 5.95 | 1620 |  |  |  | 61.919 | 277.367 | 5.86 | 1622 |  |  |  | 61.921 | 533.42 | 0.153 | 81 | 4.64
334.06 | 277.447 | 5.82 | 1609 |  |  |  | 61.92 | 277.411 | 5.95 | 1620 |  |  |  | 61.919 | 277.367 | 5.86 | 1622 |  |  |  | 61.921 | 533.42 | 0.153 | 81 | 4.64
334.56 | 277.478 | 5.83 | 1612 |  |  |  | 61.921 | 277.524 | 5.94 | 1618 |  |  |  | 61.923 | 277.336 | 5.84 | 1617 |  |  |  | 61.92 | 533.44 | 0.146 | 78 | 4.64
335.06 | 277.478 | 5.83 | 1612 |  |  |  | 61.921 | 277.524 | 5.94 | 1618 |  |  |  | 61.923 | 277.336 | 5.84 | 1617 |  |  |  | 61.92 | 533.44 | 0.146 | 78 | 4.64
335.56 | 277.373 | 5.83 | 1613 |  |  |  | 61.921 | 277.456 | 5.94 | 1620 |  |  |  | 61.921 | 277.321 | 5.87 | 1625 |  |  |  | 61.921 | 533.47 | 0.149 | 80 | 4.64
336.06 | 277.373 | 5.83 | 1613 |  |  |  | 61.921 | 277.456 | 5.94 | 1620 |  |  |  | 61.921 | 277.321 | 5.87 | 1625 |  |  |  | 61.921 | 533.47 | 0.149 | 80 | 4.64
336.56 | 277.44 | 5.81 | 1609 |  |  |  | 61.921 | 277.291 | 5.92 | 1613 |  |  |  | 61.919 | 277.416 | 5.82 | 1611 |  |  |  | 61.92 | 527.68 | 0.15 | 79 | 4.64
337.06 | 277.44 | 5.81 | 1609 |  |  |  | 61.921 | 277.291 | 5.92 | 1613 |  |  |  | 61.919 | 277.416 | 5.82 | 1611 |  |  |  | 61.92 | 527.68 | 0.15 | 79 | 4.64
337.56 | 277.368 | 5.78 | 1599 |  |  |  | 61.919 | 277.512 | 5.91 | 1611 |  |  |  | 61.919 | 277.378 | 5.8 | 1608 |  |  |  | 61.92 | 526.95 | 0.149 | 79 | 4.64
338.06 | 277.368 | 5.78 | 1599 |  |  |  | 61.919 | 277.512 | 5.91 | 1611 |  |  |  | 61.919 | 277.378 | 5.8 | 1608 |  |  |  | 61.92 | 526.95 | 0.149 | 79 | 4.64
338.56 | 277.431 | 5.81 | 1607 |  |  |  | 61.921 | 277.326 | 5.94 | 1619 |  |  |  | 61.92 | 277.346 | 5.85 | 1621 |  |  |  | 61.921 | 532.96 | 0.15 | 80 | 4.64
339.06 | 277.431 | 5.81 | 1607 |  |  |  | 61.921 | 277.326 | 5.94 | 1619 |  |  |  | 61.92 | 277.346 | 5.85 | 1621 |  |  |  | 61.921 | 532.96 | 0.15 | 80 | 4.64
339.56 | 277.359 | 5.81 | 1608 |  |  |  | 61.921 | 277.528 | 5.94 | 1618 |  |  |  | 61.923 | 277.312 | 5.87 | 1626 |  |  |  | 61.92 | 533.45 | 0.149 | 80 | 4.64
340.06 | 277.359 | 5.81 | 1608 |  |  |  | 61.921 | 277.528 | 5.94 | 1618 |  |  |  | 61.923 | 277.312 | 5.87 | 1626 |  |  |  | 61.92 | 533.45 | 0.149 | 80 | 4.64
340.56 | 277.427 | 5.83 | 1614 |  |  |  | 61.921 | 277.415 | 5.94 | 1618 |  |  |  | 61.92 | 277.285 | 5.85 | 1619 |  |  |  | 61.92 | 533.44 | 0.151 | 80 | 4.64
341.06 | 277.427 | 5.83 | 1614 |  |  |  | 61.921 | 277.415 | 5.94 | 1618 |  |  |  | 61.92 | 277.285 | 5.85 | 1619 |  |  |  | 61.92 | 533.44 | 0.151 | 80 | 4.64
341.56 | 277.33 | 5.83 | 1613 |  |  |  | 61.916 | 277.441 | 5.93 | 1617 |  |  |  | 61.92 | 277.381 | 5.85 | 1619 |  |  |  | 61.92 | 533.46 | 0.153 | 82 | 4.64
342.06 | 277.33 | 5.83 | 1613 |  |  |  | 61.916 | 277.441 | 5.93 | 1617 |  |  |  | 61.92 | 277.381 | 5.85 | 1619 |  |  |  | 61.92 | 533.46 | 0.153 | 82 | 4.64
342.56 | 277.397 | 5.76 | 1594 |  |  |  | 61.921 | 277.484 | 5.88 | 1603 |  |  |  | 61.92 | 277.352 | 5.78 | 1601 |  |  |  | 61.92 | 539.1 | 0.149 | 80 | 4.64
343.06 | 277.397 | 5.76 | 1594 |  |  |  | 61.921 | 277.484 | 5.88 | 1603 |  |  |  | 61.92 | 277.352 | 5.78 | 1601 |  |  |  | 61.92 | 539.1 | 0.149 | 80 | 4.64
343.56 | 277.463 | 5.64 | 1561 |  |  |  | 61.92 | 277.317 | 5.75 | 1565 |  |  |  | 61.918 | 277.315 | 5.66 | 1567 |  |  |  | 61.919 | 539.87 | 0.152 | 82 | 4.64
344.06 | 277.463 | 5.64 | 1561 |  |  |  | 61.92 | 277.317 | 5.75 | 1565 |  |  |  | 61.918 | 277.315 | 5.66 | 1567 |  |  |  | 61.919 | 539.87 | 0.152 | 82 | 4.64
344.56 | 277.375 | 5.83 | 1613 |  |  |  | 61.92 | 277.561 | 5.96 | 1624 |  |  |  | 61.919 | 277.29 | 5.87 | 1625 |  |  |  | 61.92 | 533.91 | 0.152 | 81 | 4.64
345.06 | 277.375 | 5.83 | 1613 |  |  |  | 61.92 | 277.561 | 5.96 | 1624 |  |  |  | 61.919 | 277.29 | 5.87 | 1625 |  |  |  | 61.92 | 533.91 | 0.152 | 81 | 4.64
345.56 | 277.424 | 5.84 | 1617 |  |  |  | 61.92 | 277.376 | 5.95 | 1619 |  |  |  | 61.921 | 277.359 | 5.86 | 1623 |  |  |  | 61.92 | 533.41 | 0.147 | 78 | 4.64
346.06 | 277.424 | 5.84 | 1617 |  |  |  | 61.92 | 277.376 | 5.95 | 1619 |  |  |  | 61.921 | 277.359 | 5.86 | 1623 |  |  |  | 61.92 | 533.41 | 0.147 | 78 | 4.64
346.56 | 277.374 | 5.83 | 1611 |  |  |  | 61.921 | 277.576 | 5.94 | 1617 |  |  |  | 61.923 | 277.337 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.15 | 80 | 4.64
347.1 | 277.374 | 5.83 | 1611 |  |  |  | 61.921 | 277.576 | 5.94 | 1617 |  |  |  | 61.923 | 277.337 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.15 | 80 | 4.64
347.6 | 277.44 | 5.82 | 1610 |  |  |  | 61.92 | 277.413 | 5.96 | 1624 |  |  |  | 61.919 | 277.303 | 5.86 | 1622 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 4.64
348.09 | 277.44 | 5.82 | 1610 |  |  |  | 61.92 | 277.413 | 5.96 | 1624 |  |  |  | 61.919 | 277.303 | 5.86 | 1622 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 4.64
348.59 | 277.366 | 5.8 | 1604 |  |  |  | 61.921 | 277.396 | 5.91 | 1608 |  |  |  | 61.919 | 277.263 | 5.82 | 1612 |  |  |  | 61.921 | 527.73 | 0.152 | 80 | 4.64
349.06 | 277.366 | 5.8 | 1604 |  |  |  | 61.921 | 277.396 | 5.91 | 1608 |  |  |  | 61.919 | 277.263 | 5.82 | 1612 |  |  |  | 61.921 | 527.73 | 0.152 | 80 | 4.64
349.56 | 277.441 | 5.81 | 1607 |  |  |  | 61.921 | 277.493 | 5.9 | 1608 |  |  |  | 61.921 | 277.353 | 5.8 | 1607 |  |  |  | 61.92 | 526.98 | 0.154 | 81 | 4.64
350.11 | 277.331 | 5.83 | 1611 |  |  |  | 61.917 | 277.351 | 5.95 | 1621 |  |  |  | 61.92 | 277.331 | 5.84 | 1616 |  |  |  | 61.921 | 532.86 | 0.153 | 81 | 4.64
350.61 | 277.331 | 5.83 | 1611 |  |  |  | 61.917 | 277.351 | 5.95 | 1621 |  |  |  | 61.92 | 277.331 | 5.84 | 1616 |  |  |  | 61.921 | 532.86 | 0.153 | 81 | 4.64
351.09 | 277.402 | 5.82 | 1611 |  |  |  | 61.92 | 277.546 | 5.95 | 1622 |  |  |  | 61.92 | 277.306 | 5.86 | 1622 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 4.64
351.59 | 277.402 | 5.82 | 1611 |  |  |  | 61.92 | 277.546 | 5.95 | 1622 |  |  |  | 61.92 | 277.306 | 5.86 | 1622 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 4.64
352.07 | 277.469 | 5.84 | 1617 |  |  |  | 61.919 | 277.37 | 5.94 | 1617 |  |  |  | 61.921 | 277.27 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.153 | 82 | 4.64
352.57 | 277.469 | 5.84 | 1617 |  |  |  | 61.919 | 277.37 | 5.94 | 1617 |  |  |  | 61.921 | 277.27 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.153 | 82 | 4.64
353.06 | 277.374 | 5.83 | 1613 |  |  |  | 61.921 | 277.563 | 5.95 | 1621 |  |  |  | 61.922 | 277.347 | 5.85 | 1619 |  |  |  | 61.921 | 533.44 | 0.148 | 79 | 4.64
353.56 | 277.374 | 5.83 | 1613 |  |  |  | 61.921 | 277.563 | 5.95 | 1621 |  |  |  | 61.922 | 277.347 | 5.85 | 1619 |  |  |  | 61.921 | 533.44 | 0.148 | 79 | 4.64
354.06 | 277.436 | 5.76 | 1592 |  |  |  | 61.92 | 277.406 | 5.88 | 1601 |  |  |  | 61.919 | 277.337 | 5.77 | 1599 |  |  |  | 61.921 | 539.07 | 0.152 | 82 | 4.64
354.56 | 277.436 | 5.76 | 1592 |  |  |  | 61.92 | 277.406 | 5.88 | 1601 |  |  |  | 61.919 | 277.337 | 5.77 | 1599 |  |  |  | 61.921 | 539.07 | 0.152 | 82 | 4.64
355.06 | 277.365 | 5.65 | 1561 |  |  |  | 61.92 | 277.315 | 5.75 | 1564 |  |  |  | 61.92 | 277.319 | 5.66 | 1566 |  |  |  | 61.919 | 539.86 | 0.153 | 83 | 4.64
355.56 | 277.365 | 5.65 | 1561 |  |  |  | 61.92 | 277.315 | 5.75 | 1564 |  |  |  | 61.92 | 277.319 | 5.66 | 1566 |  |  |  | 61.919 | 539.86 | 0.153 | 83 | 4.64
356.06 | 277.431 | 5.84 | 1615 |  |  |  | 61.921 | 277.447 | 5.95 | 1622 |  |  |  | 61.92 | 277.286 | 5.85 | 1620 |  |  |  | 61.92 | 534.03 | 0.151 | 80 | 4.64
356.57 | 277.431 | 5.84 | 1615 |  |  |  | 61.921 | 277.447 | 5.95 | 1622 |  |  |  | 61.92 | 277.286 | 5.85 | 1620 |  |  |  | 61.92 | 534.03 | 0.151 | 80 | 4.64
357.06 | 277.349 | 5.83 | 1613 |  |  |  | 61.92 | 277.345 | 5.95 | 1621 |  |  |  | 61.919 | 277.256 | 5.84 | 1617 |  |  |  | 61.921 | 533.36 | 0.15 | 80 | 4.64
357.56 | 277.349 | 5.83 | 1613 |  |  |  | 61.92 | 277.345 | 5.95 | 1621 |  |  |  | 61.919 | 277.256 | 5.84 | 1617 |  |  |  | 61.921 | 533.36 | 0.15 | 80 | 4.64
358.06 | 277.432 | 5.83 | 1612 |  |  |  | 61.921 | 277.489 | 5.95 | 1621 |  |  |  | 61.92 | 277.354 | 5.85 | 1619 |  |  |  | 61.92 | 533.39 | 0.154 | 82 | 4.64
358.56 | 277.432 | 5.83 | 1612 |  |  |  | 61.921 | 277.489 | 5.95 | 1621 |  |  |  | 61.92 | 277.354 | 5.85 | 1619 |  |  |  | 61.92 | 533.39 | 0.154 | 82 | 4.64
359.06 | 277.335 | 5.84 | 1615 |  |  |  | 61.918 | 277.343 | 5.94 | 1617 |  |  |  | 61.921 | 277.334 | 5.87 | 1625 |  |  |  | 61.921 | 533.43 | 0.15 | 80 | 4.64
359.56 | 277.335 | 5.84 | 1615 |  |  |  | 61.918 | 277.343 | 5.94 | 1617 |  |  |  | 61.921 | 277.334 | 5.87 | 1625 |  |  |  | 61.921 | 533.43 | 0.15 | 80 | 4.64
360.06 | 277.395 | 5.8 | 1604 |  |  |  | 61.921 | 277.538 | 5.9 | 1609 |  |  |  | 61.923 | 277.301 | 5.83 | 1615 |  |  |  | 61.921 | 527.75 | 0.148 | 78 | 4.64
360.56 | 277.395 | 5.8 | 1604 |  |  |  | 61.921 | 277.538 | 5.9 | 1609 |  |  |  | 61.923 | 277.301 | 5.83 | 1615 |  |  |  | 61.921 | 527.75 | 0.148 | 78 | 4.64
361.06 | 277.463 | 5.8 | 1606 |  |  |  | 61.92 | 277.413 | 5.91 | 1609 |  |  |  | 61.919 | 277.262 | 5.79 | 1604 |  |  |  | 61.921 | 526.99 | 0.152 | 80 | 4.64
361.56 | 277.463 | 5.8 | 1606 |  |  |  | 61.92 | 277.413 | 5.91 | 1609 |  |  |  | 61.919 | 277.262 | 5.79 | 1604 |  |  |  | 61.921 | 526.99 | 0.152 | 80 | 4.64
362.06 | 277.38 | 5.82 | 1610 |  |  |  | 61.921 | 277.275 | 5.95 | 1619 |  |  |  | 61.92 | 277.374 | 5.85 | 1621 |  |  |  | 61.92 | 532.82 | 0.152 | 81 | 4.64
362.57 | 277.38 | 5.82 | 1610 |  |  |  | 61.921 | 277.275 | 5.95 | 1619 |  |  |  | 61.92 | 277.374 | 5.85 | 1621 |  |  |  | 61.92 | 532.82 | 0.152 | 81 | 4.64
363.06 | 277.441 | 5.83 | 1614 |  |  |  | 61.919 | 277.445 | 5.93 | 1617 |  |  |  | 61.921 | 277.348 | 5.87 | 1625 |  |  |  | 61.921 | 533.44 | 0.151 | 80 | 4.64
363.56 | 277.441 | 5.83 | 1614 |  |  |  | 61.919 | 277.445 | 5.93 | 1617 |  |  |  | 61.921 | 277.348 | 5.87 | 1625 |  |  |  | 61.921 | 533.44 | 0.151 | 80 | 4.64
364.06 | 277.377 | 5.85 | 1619 |  |  |  | 61.92 | 277.326 | 5.94 | 1618 |  |  |  | 61.92 | 277.318 | 5.85 | 1619 |  |  |  | 61.919 | 533.38 | 0.148 | 79 | 4.64
364.56 | 277.377 | 5.85 | 1619 |  |  |  | 61.92 | 277.326 | 5.94 | 1618 |  |  |  | 61.92 | 277.318 | 5.85 | 1619 |  |  |  | 61.919 | 533.38 | 0.148 | 79 | 4.64
365.06 | 277.431 | 5.82 | 1611 |  |  |  | 61.919 | 277.481 | 5.96 | 1621 |  |  |  | 61.919 | 277.279 | 5.84 | 1617 |  |  |  | 61.92 | 533.4 | 0.151 | 81 | 4.64
365.56 | 277.431 | 5.82 | 1611 |  |  |  | 61.919 | 277.481 | 5.96 | 1621 |  |  |  | 61.919 | 277.279 | 5.84 | 1617 |  |  |  | 61.92 | 533.4 | 0.151 | 81 | 4.64
366.06 | 277.348 | 5.76 | 1592 |  |  |  | 61.921 | 277.352 | 5.89 | 1605 |  |  |  | 61.921 | 277.365 | 5.79 | 1604 |  |  |  | 61.923 | 539.04 | 0.151 | 82 | 4.64
366.56 | 277.348 | 5.76 | 1592 |  |  |  | 61.921 | 277.352 | 5.89 | 1605 |  |  |  | 61.921 | 277.365 | 5.79 | 1604 |  |  |  | 61.923 | 539.04 | 0.151 | 82 | 4.64
367.06 | 277.42 | 5.65 | 1562 |  |  |  | 61.921 | 277.533 | 5.77 | 1569 |  |  |  | 61.923 | 277.34 | 5.66 | 1568 |  |  |  | 61.921 | 539.84 | 0.148 | 80 | 4.64
367.56 | 277.42 | 5.65 | 1562 |  |  |  | 61.921 | 277.533 | 5.77 | 1569 |  |  |  | 61.923 | 277.34 | 5.66 | 1568 |  |  |  | 61.921 | 539.84 | 0.148 | 80 | 4.64
368.07 | 277.333 | 5.84 | 1617 |  |  |  | 61.917 | 277.422 | 5.95 | 1621 |  |  |  | 61.919 | 277.327 | 5.86 | 1623 |  |  |  | 61.921 | 534.05 | 0.155 | 83 | 4.64
368.57 | 277.333 | 5.84 | 1617 |  |  |  | 61.917 | 277.422 | 5.95 | 1621 |  |  |  | 61.919 | 277.327 | 5.86 | 1623 |  |  |  | 61.921 | 534.05 | 0.155 | 83 | 4.64
369.06 | 277.401 | 5.83 | 1612 |  |  |  | 61.921 | 277.252 | 5.93 | 1616 |  |  |  | 61.92 | 277.292 | 5.86 | 1621 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 4.64
369.56 | 277.401 | 5.83 | 1612 |  |  |  | 61.921 | 277.252 | 5.93 | 1616 |  |  |  | 61.92 | 277.292 | 5.86 | 1621 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 4.64
370.06 | 277.459 | 5.83 | 1612 |  |  |  | 61.92 | 277.478 | 5.94 | 1620 |  |  |  | 61.92 | 277.248 | 5.85 | 1619 |  |  |  | 61.921 | 533.43 | 0.152 | 81 | 4.64
370.56 | 277.459 | 5.83 | 1612 |  |  |  | 61.92 | 277.478 | 5.94 | 1620 |  |  |  | 61.92 | 277.248 | 5.85 | 1619 |  |  |  | 61.921 | 533.43 | 0.152 | 81 | 4.64
371.06 | 277.387 | 5.82 | 1611 |  |  |  | 61.921 | 277.301 | 5.95 | 1620 |  |  |  | 61.919 | 277.359 | 5.85 | 1621 |  |  |  | 61.92 | 533.41 | 0.15 | 80 | 4.64
371.56 | 277.387 | 5.82 | 1611 |  |  |  | 61.921 | 277.301 | 5.95 | 1620 |  |  |  | 61.919 | 277.359 | 5.85 | 1621 |  |  |  | 61.92 | 533.41 | 0.15 | 80 | 4.64
372.06 | 277.438 | 5.79 | 1601 |  |  |  | 61.92 | 277.515 | 5.92 | 1614 |  |  |  | 61.921 | 277.322 | 5.82 | 1612 |  |  |  | 61.921 | 527.82 | 0.154 | 82 | 4.64
372.56 | 277.438 | 5.79 | 1601 |  |  |  | 61.92 | 277.515 | 5.92 | 1614 |  |  |  | 61.921 | 277.322 | 5.82 | 1612 |  |  |  | 61.921 | 527.82 | 0.154 | 82 | 4.64
373.06 | 277.37 | 5.79 | 1603 |  |  |  | 61.92 | 277.378 | 5.91 | 1608 |  |  |  | 61.921 | 277.301 | 5.8 | 1606 |  |  |  | 61.92 | 526.97 | 0.147 | 77 | 4.64
373.56 | 277.37 | 5.79 | 1603 |  |  |  | 61.92 | 277.378 | 5.91 | 1608 |  |  |  | 61.921 | 277.301 | 5.8 | 1606 |  |  |  | 61.92 | 526.97 | 0.147 | 77 | 4.64
374.07 | 277.433 | 5.82 | 1611 |  |  |  | 61.92 | 277.516 | 5.94 | 1616 |  |  |  | 61.919 | 277.27 | 5.83 | 1614 |  |  |  | 61.92 | 532.67 | 0.155 | 82 | 4.64
374.57 | 277.433 | 5.82 | 1611 |  |  |  | 61.92 | 277.516 | 5.94 | 1616 |  |  |  | 61.919 | 277.27 | 5.83 | 1614 |  |  |  | 61.92 | 532.67 | 0.155 | 82 | 4.64
375.06 | 277.348 | 5.82 | 1609 |  |  |  | 61.92 | 277.448 | 5.96 | 1622 |  |  |  | 61.919 | 277.365 | 5.84 | 1618 |  |  |  | 61.92 | 533.43 | 0.154 | 82 | 4.64
375.56 | 277.348 | 5.82 | 1609 |  |  |  | 61.92 | 277.448 | 5.96 | 1622 |  |  |  | 61.919 | 277.365 | 5.84 | 1618 |  |  |  | 61.92 | 533.43 | 0.154 | 82 | 4.64
376.06 | 277.42 | 5.83 | 1612 |  |  |  | 61.921 | 277.306 | 5.96 | 1622 |  |  |  | 61.92 | 277.324 | 5.85 | 1621 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
376.56 | 277.42 | 5.83 | 1612 |  |  |  | 61.921 | 277.306 | 5.96 | 1622 |  |  |  | 61.92 | 277.324 | 5.85 | 1621 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
377.06 | 277.347 | 5.83 | 1613 |  |  |  | 61.92 | 277.48 | 5.93 | 1613 |  |  |  | 61.92 | 277.297 | 5.86 | 1623 |  |  |  | 61.921 | 533.46 | 0.143 | 76 | 4.64
377.56 | 277.347 | 5.83 | 1613 |  |  |  | 61.92 | 277.48 | 5.93 | 1613 |  |  |  | 61.92 | 277.297 | 5.86 | 1623 |  |  |  | 61.921 | 533.46 | 0.143 | 76 | 4.64
378.06 | 277.385 | 5.78 | 1598 |  |  |  | 61.92 | 277.345 | 5.9 | 1604 |  |  |  | 61.92 | 277.274 | 5.81 | 1609 |  |  |  | 61.92 | 538.94 | 0.149 | 80 | 4.64
378.6 | 277.385 | 5.78 | 1598 |  |  |  | 61.92 | 277.345 | 5.9 | 1604 |  |  |  | 61.92 | 277.274 | 5.81 | 1609 |  |  |  | 61.92 | 538.94 | 0.149 | 80 | 4.64
379.1 | 277.438 | 5.65 | 1564 |  |  |  | 61.921 | 277.548 | 5.77 | 1568 |  |  |  | 61.923 | 277.374 | 5.68 | 1573 |  |  |  | 61.923 | 539.83 | 0.15 | 81 | 4.64
379.59 | 277.438 | 5.65 | 1564 |  |  |  | 61.921 | 277.548 | 5.77 | 1568 |  |  |  | 61.923 | 277.374 | 5.68 | 1573 |  |  |  | 61.923 | 539.83 | 0.15 | 81 | 4.64
380.09 | 277.38 | 5.84 | 1614 |  |  |  | 61.921 | 277.377 | 5.96 | 1622 |  |  |  | 61.92 | 277.353 | 5.86 | 1623 |  |  |  | 61.92 | 534.15 | 0.151 | 81 | 4.64
380.57 | 277.38 | 5.84 | 1614 |  |  |  | 61.921 | 277.377 | 5.96 | 1622 |  |  |  | 61.92 | 277.353 | 5.86 | 1623 |  |  |  | 61.92 | 534.15 | 0.151 | 81 | 4.64
381.07 | 277.433 | 5.82 | 1609 |  |  |  | 61.919 | 277.474 | 5.96 | 1623 |  |  |  | 61.921 | 277.315 | 5.84 | 1617 |  |  |  | 61.921 | 533.46 | 0.151 | 80 | 4.64
381.6 | 277.433 | 5.82 | 1609 |  |  |  | 61.919 | 277.474 | 5.96 | 1623 |  |  |  | 61.921 | 277.315 | 5.84 | 1617 |  |  |  | 61.921 | 533.46 | 0.151 | 80 | 4.64
382.1 | 277.384 | 5.82 | 1610 |  |  |  | 61.921 | 277.472 | 5.94 | 1616 |  |  |  | 61.92 | 277.278 | 5.86 | 1623 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 4.64
382.59 | 277.449 | 5.84 | 1616 |  |  |  | 61.921 | 277.329 | 5.95 | 1617 |  |  |  | 61.92 | 277.252 | 5.84 | 1617 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
383.09 | 277.449 | 5.84 | 1616 |  |  |  | 61.921 | 277.329 | 5.95 | 1617 |  |  |  | 61.92 | 277.252 | 5.84 | 1617 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
383.57 | 277.356 | 5.81 | 1606 |  |  |  | 61.921 | 277.552 | 5.93 | 1614 |  |  |  | 61.92 | 277.358 | 5.81 | 1608 |  |  |  | 61.919 | 527.93 | 0.152 | 80 | 4.64
384.07 | 277.356 | 5.81 | 1606 |  |  |  | 61.921 | 277.552 | 5.93 | 1614 |  |  |  | 61.92 | 277.358 | 5.81 | 1608 |  |  |  | 61.919 | 527.93 | 0.152 | 80 | 4.64
384.56 | 277.421 | 5.78 | 1599 |  |  |  | 61.921 | 277.408 | 5.92 | 1611 |  |  |  | 61.92 | 277.332 | 5.81 | 1608 |  |  |  | 61.921 | 526.94 | 0.151 | 80 | 4.64
385.06 | 277.421 | 5.78 | 1599 |  |  |  | 61.921 | 277.408 | 5.92 | 1611 |  |  |  | 61.92 | 277.332 | 5.81 | 1608 |  |  |  | 61.921 | 526.94 | 0.151 | 80 | 4.64
385.56 | 277.405 | 5.81 | 1608 |  |  |  | 61.921 | 277.561 | 5.93 | 1614 |  |  |  | 61.923 | 277.29 | 5.85 | 1619 |  |  |  | 61.92 | 532.69 | 0.152 | 81 | 4.64
386.07 | 277.405 | 5.81 | 1608 |  |  |  | 61.921 | 277.561 | 5.93 | 1614 |  |  |  | 61.923 | 277.29 | 5.85 | 1619 |  |  |  | 61.92 | 532.69 | 0.152 | 81 | 4.64
386.57 | 277.391 | 5.82 | 1611 |  |  |  | 61.921 | 277.441 | 5.95 | 1621 |  |  |  | 61.921 | 277.264 | 5.87 | 1625 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
387.06 | 277.391 | 5.82 | 1611 |  |  |  | 61.921 | 277.441 | 5.95 | 1621 |  |  |  | 61.921 | 277.264 | 5.87 | 1625 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
387.56 | 277.445 | 5.83 | 1613 |  |  |  | 61.92 | 277.374 | 5.95 | 1619 |  |  |  | 61.92 | 277.363 | 5.85 | 1619 |  |  |  | 61.919 | 533.45 | 0.15 | 80 | 4.64
388.06 | 277.445 | 5.83 | 1613 |  |  |  | 61.92 | 277.374 | 5.95 | 1619 |  |  |  | 61.92 | 277.363 | 5.85 | 1619 |  |  |  | 61.919 | 533.45 | 0.15 | 80 | 4.64
388.56 | 277.384 | 5.84 | 1614 |  |  |  | 61.921 | 277.479 | 5.96 | 1622 |  |  |  | 61.92 | 277.34 | 5.85 | 1620 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 4.64
389.06 | 277.384 | 5.84 | 1614 |  |  |  | 61.921 | 277.479 | 5.96 | 1622 |  |  |  | 61.92 | 277.34 | 5.85 | 1620 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 4.64
389.56 | 277.433 | 5.78 | 1600 |  |  |  | 61.92 | 277.37 | 5.89 | 1604 |  |  |  | 61.92 | 277.305 | 5.8 | 1605 |  |  |  | 61.92 | 538.89 | 0.149 | 80 | 4.64
390.06 | 277.433 | 5.78 | 1600 |  |  |  | 61.92 | 277.37 | 5.89 | 1604 |  |  |  | 61.92 | 277.305 | 5.8 | 1605 |  |  |  | 61.92 | 538.89 | 0.149 | 80 | 4.64
390.56 | 277.368 | 5.63 | 1556 |  |  |  | 61.92 | 277.519 | 5.76 | 1565 |  |  |  | 61.92 | 277.27 | 5.65 | 1565 |  |  |  | 61.921 | 539.89 | 0.156 | 84 | 4.64
391.06 | 277.368 | 5.63 | 1556 |  |  |  | 61.92 | 277.519 | 5.76 | 1565 |  |  |  | 61.92 | 277.27 | 5.65 | 1565 |  |  |  | 61.921 | 539.89 | 0.156 | 84 | 4.64
391.56 | 277.459 | 5.84 | 1615 |  |  |  | 61.92 | 277.375 | 5.95 | 1619 |  |  |  | 61.92 | 277.367 | 5.86 | 1624 |  |  |  | 61.923 | 534.18 | 0.151 | 81 | 4.64
392.07 | 277.459 | 5.84 | 1615 |  |  |  | 61.92 | 277.375 | 5.95 | 1619 |  |  |  | 61.92 | 277.367 | 5.86 | 1624 |  |  |  | 61.923 | 534.18 | 0.151 | 81 | 4.64
392.57 | 277.351 | 5.83 | 1613 |  |  |  | 61.919 | 277.581 | 5.95 | 1618 |  |  |  | 61.923 | 277.351 | 5.85 | 1619 |  |  |  | 61.92 | 533.36 | 0.152 | 81 | 4.64
393.06 | 277.351 | 5.83 | 1613 |  |  |  | 61.919 | 277.581 | 5.95 | 1618 |  |  |  | 61.923 | 277.351 | 5.85 | 1619 |  |  |  | 61.92 | 533.36 | 0.152 | 81 | 4.64
393.56 | 277.43 | 5.84 | 1615 |  |  |  | 61.921 | 277.454 | 5.95 | 1621 |  |  |  | 61.918 | 277.319 | 5.83 | 1614 |  |  |  | 61.92 | 533.39 | 0.152 | 81 | 4.64
394.06 | 277.43 | 5.84 | 1615 |  |  |  | 61.921 | 277.454 | 5.95 | 1621 |  |  |  | 61.918 | 277.319 | 5.83 | 1614 |  |  |  | 61.92 | 533.39 | 0.152 | 81 | 4.64
394.56 | 277.441 | 5.81 | 1608 |  |  |  | 61.92 | 277.31 | 5.95 | 1619 |  |  |  | 61.921 | 277.286 | 5.86 | 1622 |  |  |  | 61.92 | 533.46 | 0.149 | 79 | 4.64
395.06 | 277.441 | 5.81 | 1608 |  |  |  | 61.92 | 277.31 | 5.95 | 1619 |  |  |  | 61.921 | 277.286 | 5.86 | 1622 |  |  |  | 61.92 | 533.46 | 0.149 | 79 | 4.64
395.56 | 277.386 | 5.8 | 1603 |  |  |  | 61.921 | 277.474 | 5.93 | 1612 |  |  |  | 61.919 | 277.269 | 5.83 | 1615 |  |  |  | 61.921 | 527.93 | 0.151 | 80 | 4.64
396.06 | 277.386 | 5.8 | 1603 |  |  |  | 61.921 | 277.474 | 5.93 | 1612 |  |  |  | 61.919 | 277.269 | 5.83 | 1615 |  |  |  | 61.921 | 527.93 | 0.151 | 80 | 4.64
396.56 | 277.46 | 5.8 | 1605 |  |  |  | 61.92 | 277.355 | 5.9 | 1606 |  |  |  | 61.92 | 277.359 | 5.83 | 1614 |  |  |  | 61.92 | 526.97 | 0.155 | 82 | 4.64
397.06 | 277.46 | 5.8 | 1605 |  |  |  | 61.92 | 277.355 | 5.9 | 1606 |  |  |  | 61.92 | 277.359 | 5.83 | 1614 |  |  |  | 61.92 | 526.97 | 0.155 | 82 | 4.64
397.56 | 277.372 | 5.83 | 1613 |  |  |  | 61.921 | 277.539 | 5.93 | 1616 |  |  |  | 61.923 | 277.337 | 5.84 | 1617 |  |  |  | 61.921 | 532.61 | 0.154 | 82 | 4.64
398.07 | 277.372 | 5.83 | 1613 |  |  |  | 61.921 | 277.539 | 5.93 | 1616 |  |  |  | 61.923 | 277.337 | 5.84 | 1617 |  |  |  | 61.921 | 532.61 | 0.154 | 82 | 4.64
398.57 | 277.444 | 5.82 | 1611 |  |  |  | 61.92 | 277.408 | 5.96 | 1624 |  |  |  | 61.919 | 277.297 | 5.84 | 1617 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
399.06 | 277.444 | 5.82 | 1611 |  |  |  | 61.92 | 277.408 | 5.96 | 1624 |  |  |  | 61.919 | 277.297 | 5.84 | 1617 |  |  |  | 61.92 | 533.45 | 0.152 | 81 | 4.64
399.56 | 277.364 | 5.82 | 1610 |  |  |  | 61.92 | 277.484 | 5.95 | 1620 |  |  |  | 61.919 | 277.27 | 5.84 | 1617 |  |  |  | 61.921 | 533.43 | 0.149 | 80 | 4.64
400.06 | 277.364 | 5.82 | 1610 |  |  |  | 61.92 | 277.484 | 5.95 | 1620 |  |  |  | 61.919 | 277.27 | 5.84 | 1617 |  |  |  | 61.921 | 533.43 | 0.149 | 80 | 4.64
400.56 | 277.437 | 5.81 | 1609 |  |  |  | 61.92 | 277.418 | 5.95 | 1619 |  |  |  | 61.92 | 277.363 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.152 | 81 | 4.64
401.06 | 277.437 | 5.81 | 1609 |  |  |  | 61.92 | 277.418 | 5.95 | 1619 |  |  |  | 61.92 | 277.363 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.152 | 81 | 4.64
401.56 | 277.34 | 5.8 | 1603 |  |  |  | 61.919 | 277.259 | 5.88 | 1600 |  |  |  | 61.921 | 277.343 | 5.8 | 1608 |  |  |  | 61.92 | 538.82 | 0.15 | 81 | 4.64
402.06 | 277.34 | 5.8 | 1603 |  |  |  | 61.919 | 277.259 | 5.88 | 1600 |  |  |  | 61.921 | 277.343 | 5.8 | 1608 |  |  |  | 61.92 | 538.82 | 0.15 | 81 | 4.64
402.56 | 277.398 | 5.66 | 1565 |  |  |  | 61.92 | 277.476 | 5.78 | 1572 |  |  |  | 61.919 | 277.307 | 5.66 | 1568 |  |  |  | 61.92 | 539.84 | 0.148 | 80 | 4.64
403.06 | 277.398 | 5.66 | 1565 |  |  |  | 61.92 | 277.476 | 5.78 | 1572 |  |  |  | 61.919 | 277.307 | 5.66 | 1568 |  |  |  | 61.92 | 539.84 | 0.148 | 80 | 4.64
403.56 | 277.458 | 5.82 | 1609 |  |  |  | 61.92 | 277.294 | 5.96 | 1623 |  |  |  | 61.92 | 277.274 | 5.87 | 1626 |  |  |  | 61.92 | 534.25 | 0.148 | 79 | 4.64
404.07 | 277.458 | 5.82 | 1609 |  |  |  | 61.92 | 277.294 | 5.96 | 1623 |  |  |  | 61.92 | 277.274 | 5.87 | 1626 |  |  |  | 61.92 | 534.25 | 0.148 | 79 | 4.64
404.57 | 277.396 | 5.84 | 1615 |  |  |  | 61.921 | 277.522 | 5.94 | 1619 |  |  |  | 61.922 | 277.369 | 5.86 | 1622 |  |  |  | 61.923 | 533.42 | 0.147 | 78 | 4.64
405.06 | 277.396 | 5.84 | 1615 |  |  |  | 61.921 | 277.522 | 5.94 | 1619 |  |  |  | 61.922 | 277.369 | 5.86 | 1622 |  |  |  | 61.923 | 533.42 | 0.147 | 78 | 4.64
405.56 | 277.456 | 5.83 | 1613 |  |  |  | 61.92 | 277.35 | 5.94 | 1616 |  |  |  | 61.921 | 277.35 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.151 | 80 | 4.64
406.06 | 277.456 | 5.83 | 1613 |  |  |  | 61.92 | 277.35 | 5.94 | 1616 |  |  |  | 61.921 | 277.35 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.151 | 80 | 4.64
406.56 | 277.389 | 5.82 | 1610 |  |  |  | 61.921 | 277.357 | 5.94 | 1616 |  |  |  | 61.919 | 277.328 | 5.83 | 1615 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
407.06 | 277.389 | 5.82 | 1610 |  |  |  | 61.921 | 277.357 | 5.94 | 1616 |  |  |  | 61.919 | 277.328 | 5.83 | 1615 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
407.56 | 277.438 | 5.8 | 1605 |  |  |  | 61.919 | 277.453 | 5.94 | 1617 |  |  |  | 61.919 | 277.28 | 5.82 | 1612 |  |  |  | 61.92 | 528.02 | 0.15 | 79 | 4.64
408.06 | 277.438 | 5.8 | 1605 |  |  |  | 61.919 | 277.453 | 5.94 | 1617 |  |  |  | 61.919 | 277.28 | 5.82 | 1612 |  |  |  | 61.92 | 528.02 | 0.15 | 79 | 4.64
408.56 | 277.357 | 5.8 | 1604 |  |  |  | 61.921 | 277.314 | 5.91 | 1606 |  |  |  | 61.921 | 277.243 | 5.81 | 1610 |  |  |  | 61.921 | 526.96 | 0.15 | 79 | 4.64
409.06 | 277.357 | 5.8 | 1604 |  |  |  | 61.921 | 277.314 | 5.91 | 1606 |  |  |  | 61.921 | 277.243 | 5.81 | 1610 |  |  |  | 61.921 | 526.96 | 0.15 | 79 | 4.64
409.56 | 277.432 | 5.84 | 1614 |  |  |  | 61.921 | 277.437 | 5.94 | 1617 |  |  |  | 61.918 | 277.347 | 5.84 | 1618 |  |  |  | 61.921 | 532.61 | 0.15 | 80 | 4.64
410.1 | 277.432 | 5.84 | 1614 |  |  |  | 61.921 | 277.437 | 5.94 | 1617 |  |  |  | 61.918 | 277.347 | 5.84 | 1618 |  |  |  | 61.921 | 532.61 | 0.15 | 80 | 4.64
410.6 | 277.336 | 5.83 | 1614 |  |  |  | 61.919 | 277.306 | 5.97 | 1624 |  |  |  | 61.921 | 277.327 | 5.84 | 1617 |  |  |  | 61.921 | 533.42 | 0.151 | 81 | 4.64
411.09 | 277.336 | 5.83 | 1614 |  |  |  | 61.919 | 277.306 | 5.97 | 1624 |  |  |  | 61.921 | 277.327 | 5.84 | 1617 |  |  |  | 61.921 | 533.42 | 0.151 | 81 | 4.64
411.59 | 277.416 | 5.81 | 1609 |  |  |  | 61.921 | 277.534 | 5.96 | 1623 |  |  |  | 61.923 | 277.293 | 5.86 | 1621 |  |  |  | 61.919 | 533.41 | 0.151 | 81 | 4.64
412.07 | 277.416 | 5.81 | 1609 |  |  |  | 61.921 | 277.534 | 5.96 | 1623 |  |  |  | 61.923 | 277.293 | 5.86 | 1621 |  |  |  | 61.919 | 533.41 | 0.151 | 81 | 4.64
412.57 | 277.485 | 5.83 | 1615 |  |  |  | 61.92 | 277.375 | 5.92 | 1614 |  |  |  | 61.92 | 277.257 | 5.85 | 1621 |  |  |  | 61.921 | 533.45 | 0.148 | 79 | 4.64
413.06 | 277.485 | 5.83 | 1615 |  |  |  | 61.92 | 277.375 | 5.92 | 1614 |  |  |  | 61.92 | 277.257 | 5.85 | 1621 |  |  |  | 61.921 | 533.45 | 0.148 | 79 | 4.64
413.56 | 277.398 | 5.78 | 1599 |  |  |  | 61.921 | 277.326 | 5.91 | 1607 |  |  |  | 61.919 | 277.364 | 5.8 | 1608 |  |  |  | 61.921 | 538.82 | 0.15 | 81 | 4.64
414.09 | 277.44 | 5.65 | 1562 |  |  |  | 61.92 | 277.485 | 5.75 | 1564 |  |  |  | 61.92 | 277.345 | 5.66 | 1568 |  |  |  | 61.921 | 539.84 | 0.149 | 81 | 4.64
414.59 | 277.44 | 5.65 | 1562 |  |  |  | 61.92 | 277.485 | 5.75 | 1564 |  |  |  | 61.92 | 277.345 | 5.66 | 1568 |  |  |  | 61.921 | 539.84 | 0.149 | 81 | 4.64
415.07 | 277.377 | 5.83 | 1614 |  |  |  | 61.92 | 277.338 | 5.96 | 1621 |  |  |  | 61.92 | 277.318 | 5.85 | 1619 |  |  |  | 61.92 | 534.32 | 0.146 | 78 | 4.64
415.57 | 277.377 | 5.83 | 1614 |  |  |  | 61.92 | 277.338 | 5.96 | 1621 |  |  |  | 61.92 | 277.318 | 5.85 | 1619 |  |  |  | 61.92 | 534.32 | 0.146 | 78 | 4.64
416.07 | 277.435 | 5.85 | 1618 |  |  |  | 61.92 | 277.544 | 5.95 | 1620 |  |  |  | 61.92 | 277.284 | 5.84 | 1617 |  |  |  | 61.921 | 533.45 | 0.146 | 78 | 4.64
416.57 | 277.435 | 5.85 | 1618 |  |  |  | 61.92 | 277.544 | 5.95 | 1620 |  |  |  | 61.92 | 277.284 | 5.84 | 1617 |  |  |  | 61.921 | 533.45 | 0.146 | 78 | 4.64
417.06 | 277.351 | 5.83 | 1612 |  |  |  | 61.921 | 277.415 | 5.96 | 1623 |  |  |  | 61.92 | 277.37 | 5.84 | 1618 |  |  |  | 61.923 | 533.43 | 0.149 | 79 | 4.64
417.56 | 277.351 | 5.83 | 1612 |  |  |  | 61.921 | 277.415 | 5.96 | 1623 |  |  |  | 61.92 | 277.37 | 5.84 | 1618 |  |  |  | 61.923 | 533.43 | 0.149 | 79 | 4.64
418.06 | 277.436 | 5.82 | 1610 |  |  |  | 61.92 | 277.523 | 5.94 | 1619 |  |  |  | 61.923 | 277.35 | 5.86 | 1622 |  |  |  | 61.92 | 533.4 | 0.149 | 80 | 4.64
418.56 | 277.436 | 5.82 | 1610 |  |  |  | 61.92 | 277.523 | 5.94 | 1619 |  |  |  | 61.923 | 277.35 | 5.86 | 1622 |  |  |  | 61.92 | 533.4 | 0.149 | 80 | 4.64
419.06 | 277.35 | 5.8 | 1605 |  |  |  | 61.921 | 277.399 | 5.92 | 1611 |  |  |  | 61.92 | 277.327 | 5.83 | 1616 |  |  |  | 61.92 | 528.15 | 0.15 | 79 | 4.64
419.56 | 277.35 | 5.8 | 1605 |  |  |  | 61.921 | 277.399 | 5.92 | 1611 |  |  |  | 61.92 | 277.327 | 5.83 | 1616 |  |  |  | 61.92 | 528.15 | 0.15 | 79 | 4.64
420.06 | 277.414 | 5.8 | 1604 |  |  |  | 61.919 | 277.318 | 5.91 | 1609 |  |  |  | 61.92 | 277.298 | 5.8 | 1607 |  |  |  | 61.92 | 526.98 | 0.155 | 82 | 4.64
420.56 | 277.414 | 5.8 | 1604 |  |  |  | 61.919 | 277.318 | 5.91 | 1609 |  |  |  | 61.92 | 277.298 | 5.8 | 1607 |  |  |  | 61.92 | 526.98 | 0.155 | 82 | 4.64
421.06 | 277.472 | 5.8 | 1606 |  |  |  | 61.921 | 277.448 | 5.93 | 1615 |  |  |  | 61.92 | 277.254 | 5.83 | 1614 |  |  |  | 61.921 | 532.5 | 0.148 | 79 | 4.64
421.56 | 277.472 | 5.8 | 1606 |  |  |  | 61.921 | 277.448 | 5.93 | 1615 |  |  |  | 61.92 | 277.254 | 5.83 | 1614 |  |  |  | 61.921 | 532.5 | 0.148 | 79 | 4.64
422.07 | 277.385 | 5.81 | 1606 |  |  |  | 61.921 | 277.355 | 5.94 | 1620 |  |  |  | 61.919 | 277.37 | 5.85 | 1621 |  |  |  | 61.919 | 533.43 | 0.154 | 82 | 4.64
422.57 | 277.385 | 5.81 | 1606 |  |  |  | 61.921 | 277.355 | 5.94 | 1620 |  |  |  | 61.919 | 277.37 | 5.85 | 1621 |  |  |  | 61.919 | 533.43 | 0.154 | 82 | 4.64
423.06 | 277.454 | 5.82 | 1611 |  |  |  | 61.921 | 277.54 | 5.94 | 1619 |  |  |  | 61.919 | 277.335 | 5.85 | 1619 |  |  |  | 61.92 | 533.4 | 0.155 | 83 | 4.64
423.56 | 277.454 | 5.82 | 1611 |  |  |  | 61.921 | 277.54 | 5.94 | 1619 |  |  |  | 61.919 | 277.335 | 5.85 | 1619 |  |  |  | 61.92 | 533.4 | 0.155 | 83 | 4.64
424.06 | 277.378 | 5.84 | 1615 |  |  |  | 61.92 | 277.391 | 5.96 | 1623 |  |  |  | 61.919 | 277.305 | 5.85 | 1620 |  |  |  | 61.919 | 533.4 | 0.146 | 78 | 4.64
424.56 | 277.378 | 5.84 | 1615 |  |  |  | 61.92 | 277.391 | 5.96 | 1623 |  |  |  | 61.919 | 277.305 | 5.85 | 1620 |  |  |  | 61.919 | 533.4 | 0.146 | 78 | 4.64
425.06 | 277.444 | 5.76 | 1594 |  |  |  | 61.92 | 277.584 | 5.9 | 1606 |  |  |  | 61.922 | 277.267 | 5.81 | 1608 |  |  |  | 61.921 | 538.66 | 0.151 | 81 | 4.64
425.56 | 277.444 | 5.76 | 1594 |  |  |  | 61.92 | 277.584 | 5.9 | 1606 |  |  |  | 61.922 | 277.267 | 5.81 | 1608 |  |  |  | 61.921 | 538.66 | 0.151 | 81 | 4.64
426.06 | 277.351 | 5.62 | 1556 |  |  |  | 61.92 | 277.506 | 5.73 | 1560 |  |  |  | 61.92 | 277.353 | 5.65 | 1565 |  |  |  | 61.92 | 539.91 | 0.146 | 79 | 4.64
426.56 | 277.351 | 5.62 | 1556 |  |  |  | 61.92 | 277.506 | 5.73 | 1560 |  |  |  | 61.92 | 277.353 | 5.65 | 1565 |  |  |  | 61.92 | 539.91 | 0.146 | 79 | 4.64
427.06 | 277.431 | 5.83 | 1613 |  |  |  | 61.92 | 277.338 | 5.96 | 1623 |  |  |  | 61.92 | 277.332 | 5.87 | 1627 |  |  |  | 61.92 | 534.4 | 0.152 | 81 | 4.64
427.56 | 277.431 | 5.83 | 1613 |  |  |  | 61.92 | 277.338 | 5.96 | 1623 |  |  |  | 61.92 | 277.332 | 5.87 | 1627 |  |  |  | 61.92 | 534.4 | 0.152 | 81 | 4.64
428.07 | 277.343 | 5.83 | 1613 |  |  |  | 61.918 | 277.506 | 5.94 | 1618 |  |  |  | 61.921 | 277.304 | 5.85 | 1620 |  |  |  | 61.921 | 533.46 | 0.151 | 80 | 4.64
428.57 | 277.343 | 5.83 | 1613 |  |  |  | 61.918 | 277.506 | 5.94 | 1618 |  |  |  | 61.921 | 277.304 | 5.85 | 1620 |  |  |  | 61.921 | 533.46 | 0.151 | 80 | 4.64
429.06 | 277.4 | 5.84 | 1615 |  |  |  | 61.921 | 277.352 | 5.95 | 1618 |  |  |  | 61.919 | 277.284 | 5.85 | 1618 |  |  |  | 61.92 | 533.46 | 0.146 | 78 | 4.64
429.56 | 277.4 | 5.84 | 1615 |  |  |  | 61.921 | 277.352 | 5.95 | 1618 |  |  |  | 61.919 | 277.284 | 5.85 | 1618 |  |  |  | 61.92 | 533.46 | 0.146 | 78 | 4.64
430.06 | 277.461 | 5.81 | 1606 |  |  |  | 61.92 | 277.542 | 5.95 | 1621 |  |  |  | 61.923 | 277.376 | 5.84 | 1617 |  |  |  | 61.923 | 533.45 | 0.146 | 78 | 4.64
430.56 | 277.461 | 5.81 | 1606 |  |  |  | 61.92 | 277.542 | 5.95 | 1621 |  |  |  | 61.923 | 277.376 | 5.84 | 1617 |  |  |  | 61.923 | 533.45 | 0.146 | 78 | 4.64
431.06 | 277.394 | 5.8 | 1604 |  |  |  | 61.92 | 277.414 | 5.92 | 1611 |  |  |  | 61.92 | 277.34 | 5.84 | 1618 |  |  |  | 61.92 | 528.26 | 0.145 | 77 | 4.64
431.56 | 277.394 | 5.8 | 1604 |  |  |  | 61.92 | 277.414 | 5.92 | 1611 |  |  |  | 61.92 | 277.34 | 5.84 | 1618 |  |  |  | 61.92 | 528.26 | 0.145 | 77 | 4.64
432.06 | 277.449 | 5.79 | 1603 |  |  |  | 61.92 | 277.544 | 5.91 | 1609 |  |  |  | 61.92 | 277.306 | 5.81 | 1610 |  |  |  | 61.921 | 526.96 | 0.149 | 78 | 4.64
432.56 | 277.449 | 5.79 | 1603 |  |  |  | 61.92 | 277.544 | 5.91 | 1609 |  |  |  | 61.92 | 277.306 | 5.81 | 1610 |  |  |  | 61.921 | 526.96 | 0.149 | 78 | 4.64
433.06 | 277.38 | 5.82 | 1611 |  |  |  | 61.921 | 277.425 | 5.94 | 1617 |  |  |  | 61.919 | 277.288 | 5.85 | 1619 |  |  |  | 61.92 | 532.5 | 0.144 | 77 | 4.64
433.56 | 277.38 | 5.82 | 1611 |  |  |  | 61.921 | 277.425 | 5.94 | 1617 |  |  |  | 61.919 | 277.288 | 5.85 | 1619 |  |  |  | 61.92 | 532.5 | 0.144 | 77 | 4.64
434.07 | 277.443 | 5.83 | 1612 |  |  |  | 61.92 | 277.269 | 5.96 | 1621 |  |  |  | 61.919 | 277.26 | 5.85 | 1620 |  |  |  | 61.92 | 533.46 | 0.149 | 80 | 4.64
434.57 | 277.443 | 5.83 | 1612 |  |  |  | 61.92 | 277.269 | 5.96 | 1621 |  |  |  | 61.919 | 277.26 | 5.85 | 1620 |  |  |  | 61.92 | 533.46 | 0.149 | 80 | 4.64
435.06 | 277.359 | 5.82 | 1609 |  |  |  | 61.919 | 277.519 | 5.95 | 1620 |  |  |  | 61.92 | 277.351 | 5.86 | 1622 |  |  |  | 61.919 | 533.45 | 0.149 | 80 | 4.64
435.56 | 277.359 | 5.82 | 1609 |  |  |  | 61.919 | 277.519 | 5.95 | 1620 |  |  |  | 61.92 | 277.351 | 5.86 | 1622 |  |  |  | 61.919 | 533.45 | 0.149 | 80 | 4.64
436.06 | 277.427 | 5.82 | 1611 |  |  |  | 61.921 | 277.347 | 5.95 | 1619 |  |  |  | 61.92 | 277.319 | 5.83 | 1615 |  |  |  | 61.92 | 533.45 | 0.149 | 79 | 4.64
436.56 | 277.427 | 5.82 | 1611 |  |  |  | 61.921 | 277.347 | 5.95 | 1619 |  |  |  | 61.92 | 277.319 | 5.83 | 1615 |  |  |  | 61.92 | 533.45 | 0.149 | 79 | 4.64
437.06 | 277.339 | 5.8 | 1605 |  |  |  | 61.917 | 277.552 | 5.89 | 1603 |  |  |  | 61.923 | 277.286 | 5.82 | 1612 |  |  |  | 61.92 | 538.62 | 0.147 | 79 | 4.64
437.56 | 277.339 | 5.8 | 1605 |  |  |  | 61.917 | 277.552 | 5.89 | 1603 |  |  |  | 61.923 | 277.286 | 5.82 | 1612 |  |  |  | 61.92 | 538.62 | 0.147 | 79 | 4.64
438.06 | 277.388 | 5.64 | 1560 |  |  |  | 61.92 | 277.42 | 5.77 | 1567 |  |  |  | 61.92 | 277.267 | 5.64 | 1562 |  |  |  | 61.921 | 539.88 | 0.149 | 80 | 4.64
438.56 | 277.388 | 5.64 | 1560 |  |  |  | 61.92 | 277.42 | 5.77 | 1567 |  |  |  | 61.92 | 277.267 | 5.64 | 1562 |  |  |  | 61.921 | 539.88 | 0.149 | 80 | 4.64
439.06 | 277.451 | 5.82 | 1611 |  |  |  | 61.921 | 277.384 | 5.97 | 1624 |  |  |  | 61.92 | 277.379 | 5.85 | 1621 |  |  |  | 61.92 | 534.44 | 0.144 | 77 | 4.64
439.56 | 277.451 | 5.82 | 1611 |  |  |  | 61.921 | 277.384 | 5.97 | 1624 |  |  |  | 61.92 | 277.379 | 5.85 | 1621 |  |  |  | 61.92 | 534.44 | 0.144 | 77 | 4.64
440.07 | 277.402 | 5.81 | 1608 |  |  |  | 61.921 | 277.476 | 5.95 | 1622 |  |  |  | 61.921 | 277.347 | 5.86 | 1624 |  |  |  | 61.921 | 533.45 | 0.148 | 79 | 4.64
440.57 | 277.402 | 5.81 | 1608 |  |  |  | 61.921 | 277.476 | 5.95 | 1622 |  |  |  | 61.921 | 277.347 | 5.86 | 1624 |  |  |  | 61.921 | 533.45 | 0.148 | 79 | 4.64
441.06 | 277.458 | 5.82 | 1610 |  |  |  | 61.921 | 277.31 | 5.95 | 1619 |  |  |  | 61.92 | 277.308 | 5.86 | 1622 |  |  |  | 61.919 | 533.46 | 0.149 | 79 | 4.64
441.56 | 277.458 | 5.82 | 1610 |  |  |  | 61.921 | 277.31 | 5.95 | 1619 |  |  |  | 61.92 | 277.308 | 5.86 | 1622 |  |  |  | 61.919 | 533.46 | 0.149 | 79 | 4.64
442.06 | 277.392 | 5.84 | 1616 |  |  |  | 61.921 | 277.472 | 5.94 | 1617 |  |  |  | 61.92 | 277.28 | 5.84 | 1617 |  |  |  | 61.92 | 533.45 | 0.148 | 79 | 4.64
442.59 | 277.392 | 5.84 | 1616 |  |  |  | 61.921 | 277.472 | 5.94 | 1617 |  |  |  | 61.92 | 277.28 | 5.84 | 1617 |  |  |  | 61.92 | 533.45 | 0.148 | 79 | 4.64
443.09 | 277.45 | 5.82 | 1610 |  |  |  | 61.92 | 277.331 | 5.93 | 1614 |  |  |  | 61.92 | 277.374 | 5.82 | 1612 |  |  |  | 61.922 | 528.24 | 0.142 | 75 | 4.64
443.57 | 277.45 | 5.82 | 1610 |  |  |  | 61.92 | 277.331 | 5.93 | 1614 |  |  |  | 61.92 | 277.374 | 5.82 | 1612 |  |  |  | 61.922 | 528.24 | 0.142 | 75 | 4.64
444.07 | 277.344 | 5.78 | 1597 |  |  |  | 61.92 | 277.56 | 5.92 | 1611 |  |  |  | 61.923 | 277.363 | 5.8 | 1605 |  |  |  | 61.92 | 526.98 | 0.145 | 77 | 4.64
444.56 | 277.344 | 5.78 | 1597 |  |  |  | 61.92 | 277.56 | 5.92 | 1611 |  |  |  | 61.923 | 277.363 | 5.8 | 1605 |  |  |  | 61.92 | 526.98 | 0.145 | 77 | 4.64
445.06 | 277.426 | 5.82 | 1609 |  |  |  | 61.921 | 277.378 | 5.94 | 1617 |  |  |  | 61.92 | 277.331 | 5.83 | 1615 |  |  |  | 61.919 | 532.41 | 0.149 | 79 | 4.64
445.6 | 277.322 | 5.82 | 1610 |  |  |  | 61.917 | 277.295 | 5.94 | 1617 |  |  |  | 61.92 | 277.292 | 5.87 | 1625 |  |  |  | 61.919 | 533.46 | 0.149 | 80 | 4.64
446.1 | 277.322 | 5.82 | 1610 |  |  |  | 61.917 | 277.295 | 5.94 | 1617 |  |  |  | 61.92 | 277.292 | 5.87 | 1625 |  |  |  | 61.919 | 533.46 | 0.149 | 80 | 4.64
446.57 | 277.387 | 5.83 | 1614 |  |  |  | 61.921 | 277.439 | 5.95 | 1620 |  |  |  | 61.919 | 277.259 | 5.85 | 1619 |  |  |  | 61.92 | 533.48 | 0.145 | 78 | 4.64
447.07 | 277.387 | 5.83 | 1614 |  |  |  | 61.921 | 277.439 | 5.95 | 1620 |  |  |  | 61.919 | 277.259 | 5.85 | 1619 |  |  |  | 61.92 | 533.48 | 0.145 | 78 | 4.64
447.57 | 277.454 | 5.83 | 1614 |  |  |  | 61.92 | 277.283 | 5.94 | 1618 |  |  |  | 61.92 | 277.366 | 5.84 | 1617 |  |  |  | 61.92 | 533.51 | 0.148 | 79 | 4.64
448.07 | 277.454 | 5.83 | 1614 |  |  |  | 61.92 | 277.283 | 5.94 | 1618 |  |  |  | 61.92 | 277.366 | 5.84 | 1617 |  |  |  | 61.92 | 533.51 | 0.148 | 79 | 4.64
448.56 | 277.383 | 5.79 | 1603 |  |  |  | 61.921 | 277.476 | 5.92 | 1612 |  |  |  | 61.92 | 277.342 | 5.81 | 1610 |  |  |  | 61.921 | 538.52 | 0.149 | 80 | 4.64
449.06 | 277.383 | 5.79 | 1603 |  |  |  | 61.921 | 277.476 | 5.92 | 1612 |  |  |  | 61.92 | 277.342 | 5.81 | 1610 |  |  |  | 61.921 | 538.52 | 0.149 | 80 | 4.64
449.56 | 277.441 | 5.63 | 1558 |  |  |  | 61.921 | 277.355 | 5.75 | 1563 |  |  |  | 61.92 | 277.302 | 5.67 | 1570 |  |  |  | 61.92 | 539.89 | 0.149 | 80 | 4.64
450.06 | 277.441 | 5.63 | 1558 |  |  |  | 61.921 | 277.355 | 5.75 | 1563 |  |  |  | 61.92 | 277.302 | 5.67 | 1570 |  |  |  | 61.92 | 539.89 | 0.149 | 80 | 4.64
450.56 | 277.364 | 5.83 | 1614 |  |  |  | 61.921 | 277.502 | 5.95 | 1620 |  |  |  | 61.922 | 277.273 | 5.86 | 1621 |  |  |  | 61.92 | 534.54 | 0.147 | 78 | 4.64
451.06 | 277.364 | 5.83 | 1614 |  |  |  | 61.921 | 277.502 | 5.95 | 1620 |  |  |  | 61.922 | 277.273 | 5.86 | 1621 |  |  |  | 61.92 | 534.54 | 0.147 | 78 | 4.64
451.56 | 277.438 | 5.83 | 1613 |  |  |  | 61.921 | 277.394 | 5.95 | 1622 |  |  |  | 61.92 | 277.365 | 5.83 | 1614 |  |  |  | 61.92 | 533.48 | 0.153 | 82 | 4.64
452.07 | 277.438 | 5.83 | 1613 |  |  |  | 61.921 | 277.394 | 5.95 | 1622 |  |  |  | 61.92 | 277.365 | 5.83 | 1614 |  |  |  | 61.92 | 533.48 | 0.153 | 82 | 4.64
452.57 | 277.343 | 5.83 | 1614 |  |  |  | 61.92 | 277.29 | 5.96 | 1623 |  |  |  | 61.92 | 277.337 | 5.84 | 1619 |  |  |  | 61.921 | 533.46 | 0.154 | 82 | 4.64
453.06 | 277.343 | 5.83 | 1614 |  |  |  | 61.92 | 277.29 | 5.96 | 1623 |  |  |  | 61.92 | 277.337 | 5.84 | 1619 |  |  |  | 61.921 | 533.46 | 0.154 | 82 | 4.64
453.56 | 277.416 | 5.82 | 1609 |  |  |  | 61.921 | 277.454 | 5.95 | 1620 |  |  |  | 61.919 | 277.302 | 5.84 | 1616 |  |  |  | 61.919 | 533.46 | 0.149 | 79 | 4.64
454.06 | 277.416 | 5.82 | 1609 |  |  |  | 61.921 | 277.454 | 5.95 | 1620 |  |  |  | 61.919 | 277.302 | 5.84 | 1616 |  |  |  | 61.919 | 533.46 | 0.149 | 79 | 4.64
454.56 | 277.386 | 5.8 | 1606 |  |  |  | 61.92 | 277.35 | 5.93 | 1612 |  |  |  | 61.919 | 277.269 | 5.84 | 1618 |  |  |  | 61.92 | 528.41 | 0.15 | 80 | 4.64
455.06 | 277.386 | 5.8 | 1606 |  |  |  | 61.92 | 277.35 | 5.93 | 1612 |  |  |  | 61.919 | 277.269 | 5.84 | 1618 |  |  |  | 61.92 | 528.41 | 0.15 | 80 | 4.64
455.56 | 277.391 | 5.8 | 1604 |  |  |  | 61.92 | 277.502 | 5.9 | 1605 |  |  |  | 61.922 | 277.372 | 5.81 | 1610 |  |  |  | 61.92 | 527.02 | 0.149 | 79 | 4.64
456.06 | 277.391 | 5.8 | 1604 |  |  |  | 61.92 | 277.502 | 5.9 | 1605 |  |  |  | 61.922 | 277.372 | 5.81 | 1610 |  |  |  | 61.92 | 527.02 | 0.149 | 79 | 4.64
456.56 | 277.451 | 5.81 | 1607 |  |  |  | 61.92 | 277.373 | 5.94 | 1615 |  |  |  | 61.92 | 277.354 | 5.83 | 1614 |  |  |  | 61.918 | 532.27 | 0.146 | 78 | 4.64
457.06 | 277.451 | 5.81 | 1607 |  |  |  | 61.92 | 277.373 | 5.94 | 1615 |  |  |  | 61.92 | 277.354 | 5.83 | 1614 |  |  |  | 61.918 | 532.27 | 0.146 | 78 | 4.64
457.56 | 277.381 | 5.83 | 1612 |  |  |  | 61.92 | 277.486 | 5.94 | 1618 |  |  |  | 61.92 | 277.32 | 5.85 | 1621 |  |  |  | 61.921 | 533.45 | 0.147 | 78 | 4.64
458.07 | 277.381 | 5.83 | 1612 |  |  |  | 61.92 | 277.486 | 5.94 | 1618 |  |  |  | 61.92 | 277.32 | 5.85 | 1621 |  |  |  | 61.921 | 533.45 | 0.147 | 78 | 4.64
458.57 | 277.444 | 5.83 | 1613 |  |  |  | 61.921 | 277.454 | 5.96 | 1622 |  |  |  | 61.92 | 277.273 | 5.85 | 1619 |  |  |  | 61.92 | 533.47 | 0.144 | 77 | 4.64
459.06 | 277.444 | 5.83 | 1613 |  |  |  | 61.921 | 277.454 | 5.96 | 1622 |  |  |  | 61.92 | 277.273 | 5.85 | 1619 |  |  |  | 61.92 | 533.47 | 0.144 | 77 | 4.64
459.56 | 277.367 | 5.81 | 1608 |  |  |  | 61.923 | 277.304 | 5.96 | 1621 |  |  |  | 61.92 | 277.247 | 5.86 | 1623 |  |  |  | 61.921 | 533.47 | 0.146 | 78 | 4.64
460.06 | 277.367 | 5.81 | 1608 |  |  |  | 61.923 | 277.304 | 5.96 | 1621 |  |  |  | 61.92 | 277.247 | 5.86 | 1623 |  |  |  | 61.921 | 533.47 | 0.146 | 78 | 4.64
460.56 | 277.438 | 5.8 | 1605 |  |  |  | 61.919 | 277.481 | 5.93 | 1614 |  |  |  | 61.92 | 277.349 | 5.82 | 1613 |  |  |  | 61.919 | 538.54 | 0.146 | 79 | 4.64
461.06 | 277.438 | 5.8 | 1605 |  |  |  | 61.919 | 277.481 | 5.93 | 1614 |  |  |  | 61.92 | 277.349 | 5.82 | 1613 |  |  |  | 61.919 | 538.54 | 0.146 | 79 | 4.64
461.56 | 277.341 | 5.65 | 1562 |  |  |  | 61.921 | 277.374 | 5.76 | 1567 |  |  |  | 61.92 | 277.328 | 5.64 | 1562 |  |  |  | 61.921 | 539.9 | 0.151 | 82 | 4.64
462.06 | 277.341 | 5.65 | 1562 |  |  |  | 61.921 | 277.374 | 5.76 | 1567 |  |  |  | 61.92 | 277.328 | 5.64 | 1562 |  |  |  | 61.921 | 539.9 | 0.151 | 82 | 4.64
462.56 | 277.41 | 5.84 | 1617 |  |  |  | 61.921 | 277.576 | 5.94 | 1620 |  |  |  | 61.922 | 277.292 | 5.87 | 1624 |  |  |  | 61.92 | 534.55 | 0.147 | 78 | 4.64
463.06 | 277.41 | 5.84 | 1617 |  |  |  | 61.921 | 277.576 | 5.94 | 1620 |  |  |  | 61.922 | 277.292 | 5.87 | 1624 |  |  |  | 61.92 | 534.55 | 0.147 | 78 | 4.64
463.56 | 277.466 | 5.81 | 1608 |  |  |  | 61.92 | 277.436 | 5.95 | 1623 |  |  |  | 61.921 | 277.251 | 5.86 | 1622 |  |  |  | 61.921 | 533.42 | 0.149 | 80 | 4.64
464.07 | 277.466 | 5.81 | 1608 |  |  |  | 61.92 | 277.436 | 5.95 | 1623 |  |  |  | 61.921 | 277.251 | 5.86 | 1622 |  |  |  | 61.921 | 533.42 | 0.149 | 80 | 4.64
464.57 | 277.389 | 5.82 | 1610 |  |  |  | 61.921 | 277.406 | 5.96 | 1623 |  |  |  | 61.919 | 277.348 | 5.86 | 1622 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
465.06 | 277.389 | 5.82 | 1610 |  |  |  | 61.921 | 277.406 | 5.96 | 1623 |  |  |  | 61.919 | 277.348 | 5.86 | 1622 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
465.56 | 277.455 | 5.83 | 1613 |  |  |  | 61.92 | 277.467 | 5.94 | 1618 |  |  |  | 61.92 | 277.332 | 5.87 | 1624 |  |  |  | 61.92 | 533.43 | 0.151 | 81 | 4.64
466.06 | 277.455 | 5.83 | 1613 |  |  |  | 61.92 | 277.467 | 5.94 | 1618 |  |  |  | 61.92 | 277.332 | 5.87 | 1624 |  |  |  | 61.92 | 533.43 | 0.151 | 81 | 4.64
466.56 | 277.393 | 5.8 | 1605 |  |  |  | 61.92 | 277.326 | 5.93 | 1613 |  |  |  | 61.919 | 277.309 | 5.82 | 1611 |  |  |  | 61.919 | 528.41 | 0.152 | 80 | 4.64
467.06 | 277.393 | 5.8 | 1605 |  |  |  | 61.92 | 277.326 | 5.93 | 1613 |  |  |  | 61.919 | 277.309 | 5.82 | 1611 |  |  |  | 61.919 | 528.41 | 0.152 | 80 | 4.64
467.56 | 277.452 | 5.79 | 1601 |  |  |  | 61.921 | 277.578 | 5.9 | 1606 |  |  |  | 61.92 | 277.274 | 5.81 | 1608 |  |  |  | 61.92 | 526.99 | 0.15 | 79 | 4.64
468.06 | 277.452 | 5.79 | 1601 |  |  |  | 61.921 | 277.578 | 5.9 | 1606 |  |  |  | 61.92 | 277.274 | 5.81 | 1608 |  |  |  | 61.92 | 526.99 | 0.15 | 79 | 4.64
468.56 | 277.361 | 5.81 | 1608 |  |  |  | 61.919 | 277.382 | 5.94 | 1617 |  |  |  | 61.92 | 277.361 | 5.85 | 1620 |  |  |  | 61.921 | 532.28 | 0.149 | 79 | 4.64
469.06 | 277.361 | 5.81 | 1608 |  |  |  | 61.919 | 277.382 | 5.94 | 1617 |  |  |  | 61.92 | 277.361 | 5.85 | 1620 |  |  |  | 61.921 | 532.28 | 0.149 | 79 | 4.64
469.56 | 277.439 | 5.83 | 1613 |  |  |  | 61.921 | 277.535 | 5.94 | 1619 |  |  |  | 61.922 | 277.325 | 5.85 | 1621 |  |  |  | 61.919 | 533.44 | 0.151 | 81 | 4.64
470.07 | 277.439 | 5.83 | 1613 |  |  |  | 61.921 | 277.535 | 5.94 | 1619 |  |  |  | 61.922 | 277.325 | 5.85 | 1621 |  |  |  | 61.919 | 533.44 | 0.151 | 81 | 4.64
470.57 | 277.341 | 5.81 | 1608 |  |  |  | 61.92 | 277.47 | 5.95 | 1622 |  |  |  | 61.92 | 277.317 | 5.84 | 1618 |  |  |  | 61.92 | 533.45 | 0.147 | 79 | 4.64
471.06 | 277.341 | 5.81 | 1608 |  |  |  | 61.92 | 277.47 | 5.95 | 1622 |  |  |  | 61.92 | 277.317 | 5.84 | 1618 |  |  |  | 61.92 | 533.45 | 0.147 | 79 | 4.64
471.56 | 277.41 | 5.83 | 1613 |  |  |  | 61.921 | 277.347 | 5.96 | 1623 |  |  |  | 61.92 | 277.293 | 5.85 | 1620 |  |  |  | 61.921 | 533.45 | 0.151 | 80 | 4.64
472.06 | 277.41 | 5.83 | 1613 |  |  |  | 61.921 | 277.347 | 5.96 | 1623 |  |  |  | 61.92 | 277.293 | 5.85 | 1620 |  |  |  | 61.921 | 533.45 | 0.151 | 80 | 4.64
472.56 | 277.463 | 5.8 | 1606 |  |  |  | 61.92 | 277.499 | 5.92 | 1614 |  |  |  | 61.919 | 277.368 | 5.84 | 1616 |  |  |  | 61.922 | 538.4 | 0.148 | 80 | 4.64
473.06 | 277.463 | 5.8 | 1606 |  |  |  | 61.92 | 277.499 | 5.92 | 1614 |  |  |  | 61.919 | 277.368 | 5.84 | 1616 |  |  |  | 61.922 | 538.4 | 0.148 | 80 | 4.64
473.56 | 277.394 | 5.64 | 1562 |  |  |  | 61.92 | 277.366 | 5.75 | 1565 |  |  |  | 61.921 | 277.348 | 5.66 | 1567 |  |  |  | 61.921 | 539.89 | 0.15 | 81 | 4.64
474.09 | 277.394 | 5.64 | 1562 |  |  |  | 61.92 | 277.366 | 5.75 | 1565 |  |  |  | 61.921 | 277.348 | 5.66 | 1567 |  |  |  | 61.921 | 539.89 | 0.15 | 81 | 4.64
474.59 | 277.443 | 5.84 | 1615 |  |  |  | 61.921 | 277.532 | 5.96 | 1624 |  |  |  | 61.919 | 277.327 | 5.85 | 1620 |  |  |  | 61.919 | 534.63 | 0.154 | 82 | 4.64
475.07 | 277.443 | 5.84 | 1615 |  |  |  | 61.921 | 277.532 | 5.96 | 1624 |  |  |  | 61.919 | 277.327 | 5.85 | 1620 |  |  |  | 61.919 | 534.63 | 0.154 | 82 | 4.64
475.57 | 277.388 | 5.81 | 1608 |  |  |  | 61.92 | 277.361 | 5.93 | 1617 |  |  |  | 61.919 | 277.308 | 5.85 | 1619 |  |  |  | 61.92 | 533.48 | 0.145 | 77 | 4.64
476.07 | 277.388 | 5.81 | 1608 |  |  |  | 61.92 | 277.361 | 5.93 | 1617 |  |  |  | 61.919 | 277.308 | 5.85 | 1619 |  |  |  | 61.92 | 533.48 | 0.145 | 77 | 4.64
476.57 | 277.457 | 5.82 | 1611 |  |  |  | 61.92 | 277.589 | 5.94 | 1620 |  |  |  | 61.922 | 277.266 | 5.87 | 1624 |  |  |  | 61.92 | 533.48 | 0.153 | 81 | 4.64
477.1 | 277.366 | 5.83 | 1613 |  |  |  | 61.92 | 277.418 | 5.93 | 1616 |  |  |  | 61.92 | 277.364 | 5.85 | 1620 |  |  |  | 61.92 | 533.47 | 0.151 | 80 | 4.64
477.6 | 277.366 | 5.83 | 1613 |  |  |  | 61.92 | 277.418 | 5.93 | 1616 |  |  |  | 61.92 | 277.364 | 5.85 | 1620 |  |  |  | 61.92 | 533.47 | 0.151 | 80 | 4.64
478.08 | 277.44 | 5.8 | 1605 |  |  |  | 61.92 | 277.295 | 5.92 | 1613 |  |  |  | 61.92 | 277.32 | 5.84 | 1618 |  |  |  | 61.921 | 528.44 | 0.149 | 79 | 4.64
478.58 | 277.44 | 5.8 | 1605 |  |  |  | 61.92 | 277.295 | 5.92 | 1613 |  |  |  | 61.92 | 277.32 | 5.84 | 1618 |  |  |  | 61.921 | 528.44 | 0.149 | 79 | 4.64
479.06 | 277.336 | 5.78 | 1598 |  |  |  | 61.918 | 277.486 | 5.9 | 1609 |  |  |  | 61.92 | 277.301 | 5.82 | 1612 |  |  |  | 61.919 | 526.96 | 0.146 | 77 | 4.64
479.56 | 277.336 | 5.78 | 1598 |  |  |  | 61.918 | 277.486 | 5.9 | 1609 |  |  |  | 61.92 | 277.301 | 5.82 | 1612 |  |  |  | 61.919 | 526.96 | 0.146 | 77 | 4.64
480.06 | 277.404 | 5.82 | 1610 |  |  |  | 61.92 | 277.339 | 5.92 | 1613 |  |  |  | 61.919 | 277.266 | 5.85 | 1618 |  |  |  | 61.92 | 532.1 | 0.148 | 79 | 4.64
480.56 | 277.404 | 5.82 | 1610 |  |  |  | 61.92 | 277.339 | 5.92 | 1613 |  |  |  | 61.919 | 277.266 | 5.85 | 1618 |  |  |  | 61.92 | 532.1 | 0.148 | 79 | 4.64
481.06 | 277.47 | 5.83 | 1613 |  |  |  | 61.921 | 277.526 | 5.94 | 1620 |  |  |  | 61.922 | 277.374 | 5.84 | 1619 |  |  |  | 61.92 | 533.38 | 0.15 | 80 | 4.64
481.56 | 277.47 | 5.83 | 1613 |  |  |  | 61.921 | 277.526 | 5.94 | 1620 |  |  |  | 61.922 | 277.374 | 5.84 | 1619 |  |  |  | 61.92 | 533.38 | 0.15 | 80 | 4.64
482.07 | 277.391 | 5.82 | 1611 |  |  |  | 61.921 | 277.401 | 5.96 | 1624 |  |  |  | 61.92 | 277.338 | 5.85 | 1619 |  |  |  | 61.92 | 533.37 | 0.144 | 77 | 4.64
482.57 | 277.391 | 5.82 | 1611 |  |  |  | 61.921 | 277.401 | 5.96 | 1624 |  |  |  | 61.92 | 277.338 | 5.85 | 1619 |  |  |  | 61.92 | 533.37 | 0.144 | 77 | 4.64
483.06 | 277.45 | 5.83 | 1614 |  |  |  | 61.92 | 277.471 | 5.94 | 1620 |  |  |  | 61.92 | 277.302 | 5.86 | 1623 |  |  |  | 61.921 | 533.39 | 0.15 | 80 | 4.64
483.56 | 277.45 | 5.83 | 1614 |  |  |  | 61.92 | 277.471 | 5.94 | 1620 |  |  |  | 61.92 | 277.302 | 5.86 | 1623 |  |  |  | 61.921 | 533.39 | 0.15 | 80 | 4.64
484.06 | 277.381 | 5.82 | 1611 |  |  |  | 61.921 | 277.392 | 5.91 | 1610 |  |  |  | 61.92 | 277.277 | 5.84 | 1616 |  |  |  | 61.921 | 538.25 | 0.144 | 78 | 4.64
484.56 | 277.381 | 5.82 | 1611 |  |  |  | 61.921 | 277.392 | 5.91 | 1610 |  |  |  | 61.92 | 277.277 | 5.84 | 1616 |  |  |  | 61.921 | 538.25 | 0.144 | 78 | 4.64
485.06 | 277.446 | 5.68 | 1571 |  |  |  | 61.92 | 277.289 | 5.79 | 1574 |  |  |  | 61.92 | 277.372 | 5.68 | 1574 |  |  |  | 61.92 | 539.81 | 0.145 | 78 | 4.64
485.56 | 277.446 | 5.68 | 1571 |  |  |  | 61.92 | 277.289 | 5.79 | 1574 |  |  |  | 61.92 | 277.372 | 5.68 | 1574 |  |  |  | 61.92 | 539.81 | 0.145 | 78 | 4.64
486.06 | 277.354 | 5.83 | 1613 |  |  |  | 61.921 | 277.467 | 5.96 | 1626 |  |  |  | 61.919 | 277.348 | 5.85 | 1620 |  |  |  | 61.92 | 534.59 | 0.145 | 78 | 4.64
486.56 | 277.354 | 5.83 | 1613 |  |  |  | 61.921 | 277.467 | 5.96 | 1626 |  |  |  | 61.919 | 277.348 | 5.85 | 1620 |  |  |  | 61.92 | 534.59 | 0.145 | 78 | 4.64
487.06 | 277.419 | 5.82 | 1610 |  |  |  | 61.921 | 277.342 | 5.95 | 1619 |  |  |  | 61.921 | 277.305 | 5.86 | 1622 |  |  |  | 61.921 | 533.39 | 0.144 | 77 | 4.64
487.56 | 277.419 | 5.82 | 1610 |  |  |  | 61.921 | 277.342 | 5.95 | 1619 |  |  |  | 61.921 | 277.305 | 5.86 | 1622 |  |  |  | 61.921 | 533.39 | 0.144 | 77 | 4.64
488.07 | 277.344 | 5.84 | 1616 |  |  |  | 61.918 | 277.466 | 5.94 | 1620 |  |  |  | 61.922 | 277.281 | 5.85 | 1620 |  |  |  | 61.921 | 533.33 | 0.149 | 80 | 4.64
488.57 | 277.344 | 5.84 | 1616 |  |  |  | 61.918 | 277.466 | 5.94 | 1620 |  |  |  | 61.922 | 277.281 | 5.85 | 1620 |  |  |  | 61.921 | 533.33 | 0.149 | 80 | 4.64
489.06 | 277.395 | 5.84 | 1616 |  |  |  | 61.921 | 277.372 | 5.96 | 1621 |  |  |  | 61.92 | 277.258 | 5.86 | 1623 |  |  |  | 61.92 | 533.4 | 0.147 | 78 | 4.64
489.56 | 277.395 | 5.84 | 1616 |  |  |  | 61.921 | 277.372 | 5.96 | 1621 |  |  |  | 61.92 | 277.258 | 5.86 | 1623 |  |  |  | 61.92 | 533.4 | 0.147 | 78 | 4.64
490.06 | 277.46 | 5.79 | 1602 |  |  |  | 61.92 | 277.421 | 5.92 | 1611 |  |  |  | 61.92 | 277.371 | 5.83 | 1614 |  |  |  | 61.92 | 528.41 | 0.149 | 79 | 4.64
490.56 | 277.46 | 5.79 | 1602 |  |  |  | 61.92 | 277.421 | 5.92 | 1611 |  |  |  | 61.92 | 277.371 | 5.83 | 1614 |  |  |  | 61.92 | 528.41 | 0.149 | 79 | 4.64
491.06 | 277.405 | 5.78 | 1598 |  |  |  | 61.921 | 277.438 | 5.9 | 1606 |  |  |  | 61.919 | 277.334 | 5.83 | 1613 |  |  |  | 61.92 | 526.94 | 0.146 | 77 | 4.64
491.56 | 277.405 | 5.78 | 1598 |  |  |  | 61.921 | 277.438 | 5.9 | 1606 |  |  |  | 61.919 | 277.334 | 5.83 | 1613 |  |  |  | 61.92 | 526.94 | 0.146 | 77 | 4.64
492.06 | 277.444 | 5.82 | 1610 |  |  |  | 61.92 | 277.275 | 5.93 | 1614 |  |  |  | 61.919 | 277.296 | 5.84 | 1618 |  |  |  | 61.92 | 532.27 | 0.144 | 77 | 4.64
492.56 | 277.444 | 5.82 | 1610 |  |  |  | 61.92 | 277.275 | 5.93 | 1614 |  |  |  | 61.919 | 277.296 | 5.84 | 1618 |  |  |  | 61.92 | 532.27 | 0.144 | 77 | 4.64
493.06 | 277.39 | 5.83 | 1613 |  |  |  | 61.92 | 277.433 | 5.95 | 1621 |  |  |  | 61.918 | 277.267 | 5.84 | 1618 |  |  |  | 61.92 | 533.39 | 0.149 | 79 | 4.64
493.56 | 277.39 | 5.83 | 1613 |  |  |  | 61.92 | 277.433 | 5.95 | 1621 |  |  |  | 61.918 | 277.267 | 5.84 | 1618 |  |  |  | 61.92 | 533.39 | 0.149 | 79 | 4.64
494.07 | 277.449 | 5.81 | 1609 |  |  |  | 61.919 | 277.326 | 5.94 | 1618 |  |  |  | 61.921 | 277.364 | 5.84 | 1618 |  |  |  | 61.92 | 533.4 | 0.147 | 78 | 4.64
494.57 | 277.449 | 5.81 | 1609 |  |  |  | 61.919 | 277.326 | 5.94 | 1618 |  |  |  | 61.921 | 277.364 | 5.84 | 1618 |  |  |  | 61.92 | 533.4 | 0.147 | 78 | 4.64
495.06 | 277.347 | 5.83 | 1613 |  |  |  | 61.92 | 277.543 | 5.95 | 1620 |  |  |  | 61.922 | 277.338 | 5.86 | 1622 |  |  |  | 61.92 | 533.4 | 0.149 | 80 | 4.64
495.56 | 277.347 | 5.83 | 1613 |  |  |  | 61.92 | 277.543 | 5.95 | 1620 |  |  |  | 61.922 | 277.338 | 5.86 | 1622 |  |  |  | 61.92 | 533.4 | 0.149 | 80 | 4.64
496.06 | 277.434 | 5.8 | 1606 |  |  |  | 61.921 | 277.391 | 5.92 | 1611 |  |  |  | 61.919 | 277.297 | 5.83 | 1613 |  |  |  | 61.92 | 538.44 | 0.146 | 79 | 4.64
496.56 | 277.434 | 5.8 | 1606 |  |  |  | 61.921 | 277.391 | 5.92 | 1611 |  |  |  | 61.919 | 277.297 | 5.83 | 1613 |  |  |  | 61.92 | 538.44 | 0.146 | 79 | 4.64
497.06 | 277.334 | 5.65 | 1563 |  |  |  | 61.918 | 277.434 | 5.75 | 1567 |  |  |  | 61.92 | 277.266 | 5.67 | 1569 |  |  |  | 61.92 | 539.85 | 0.148 | 80 | 4.64
497.56 | 277.334 | 5.65 | 1563 |  |  |  | 61.918 | 277.434 | 5.75 | 1567 |  |  |  | 61.92 | 277.266 | 5.67 | 1569 |  |  |  | 61.92 | 539.85 | 0.148 | 80 | 4.64
498.06 | 277.405 | 5.83 | 1613 |  |  |  | 61.92 | 277.459 | 5.96 | 1625 |  |  |  | 61.92 | 277.367 | 5.85 | 1621 |  |  |  | 61.921 | 534.35 | 0.143 | 77 | 4.64
498.56 | 277.405 | 5.83 | 1613 |  |  |  | 61.92 | 277.459 | 5.96 | 1625 |  |  |  | 61.92 | 277.367 | 5.85 | 1621 |  |  |  | 61.921 | 534.35 | 0.143 | 77 | 4.64
499.06 | 277.454 | 5.82 | 1611 |  |  |  | 61.92 | 277.29 | 5.94 | 1619 |  |  |  | 61.92 | 277.355 | 5.85 | 1620 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
499.56 | 277.454 | 5.82 | 1611 |  |  |  | 61.92 | 277.29 | 5.94 | 1619 |  |  |  | 61.92 | 277.355 | 5.85 | 1620 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
500.07 | 277.387 | 5.84 | 1617 |  |  |  | 61.921 | 277.523 | 5.95 | 1623 |  |  |  | 61.921 | 277.313 | 5.86 | 1622 |  |  |  | 61.921 | 533.44 | 0.148 | 79 | 4.64
500.57 | 277.387 | 5.84 | 1617 |  |  |  | 61.921 | 277.523 | 5.95 | 1623 |  |  |  | 61.921 | 277.313 | 5.86 | 1622 |  |  |  | 61.921 | 533.44 | 0.148 | 79 | 4.64
501.06 | 277.444 | 5.84 | 1615 |  |  |  | 61.92 | 277.35 | 5.94 | 1620 |  |  |  | 61.92 | 277.273 | 5.86 | 1621 |  |  |  | 61.92 | 533.41 | 0.146 | 78 | 4.64
501.56 | 277.444 | 5.84 | 1615 |  |  |  | 61.92 | 277.35 | 5.94 | 1620 |  |  |  | 61.92 | 277.273 | 5.86 | 1621 |  |  |  | 61.92 | 533.41 | 0.146 | 78 | 4.64
502.06 | 277.366 | 5.79 | 1603 |  |  |  | 61.92 | 277.558 | 5.91 | 1611 |  |  |  | 61.923 | 277.358 | 5.82 | 1612 |  |  |  | 61.921 | 528.28 | 0.148 | 78 | 4.64
502.56 | 277.366 | 5.79 | 1603 |  |  |  | 61.92 | 277.558 | 5.91 | 1611 |  |  |  | 61.923 | 277.358 | 5.82 | 1612 |  |  |  | 61.921 | 528.28 | 0.148 | 78 | 4.64
503.06 | 277.45 | 5.78 | 1600 |  |  |  | 61.919 | 277.413 | 5.91 | 1611 |  |  |  | 61.919 | 277.344 | 5.81 | 1610 |  |  |  | 61.92 | 526.94 | 0.144 | 76 | 4.64
503.56 | 277.45 | 5.78 | 1600 |  |  |  | 61.919 | 277.413 | 5.91 | 1611 |  |  |  | 61.919 | 277.344 | 5.81 | 1610 |  |  |  | 61.92 | 526.94 | 0.144 | 76 | 4.64
504.06 | 277.353 | 5.81 | 1606 |  |  |  | 61.921 | 277.378 | 5.92 | 1614 |  |  |  | 61.92 | 277.319 | 5.85 | 1619 |  |  |  | 61.92 | 532.36 | 0.144 | 76 | 4.64
504.56 | 277.353 | 5.81 | 1606 |  |  |  | 61.921 | 277.378 | 5.92 | 1614 |  |  |  | 61.92 | 277.319 | 5.85 | 1619 |  |  |  | 61.92 | 532.36 | 0.144 | 76 | 4.64
505.06 | 277.431 | 5.83 | 1614 |  |  |  | 61.921 | 277.479 | 5.94 | 1619 |  |  |  | 61.92 | 277.273 | 5.85 | 1621 |  |  |  | 61.921 | 533.44 | 0.144 | 77 | 4.64
505.56 | 277.431 | 5.83 | 1614 |  |  |  | 61.921 | 277.479 | 5.94 | 1619 |  |  |  | 61.92 | 277.273 | 5.85 | 1621 |  |  |  | 61.921 | 533.44 | 0.144 | 77 | 4.64
506.07 | 277.356 | 5.84 | 1617 |  |  |  | 61.918 | 277.335 | 5.96 | 1623 |  |  |  | 61.92 | 277.291 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.147 | 78 | 4.64
506.57 | 277.356 | 5.84 | 1617 |  |  |  | 61.918 | 277.335 | 5.96 | 1623 |  |  |  | 61.92 | 277.291 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.147 | 78 | 4.64
507.06 | 277.405 | 5.83 | 1613 |  |  |  | 61.921 | 277.515 | 5.94 | 1619 |  |  |  | 61.918 | 277.353 | 5.85 | 1620 |  |  |  | 61.921 | 533.37 | 0.149 | 80 | 4.64
507.6 | 277.405 | 5.83 | 1613 |  |  |  | 61.921 | 277.515 | 5.94 | 1619 |  |  |  | 61.918 | 277.353 | 5.85 | 1620 |  |  |  | 61.921 | 533.37 | 0.149 | 80 | 4.64
508.1 | 277.451 | 5.78 | 1601 |  |  |  | 61.92 | 277.368 | 5.92 | 1612 |  |  |  | 61.921 | 277.334 | 5.84 | 1616 |  |  |  | 61.919 | 538.51 | 0.146 | 79 | 4.64
508.58 | 277.451 | 5.78 | 1601 |  |  |  | 61.92 | 277.368 | 5.92 | 1612 |  |  |  | 61.921 | 277.334 | 5.84 | 1616 |  |  |  | 61.919 | 538.51 | 0.146 | 79 | 4.64
509.08 | 277.382 | 5.65 | 1563 |  |  |  | 61.921 | 277.597 | 5.76 | 1569 |  |  |  | 61.923 | 277.282 | 5.68 | 1574 |  |  |  | 61.921 | 539.81 | 0.144 | 78 | 4.64
509.57 | 277.382 | 5.65 | 1563 |  |  |  | 61.921 | 277.597 | 5.76 | 1569 |  |  |  | 61.923 | 277.282 | 5.68 | 1574 |  |  |  | 61.921 | 539.81 | 0.144 | 78 | 4.64
510.07 | 277.443 | 5.84 | 1615 |  |  |  | 61.919 | 277.427 | 5.96 | 1622 |  |  |  | 61.92 | 277.249 | 5.87 | 1625 |  |  |  | 61.919 | 534.48 | 0.148 | 79 | 4.64
510.56 | 277.443 | 5.84 | 1615 |  |  |  | 61.919 | 277.427 | 5.96 | 1622 |  |  |  | 61.92 | 277.249 | 5.87 | 1625 |  |  |  | 61.919 | 534.48 | 0.148 | 79 | 4.64
511.06 | 277.363 | 5.84 | 1615 |  |  |  | 61.921 | 277.334 | 5.96 | 1620 |  |  |  | 61.92 | 277.349 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.147 | 79 | 4.64
511.59 | 277.438 | 5.82 | 1610 |  |  |  | 61.921 | 277.466 | 5.94 | 1619 |  |  |  | 61.92 | 277.331 | 5.86 | 1624 |  |  |  | 61.92 | 533.37 | 0.145 | 77 | 4.64
512.09 | 277.438 | 5.82 | 1610 |  |  |  | 61.921 | 277.466 | 5.94 | 1619 |  |  |  | 61.92 | 277.331 | 5.86 | 1624 |  |  |  | 61.92 | 533.37 | 0.145 | 77 | 4.64
512.58 | 277.342 | 5.81 | 1607 |  |  |  | 61.919 | 277.331 | 5.94 | 1620 |  |  |  | 61.92 | 277.299 | 5.86 | 1622 |  |  |  | 61.921 | 533.39 | 0.148 | 79 | 4.64
513.08 | 277.342 | 5.81 | 1607 |  |  |  | 61.919 | 277.331 | 5.94 | 1620 |  |  |  | 61.92 | 277.299 | 5.86 | 1622 |  |  |  | 61.921 | 533.39 | 0.148 | 79 | 4.64
513.57 | 277.421 | 5.8 | 1604 |  |  |  | 61.921 | 277.551 | 5.92 | 1615 |  |  |  | 61.919 | 277.252 | 5.83 | 1614 |  |  |  | 61.92 | 528.24 | 0.149 | 79 | 4.64
514.07 | 277.421 | 5.8 | 1604 |  |  |  | 61.921 | 277.551 | 5.92 | 1615 |  |  |  | 61.919 | 277.252 | 5.83 | 1614 |  |  |  | 61.92 | 528.24 | 0.149 | 79 | 4.64
514.56 | 277.39 | 5.8 | 1604 |  |  |  | 61.919 | 277.415 | 5.91 | 1610 |  |  |  | 61.92 | 277.36 | 5.82 | 1611 |  |  |  | 61.921 | 526.96 | 0.148 | 78 | 4.64
515.06 | 277.39 | 5.8 | 1604 |  |  |  | 61.919 | 277.415 | 5.91 | 1610 |  |  |  | 61.92 | 277.36 | 5.82 | 1611 |  |  |  | 61.921 | 526.96 | 0.148 | 78 | 4.64
515.56 | 277.407 | 5.82 | 1610 |  |  |  | 61.921 | 277.57 | 5.92 | 1613 |  |  |  | 61.923 | 277.329 | 5.83 | 1614 |  |  |  | 61.921 | 532.32 | 0.146 | 78 | 4.64
516.06 | 277.407 | 5.82 | 1610 |  |  |  | 61.921 | 277.57 | 5.92 | 1613 |  |  |  | 61.923 | 277.329 | 5.83 | 1614 |  |  |  | 61.921 | 532.32 | 0.146 | 78 | 4.64
516.56 | 277.46 | 5.83 | 1614 |  |  |  | 61.919 | 277.425 | 5.94 | 1620 |  |  |  | 61.92 | 277.315 | 5.86 | 1624 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
517.06 | 277.46 | 5.83 | 1614 |  |  |  | 61.919 | 277.425 | 5.94 | 1620 |  |  |  | 61.92 | 277.315 | 5.86 | 1624 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
517.56 | 277.393 | 5.85 | 1617 |  |  |  | 61.921 | 277.311 | 5.95 | 1619 |  |  |  | 61.918 | 277.276 | 5.86 | 1622 |  |  |  | 61.919 | 533.38 | 0.147 | 79 | 4.64
518.07 | 277.393 | 5.85 | 1617 |  |  |  | 61.921 | 277.311 | 5.95 | 1619 |  |  |  | 61.918 | 277.276 | 5.86 | 1622 |  |  |  | 61.919 | 533.38 | 0.147 | 79 | 4.64
518.57 | 277.458 | 5.81 | 1609 |  |  |  | 61.92 | 277.467 | 5.92 | 1614 |  |  |  | 61.921 | 277.362 | 5.85 | 1620 |  |  |  | 61.918 | 533.43 | 0.152 | 81 | 4.64
519.06 | 277.458 | 5.81 | 1609 |  |  |  | 61.92 | 277.467 | 5.92 | 1614 |  |  |  | 61.921 | 277.362 | 5.85 | 1620 |  |  |  | 61.918 | 533.43 | 0.152 | 81 | 4.64
519.56 | 277.357 | 5.8 | 1605 |  |  |  | 61.921 | 277.323 | 5.92 | 1611 |  |  |  | 61.92 | 277.335 | 5.82 | 1612 |  |  |  | 61.921 | 538.41 | 0.151 | 81 | 4.64
520.06 | 277.357 | 5.8 | 1605 |  |  |  | 61.921 | 277.323 | 5.92 | 1611 |  |  |  | 61.92 | 277.335 | 5.82 | 1612 |  |  |  | 61.921 | 538.41 | 0.151 | 81 | 4.64
520.56 | 277.436 | 5.66 | 1565 |  |  |  | 61.921 | 277.488 | 5.77 | 1570 |  |  |  | 61.923 | 277.309 | 5.68 | 1571 |  |  |  | 61.92 | 539.81 | 0.153 | 83 | 4.64
521.06 | 277.436 | 5.66 | 1565 |  |  |  | 61.921 | 277.488 | 5.77 | 1570 |  |  |  | 61.923 | 277.309 | 5.68 | 1571 |  |  |  | 61.92 | 539.81 | 0.153 | 83 | 4.64
521.56 | 277.341 | 5.83 | 1614 |  |  |  | 61.92 | 277.391 | 5.96 | 1623 |  |  |  | 61.919 | 277.289 | 5.85 | 1620 |  |  |  | 61.92 | 534.51 | 0.148 | 79 | 4.64
522.06 | 277.341 | 5.83 | 1614 |  |  |  | 61.92 | 277.391 | 5.96 | 1623 |  |  |  | 61.919 | 277.289 | 5.85 | 1620 |  |  |  | 61.92 | 534.51 | 0.148 | 79 | 4.64
522.56 | 277.412 | 5.82 | 1610 |  |  |  | 61.921 | 277.526 | 5.95 | 1620 |  |  |  | 61.921 | 277.371 | 5.85 | 1621 |  |  |  | 61.923 | 533.35 | 0.152 | 81 | 4.64
523.06 | 277.412 | 5.82 | 1610 |  |  |  | 61.921 | 277.526 | 5.95 | 1620 |  |  |  | 61.921 | 277.371 | 5.85 | 1621 |  |  |  | 61.923 | 533.35 | 0.152 | 81 | 4.64
523.56 | 277.449 | 5.83 | 1613 |  |  |  | 61.921 | 277.442 | 5.94 | 1617 |  |  |  | 61.92 | 277.345 | 5.86 | 1624 |  |  |  | 61.921 | 533.39 | 0.148 | 79 | 4.64
524.07 | 277.449 | 5.83 | 1613 |  |  |  | 61.921 | 277.442 | 5.94 | 1617 |  |  |  | 61.92 | 277.345 | 5.86 | 1624 |  |  |  | 61.921 | 533.39 | 0.148 | 79 | 4.64
524.57 | 277.391 | 5.83 | 1614 |  |  |  | 61.921 | 277.291 | 5.93 | 1616 |  |  |  | 61.92 | 277.318 | 5.85 | 1618 |  |  |  | 61.919 | 533.36 | 0.153 | 81 | 4.64
525.06 | 277.391 | 5.83 | 1614 |  |  |  | 61.921 | 277.291 | 5.93 | 1616 |  |  |  | 61.92 | 277.318 | 5.85 | 1618 |  |  |  | 61.919 | 533.36 | 0.153 | 81 | 4.64
525.56 | 277.447 | 5.8 | 1604 |  |  |  | 61.919 | 277.478 | 5.92 | 1613 |  |  |  | 61.92 | 277.296 | 5.82 | 1612 |  |  |  | 61.921 | 528.3 | 0.142 | 75 | 4.64
526.06 | 277.447 | 5.8 | 1604 |  |  |  | 61.919 | 277.478 | 5.92 | 1613 |  |  |  | 61.92 | 277.296 | 5.82 | 1612 |  |  |  | 61.921 | 528.3 | 0.142 | 75 | 4.64
526.56 | 277.385 | 5.77 | 1597 |  |  |  | 61.921 | 277.334 | 5.9 | 1609 |  |  |  | 61.92 | 277.268 | 5.81 | 1608 |  |  |  | 61.92 | 526.97 | 0.144 | 76 | 4.64
527.06 | 277.385 | 5.77 | 1597 |  |  |  | 61.921 | 277.334 | 5.9 | 1609 |  |  |  | 61.92 | 277.268 | 5.81 | 1608 |  |  |  | 61.92 | 526.97 | 0.144 | 76 | 4.64
527.56 | 277.455 | 5.81 | 1608 |  |  |  | 61.921 | 277.531 | 5.92 | 1614 |  |  |  | 61.923 | 277.357 | 5.85 | 1620 |  |  |  | 61.921 | 532.21 | 0.15 | 80 | 4.64
528.06 | 277.455 | 5.81 | 1608 |  |  |  | 61.921 | 277.531 | 5.92 | 1614 |  |  |  | 61.923 | 277.357 | 5.85 | 1620 |  |  |  | 61.921 | 532.21 | 0.15 | 80 | 4.64
528.56 | 277.371 | 5.83 | 1613 |  |  |  | 61.919 | 277.395 | 5.93 | 1615 |  |  |  | 61.92 | 277.327 | 5.84 | 1618 |  |  |  | 61.921 | 533.33 | 0.152 | 81 | 4.64
529.06 | 277.371 | 5.83 | 1613 |  |  |  | 61.919 | 277.395 | 5.93 | 1615 |  |  |  | 61.92 | 277.327 | 5.84 | 1618 |  |  |  | 61.921 | 533.33 | 0.152 | 81 | 4.64
529.56 | 277.437 | 5.84 | 1616 |  |  |  | 61.921 | 277.439 | 5.95 | 1620 |  |  |  | 61.919 | 277.297 | 5.84 | 1616 |  |  |  | 61.921 | 533.36 | 0.15 | 80 | 4.64
530.07 | 277.437 | 5.84 | 1616 |  |  |  | 61.921 | 277.439 | 5.95 | 1620 |  |  |  | 61.919 | 277.297 | 5.84 | 1616 |  |  |  | 61.921 | 533.36 | 0.15 | 80 | 4.64
530.57 | 277.348 | 5.82 | 1610 |  |  |  | 61.919 | 277.398 | 5.94 | 1619 |  |  |  | 61.918 | 277.274 | 5.86 | 1622 |  |  |  | 61.92 | 533.36 | 0.15 | 80 | 4.64
531.06 | 277.348 | 5.82 | 1610 |  |  |  | 61.919 | 277.398 | 5.94 | 1619 |  |  |  | 61.918 | 277.274 | 5.86 | 1622 |  |  |  | 61.92 | 533.36 | 0.15 | 80 | 4.64
531.56 | 277.412 | 5.8 | 1605 |  |  |  | 61.921 | 277.268 | 5.9 | 1609 |  |  |  | 61.921 | 277.375 | 5.84 | 1617 |  |  |  | 61.92 | 538.33 | 0.149 | 80 | 4.64
532.06 | 277.412 | 5.8 | 1605 |  |  |  | 61.921 | 277.268 | 5.9 | 1609 |  |  |  | 61.921 | 277.375 | 5.84 | 1617 |  |  |  | 61.92 | 538.33 | 0.149 | 80 | 4.64
532.56 | 277.446 | 5.67 | 1568 |  |  |  | 61.92 | 277.484 | 5.76 | 1570 |  |  |  | 61.92 | 277.334 | 5.69 | 1575 |  |  |  | 61.921 | 539.79 | 0.148 | 80 | 4.64
533.06 | 277.446 | 5.67 | 1568 |  |  |  | 61.92 | 277.484 | 5.76 | 1570 |  |  |  | 61.92 | 277.334 | 5.69 | 1575 |  |  |  | 61.921 | 539.79 | 0.148 | 80 | 4.64
533.56 | 277.395 | 5.85 | 1618 |  |  |  | 61.921 | 277.314 | 5.95 | 1622 |  |  |  | 61.92 | 277.303 | 5.85 | 1619 |  |  |  | 61.92 | 534.59 | 0.149 | 80 | 4.64
534.06 | 277.395 | 5.85 | 1618 |  |  |  | 61.921 | 277.314 | 5.95 | 1622 |  |  |  | 61.92 | 277.303 | 5.85 | 1619 |  |  |  | 61.92 | 534.59 | 0.149 | 80 | 4.64
534.56 | 277.452 | 5.81 | 1608 |  |  |  | 61.92 | 277.518 | 5.94 | 1619 |  |  |  | 61.923 | 277.271 | 5.85 | 1620 |  |  |  | 61.919 | 533.45 | 0.154 | 82 | 4.64
535.06 | 277.452 | 5.81 | 1608 |  |  |  | 61.92 | 277.518 | 5.94 | 1619 |  |  |  | 61.923 | 277.271 | 5.85 | 1620 |  |  |  | 61.919 | 533.45 | 0.154 | 82 | 4.64
535.56 | 277.39 | 5.83 | 1613 |  |  |  | 61.921 | 277.387 | 5.93 | 1615 |  |  |  | 61.919 | 277.374 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
536.07 | 277.39 | 5.83 | 1613 |  |  |  | 61.921 | 277.387 | 5.93 | 1615 |  |  |  | 61.919 | 277.374 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
536.57 | 277.466 | 5.83 | 1613 |  |  |  | 61.919 | 277.322 | 5.93 | 1616 |  |  |  | 61.919 | 277.348 | 5.86 | 1623 |  |  |  | 61.92 | 533.39 | 0.148 | 79 | 4.64
537.06 | 277.466 | 5.83 | 1613 |  |  |  | 61.919 | 277.322 | 5.93 | 1616 |  |  |  | 61.919 | 277.348 | 5.86 | 1623 |  |  |  | 61.92 | 533.39 | 0.148 | 79 | 4.64
537.56 | 277.361 | 5.81 | 1606 |  |  |  | 61.92 | 277.465 | 5.92 | 1612 |  |  |  | 61.919 | 277.305 | 5.81 | 1609 |  |  |  | 61.92 | 528.45 | 0.151 | 80 | 4.64
538.06 | 277.361 | 5.81 | 1606 |  |  |  | 61.92 | 277.465 | 5.92 | 1612 |  |  |  | 61.919 | 277.305 | 5.81 | 1609 |  |  |  | 61.92 | 528.45 | 0.151 | 80 | 4.64
538.56 | 277.438 | 5.78 | 1599 |  |  |  | 61.92 | 277.315 | 5.91 | 1608 |  |  |  | 61.92 | 277.266 | 5.82 | 1611 |  |  |  | 61.92 | 526.94 | 0.153 | 81 | 4.64
539.1 | 277.438 | 5.78 | 1599 |  |  |  | 61.92 | 277.315 | 5.91 | 1608 |  |  |  | 61.92 | 277.266 | 5.82 | 1611 |  |  |  | 61.92 | 526.94 | 0.153 | 81 | 4.64
539.6 | 277.307 | 5.81 | 1608 |  |  |  | 61.92 | 277.499 | 5.92 | 1613 |  |  |  | 61.92 | 277.358 | 5.85 | 1621 |  |  |  | 61.92 | 532.1 | 0.145 | 77 | 4.64
540.08 | 277.307 | 5.81 | 1608 |  |  |  | 61.92 | 277.499 | 5.92 | 1613 |  |  |  | 61.92 | 277.358 | 5.85 | 1621 |  |  |  | 61.92 | 532.1 | 0.145 | 77 | 4.64
540.58 | 277.368 | 5.82 | 1611 |  |  |  | 61.921 | 277.373 | 5.94 | 1618 |  |  |  | 61.92 | 277.349 | 5.86 | 1622 |  |  |  | 61.92 | 533.36 | 0.152 | 81 | 4.64
541.07 | 277.368 | 5.82 | 1611 |  |  |  | 61.921 | 277.373 | 5.94 | 1618 |  |  |  | 61.92 | 277.349 | 5.86 | 1622 |  |  |  | 61.92 | 533.36 | 0.152 | 81 | 4.64
541.57 | 277.439 | 5.83 | 1614 |  |  |  | 61.919 | 277.587 | 5.95 | 1620 |  |  |  | 61.923 | 277.318 | 5.85 | 1621 |  |  |  | 61.919 | 533.37 | 0.15 | 80 | 4.64
542.11 | 277.439 | 5.83 | 1614 |  |  |  | 61.919 | 277.587 | 5.95 | 1620 |  |  |  | 61.923 | 277.318 | 5.85 | 1621 |  |  |  | 61.919 | 533.37 | 0.15 | 80 | 4.64
542.61 | 277.36 | 5.84 | 1616 |  |  |  | 61.92 | 277.445 | 5.96 | 1623 |  |  |  | 61.919 | 277.284 | 5.84 | 1617 |  |  |  | 61.92 | 533.38 | 0.148 | 79 | 4.64
543.09 | 277.428 | 5.8 | 1605 |  |  |  | 61.921 | 277.332 | 5.93 | 1613 |  |  |  | 61.919 | 277.277 | 5.83 | 1615 |  |  |  | 61.921 | 538.3 | 0.15 | 81 | 4.64
543.59 | 277.428 | 5.8 | 1605 |  |  |  | 61.921 | 277.332 | 5.93 | 1613 |  |  |  | 61.919 | 277.277 | 5.83 | 1615 |  |  |  | 61.921 | 538.3 | 0.15 | 81 | 4.64
544.08 | 277.348 | 5.64 | 1560 |  |  |  | 61.92 | 277.509 | 5.78 | 1573 |  |  |  | 61.919 | 277.345 | 5.67 | 1571 |  |  |  | 61.921 | 539.81 | 0.149 | 80 | 4.64
544.58 | 277.348 | 5.64 | 1560 |  |  |  | 61.92 | 277.509 | 5.78 | 1573 |  |  |  | 61.919 | 277.345 | 5.67 | 1571 |  |  |  | 61.921 | 539.81 | 0.149 | 80 | 4.64
545.06 | 277.418 | 5.84 | 1617 |  |  |  | 61.919 | 277.384 | 5.95 | 1617 |  |  |  | 61.919 | 277.323 | 5.88 | 1628 |  |  |  | 61.919 | 534.67 | 0.149 | 80 | 4.64
545.56 | 277.418 | 5.84 | 1617 |  |  |  | 61.919 | 277.384 | 5.95 | 1617 |  |  |  | 61.919 | 277.323 | 5.88 | 1628 |  |  |  | 61.919 | 534.67 | 0.149 | 80 | 4.64
546.06 | 277.335 | 5.82 | 1611 |  |  |  | 61.919 | 277.579 | 5.93 | 1617 |  |  |  | 61.922 | 277.287 | 5.84 | 1617 |  |  |  | 61.921 | 533.4 | 0.152 | 81 | 4.64
546.56 | 277.335 | 5.82 | 1611 |  |  |  | 61.919 | 277.579 | 5.93 | 1617 |  |  |  | 61.922 | 277.287 | 5.84 | 1617 |  |  |  | 61.921 | 533.4 | 0.152 | 81 | 4.64
547.06 | 277.4 | 5.83 | 1614 |  |  |  | 61.921 | 277.432 | 5.96 | 1621 |  |  |  | 61.92 | 277.261 | 5.83 | 1615 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 4.64
547.56 | 277.4 | 5.83 | 1614 |  |  |  | 61.921 | 277.432 | 5.96 | 1621 |  |  |  | 61.92 | 277.261 | 5.83 | 1615 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 4.64
548.07 | 277.32 | 5.82 | 1611 |  |  |  | 61.921 | 277.519 | 5.94 | 1617 |  |  |  | 61.922 | 277.357 | 5.86 | 1623 |  |  |  | 61.921 | 533.38 | 0.146 | 78 | 4.64
548.57 | 277.32 | 5.82 | 1611 |  |  |  | 61.921 | 277.519 | 5.94 | 1617 |  |  |  | 61.922 | 277.357 | 5.86 | 1623 |  |  |  | 61.921 | 533.38 | 0.146 | 78 | 4.64
549.06 | 277.378 | 5.8 | 1606 |  |  |  | 61.92 | 277.449 | 5.92 | 1612 |  |  |  | 61.919 | 277.334 | 5.83 | 1614 |  |  |  | 61.919 | 528.49 | 0.15 | 79 | 4.64
549.56 | 277.378 | 5.8 | 1606 |  |  |  | 61.92 | 277.449 | 5.92 | 1612 |  |  |  | 61.919 | 277.334 | 5.83 | 1614 |  |  |  | 61.919 | 528.49 | 0.15 | 79 | 4.64
550.06 | 277.438 | 5.79 | 1602 |  |  |  | 61.92 | 277.351 | 5.9 | 1605 |  |  |  | 61.919 | 277.3 | 5.83 | 1614 |  |  |  | 61.92 | 526.94 | 0.148 | 78 | 4.64
550.56 | 277.438 | 5.79 | 1602 |  |  |  | 61.92 | 277.351 | 5.9 | 1605 |  |  |  | 61.919 | 277.3 | 5.83 | 1614 |  |  |  | 61.92 | 526.94 | 0.148 | 78 | 4.64
551.06 | 277.374 | 5.82 | 1609 |  |  |  | 61.921 | 277.511 | 5.93 | 1614 |  |  |  | 61.921 | 277.265 | 5.83 | 1615 |  |  |  | 61.92 | 532.02 | 0.146 | 78 | 4.64
551.56 | 277.374 | 5.82 | 1609 |  |  |  | 61.921 | 277.511 | 5.93 | 1614 |  |  |  | 61.921 | 277.265 | 5.83 | 1615 |  |  |  | 61.92 | 532.02 | 0.146 | 78 | 4.64
552.06 | 277.426 | 5.82 | 1611 |  |  |  | 61.919 | 277.389 | 5.96 | 1622 |  |  |  | 61.92 | 277.366 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.144 | 77 | 4.64
552.56 | 277.426 | 5.82 | 1611 |  |  |  | 61.919 | 277.389 | 5.96 | 1622 |  |  |  | 61.92 | 277.366 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.144 | 77 | 4.64
553.06 | 277.377 | 5.82 | 1609 |  |  |  | 61.921 | 277.558 | 5.96 | 1622 |  |  |  | 61.923 | 277.353 | 5.85 | 1621 |  |  |  | 61.921 | 533.38 | 0.148 | 79 | 4.64
553.56 | 277.377 | 5.82 | 1609 |  |  |  | 61.921 | 277.558 | 5.96 | 1622 |  |  |  | 61.923 | 277.353 | 5.85 | 1621 |  |  |  | 61.921 | 533.38 | 0.148 | 79 | 4.64
554.07 | 277.449 | 5.82 | 1612 |  |  |  | 61.922 | 277.427 | 5.94 | 1618 |  |  |  | 61.919 | 277.326 | 5.86 | 1622 |  |  |  | 61.92 | 533.46 | 0.15 | 80 | 4.64
554.57 | 277.449 | 5.82 | 1612 |  |  |  | 61.922 | 277.427 | 5.94 | 1618 |  |  |  | 61.919 | 277.326 | 5.86 | 1622 |  |  |  | 61.92 | 533.46 | 0.15 | 80 | 4.64
555.06 | 277.358 | 5.81 | 1608 |  |  |  | 61.92 | 277.435 | 5.91 | 1611 |  |  |  | 61.92 | 277.272 | 5.83 | 1615 |  |  |  | 61.92 | 538.2 | 0.151 | 81 | 4.64
555.56 | 277.358 | 5.81 | 1608 |  |  |  | 61.92 | 277.435 | 5.91 | 1611 |  |  |  | 61.92 | 277.272 | 5.83 | 1615 |  |  |  | 61.92 | 538.2 | 0.151 | 81 | 4.64
556.06 | 277.416 | 5.65 | 1562 |  |  |  | 61.921 | 277.49 | 5.78 | 1572 |  |  |  | 61.92 | 277.361 | 5.67 | 1570 |  |  |  | 61.92 | 539.79 | 0.154 | 83 | 4.64
556.56 | 277.416 | 5.65 | 1562 |  |  |  | 61.921 | 277.49 | 5.78 | 1572 |  |  |  | 61.92 | 277.361 | 5.67 | 1570 |  |  |  | 61.92 | 539.79 | 0.154 | 83 | 4.64
557.06 | 277.347 | 5.85 | 1618 |  |  |  | 61.92 | 277.31 | 5.97 | 1625 |  |  |  | 61.919 | 277.344 | 5.86 | 1624 |  |  |  | 61.919 | 534.72 | 0.152 | 81 | 4.64
557.56 | 277.347 | 5.85 | 1618 |  |  |  | 61.92 | 277.31 | 5.97 | 1625 |  |  |  | 61.919 | 277.344 | 5.86 | 1624 |  |  |  | 61.919 | 534.72 | 0.152 | 81 | 4.64
558.06 | 277.411 | 5.81 | 1608 |  |  |  | 61.921 | 277.514 | 5.93 | 1615 |  |  |  | 61.92 | 277.326 | 5.87 | 1625 |  |  |  | 61.919 | 533.4 | 0.151 | 81 | 4.64
558.56 | 277.411 | 5.81 | 1608 |  |  |  | 61.921 | 277.514 | 5.93 | 1615 |  |  |  | 61.92 | 277.326 | 5.87 | 1625 |  |  |  | 61.919 | 533.4 | 0.151 | 81 | 4.64
559.06 | 277.473 | 5.83 | 1615 |  |  |  | 61.92 | 277.38 | 5.95 | 1617 |  |  |  | 61.92 | 277.287 | 5.85 | 1619 |  |  |  | 61.921 | 533.42 | 0.151 | 80 | 4.64
559.56 | 277.473 | 5.83 | 1615 |  |  |  | 61.92 | 277.38 | 5.95 | 1617 |  |  |  | 61.92 | 277.287 | 5.85 | 1619 |  |  |  | 61.921 | 533.42 | 0.151 | 80 | 4.64
560.07 | 277.408 | 5.84 | 1616 |  |  |  | 61.92 | 277.565 | 5.96 | 1622 |  |  |  | 61.923 | 277.377 | 5.85 | 1619 |  |  |  | 61.923 | 533.44 | 0.151 | 80 | 4.64
560.57 | 277.408 | 5.84 | 1616 |  |  |  | 61.92 | 277.565 | 5.96 | 1622 |  |  |  | 61.923 | 277.377 | 5.85 | 1619 |  |  |  | 61.923 | 533.44 | 0.151 | 80 | 4.64
561.06 | 277.456 | 5.79 | 1603 |  |  |  | 61.92 | 277.435 | 5.92 | 1609 |  |  |  | 61.919 | 277.342 | 5.82 | 1612 |  |  |  | 61.92 | 528.53 | 0.147 | 78 | 4.64
561.56 | 277.456 | 5.79 | 1603 |  |  |  | 61.92 | 277.435 | 5.92 | 1609 |  |  |  | 61.919 | 277.342 | 5.82 | 1612 |  |  |  | 61.92 | 528.53 | 0.147 | 78 | 4.64
562.06 | 277.375 | 5.78 | 1598 |  |  |  | 61.921 | 277.323 | 5.91 | 1607 |  |  |  | 61.919 | 277.32 | 5.81 | 1610 |  |  |  | 61.92 | 526.96 | 0.151 | 79 | 4.64
562.56 | 277.375 | 5.78 | 1598 |  |  |  | 61.921 | 277.323 | 5.91 | 1607 |  |  |  | 61.919 | 277.32 | 5.81 | 1610 |  |  |  | 61.92 | 526.96 | 0.151 | 79 | 4.64
563.06 | 277.445 | 5.82 | 1609 |  |  |  | 61.92 | 277.468 | 5.93 | 1613 |  |  |  | 61.921 | 277.292 | 5.85 | 1619 |  |  |  | 61.921 | 532.04 | 0.152 | 81 | 4.64
563.56 | 277.445 | 5.82 | 1609 |  |  |  | 61.92 | 277.468 | 5.93 | 1613 |  |  |  | 61.921 | 277.292 | 5.85 | 1619 |  |  |  | 61.921 | 532.04 | 0.152 | 81 | 4.64
564.06 | 277.361 | 5.84 | 1616 |  |  |  | 61.92 | 277.296 | 5.95 | 1621 |  |  |  | 61.919 | 277.252 | 5.84 | 1617 |  |  |  | 61.92 | 533.43 | 0.15 | 80 | 4.64
564.56 | 277.361 | 5.84 | 1616 |  |  |  | 61.92 | 277.296 | 5.95 | 1621 |  |  |  | 61.919 | 277.252 | 5.84 | 1617 |  |  |  | 61.92 | 533.43 | 0.15 | 80 | 4.64
565.06 | 277.421 | 5.83 | 1612 |  |  |  | 61.921 | 277.529 | 5.95 | 1619 |  |  |  | 61.92 | 277.345 | 5.84 | 1618 |  |  |  | 61.92 | 533.44 | 0.151 | 81 | 4.64
565.56 | 277.421 | 5.83 | 1612 |  |  |  | 61.921 | 277.529 | 5.95 | 1619 |  |  |  | 61.92 | 277.345 | 5.84 | 1618 |  |  |  | 61.92 | 533.44 | 0.151 | 81 | 4.64
566.07 | 277.352 | 5.82 | 1610 |  |  |  | 61.919 | 277.331 | 5.95 | 1618 |  |  |  | 61.92 | 277.314 | 5.86 | 1623 |  |  |  | 61.921 | 533.48 | 0.146 | 78 | 4.64
566.57 | 277.352 | 5.82 | 1610 |  |  |  | 61.919 | 277.331 | 5.95 | 1618 |  |  |  | 61.92 | 277.314 | 5.86 | 1623 |  |  |  | 61.921 | 533.48 | 0.146 | 78 | 4.64
567.06 | 277.414 | 5.8 | 1605 |  |  |  | 61.921 | 277.486 | 5.93 | 1614 |  |  |  | 61.922 | 277.288 | 5.84 | 1616 |  |  |  | 61.92 | 538.23 | 0.148 | 79 | 4.64
567.56 | 277.414 | 5.8 | 1605 |  |  |  | 61.921 | 277.486 | 5.93 | 1614 |  |  |  | 61.922 | 277.288 | 5.84 | 1616 |  |  |  | 61.92 | 538.23 | 0.148 | 79 | 4.64
568.06 | 277.457 | 5.64 | 1562 |  |  |  | 61.92 | 277.416 | 5.77 | 1569 |  |  |  | 61.919 | 277.259 | 5.66 | 1566 |  |  |  | 61.92 | 539.85 | 0.154 | 83 | 4.64
568.56 | 277.457 | 5.64 | 1562 |  |  |  | 61.92 | 277.416 | 5.77 | 1569 |  |  |  | 61.919 | 277.259 | 5.66 | 1566 |  |  |  | 61.92 | 539.85 | 0.154 | 83 | 4.64
569.06 | 277.405 | 5.83 | 1612 |  |  |  | 61.921 | 277.291 | 5.97 | 1622 |  |  |  | 61.918 | 277.367 | 5.86 | 1623 |  |  |  | 61.921 | 534.82 | 0.148 | 79 | 4.64
569.56 | 277.405 | 5.83 | 1612 |  |  |  | 61.921 | 277.291 | 5.97 | 1622 |  |  |  | 61.918 | 277.367 | 5.86 | 1623 |  |  |  | 61.921 | 534.82 | 0.148 | 79 | 4.64
570.06 | 277.458 | 5.81 | 1609 |  |  |  | 61.921 | 277.475 | 5.94 | 1617 |  |  |  | 61.921 | 277.327 | 5.86 | 1623 |  |  |  | 61.921 | 533.44 | 0.152 | 81 | 4.64
570.6 | 277.458 | 5.81 | 1609 |  |  |  | 61.921 | 277.475 | 5.94 | 1617 |  |  |  | 61.921 | 277.327 | 5.86 | 1623 |  |  |  | 61.921 | 533.44 | 0.152 | 81 | 4.64
571.1 | 277.373 | 5.82 | 1612 |  |  |  | 61.919 | 277.347 | 5.96 | 1621 |  |  |  | 61.919 | 277.298 | 5.86 | 1621 |  |  |  | 61.92 | 533.4 | 0.155 | 83 | 4.64
571.58 | 277.373 | 5.82 | 1612 |  |  |  | 61.919 | 277.347 | 5.96 | 1621 |  |  |  | 61.919 | 277.298 | 5.86 | 1621 |  |  |  | 61.92 | 533.4 | 0.155 | 83 | 4.64
572.08 | 277.454 | 5.84 | 1617 |  |  |  | 61.921 | 277.514 | 5.96 | 1623 |  |  |  | 61.922 | 277.276 | 5.86 | 1622 |  |  |  | 61.92 | 533.44 | 0.147 | 78 | 4.64
572.57 | 277.454 | 5.84 | 1617 |  |  |  | 61.921 | 277.514 | 5.96 | 1623 |  |  |  | 61.922 | 277.276 | 5.86 | 1622 |  |  |  | 61.92 | 533.44 | 0.147 | 78 | 4.64
573.07 | 277.355 | 5.8 | 1604 |  |  |  | 61.92 | 277.342 | 5.94 | 1615 |  |  |  | 61.92 | 277.376 | 5.82 | 1612 |  |  |  | 61.921 | 528.68 | 0.153 | 81 | 4.64
573.56 | 277.355 | 5.8 | 1604 |  |  |  | 61.92 | 277.342 | 5.94 | 1615 |  |  |  | 61.92 | 277.376 | 5.82 | 1612 |  |  |  | 61.921 | 528.68 | 0.153 | 81 | 4.64
574.06 | 277.424 | 5.78 | 1600 |  |  |  | 61.921 | 277.43 | 5.92 | 1610 |  |  |  | 61.92 | 277.339 | 5.8 | 1606 |  |  |  | 61.92 | 526.97 | 0.148 | 78 | 4.64
574.59 | 277.352 | 5.81 | 1608 |  |  |  | 61.92 | 277.403 | 5.94 | 1615 |  |  |  | 61.92 | 277.306 | 5.85 | 1620 |  |  |  | 61.92 | 531.93 | 0.148 | 79 | 4.64
575.09 | 277.352 | 5.81 | 1608 |  |  |  | 61.92 | 277.403 | 5.94 | 1615 |  |  |  | 61.92 | 277.306 | 5.85 | 1620 |  |  |  | 61.92 | 531.93 | 0.148 | 79 | 4.64
575.58 | 277.409 | 5.83 | 1613 |  |  |  | 61.921 | 277.295 | 5.95 | 1621 |  |  |  | 61.92 | 277.275 | 5.85 | 1620 |  |  |  | 61.92 | 533.43 | 0.151 | 81 | 4.64
576.08 | 277.409 | 5.83 | 1613 |  |  |  | 61.921 | 277.295 | 5.95 | 1621 |  |  |  | 61.92 | 277.275 | 5.85 | 1620 |  |  |  | 61.92 | 533.43 | 0.151 | 81 | 4.64
576.56 | 277.465 | 5.82 | 1611 |  |  |  | 61.92 | 277.499 | 5.96 | 1624 |  |  |  | 61.919 | 277.375 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.149 | 79 | 4.64
577.06 | 277.465 | 5.82 | 1611 |  |  |  | 61.92 | 277.499 | 5.96 | 1624 |  |  |  | 61.919 | 277.375 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.149 | 79 | 4.64
577.56 | 277.405 | 5.8 | 1606 |  |  |  | 61.921 | 277.348 | 5.95 | 1617 |  |  |  | 61.919 | 277.359 | 5.86 | 1623 |  |  |  | 61.921 | 533.41 | 0.148 | 79 | 4.64
578.07 | 277.405 | 5.8 | 1606 |  |  |  | 61.921 | 277.348 | 5.95 | 1617 |  |  |  | 61.919 | 277.359 | 5.86 | 1623 |  |  |  | 61.921 | 533.41 | 0.148 | 79 | 4.64
578.57 | 277.454 | 5.8 | 1605 |  |  |  | 61.921 | 277.559 | 5.92 | 1612 |  |  |  | 61.922 | 277.318 | 5.83 | 1613 |  |  |  | 61.92 | 538.16 | 0.148 | 80 | 4.64
579.06 | 277.454 | 5.8 | 1605 |  |  |  | 61.921 | 277.559 | 5.92 | 1612 |  |  |  | 61.922 | 277.318 | 5.83 | 1613 |  |  |  | 61.92 | 538.16 | 0.148 | 80 | 4.64
579.56 | 277.364 | 5.65 | 1563 |  |  |  | 61.92 | 277.419 | 5.77 | 1566 |  |  |  | 61.92 | 277.279 | 5.68 | 1572 |  |  |  | 61.92 | 539.86 | 0.152 | 82 | 4.64
580.06 | 277.364 | 5.65 | 1563 |  |  |  | 61.92 | 277.419 | 5.77 | 1566 |  |  |  | 61.92 | 277.279 | 5.68 | 1572 |  |  |  | 61.92 | 539.86 | 0.152 | 82 | 4.64
580.56 | 277.447 | 5.83 | 1615 |  |  |  | 61.92 | 277.318 | 5.97 | 1625 |  |  |  | 61.919 | 277.353 | 5.84 | 1619 |  |  |  | 61.921 | 534.92 | 0.148 | 79 | 4.64
581.06 | 277.447 | 5.83 | 1615 |  |  |  | 61.92 | 277.318 | 5.97 | 1625 |  |  |  | 61.919 | 277.353 | 5.84 | 1619 |  |  |  | 61.921 | 534.92 | 0.148 | 79 | 4.64
581.56 | 277.364 | 5.83 | 1614 |  |  |  | 61.919 | 277.461 | 5.95 | 1620 |  |  |  | 61.92 | 277.35 | 5.85 | 1621 |  |  |  | 61.921 | 533.45 | 0.142 | 76 | 4.64
582.06 | 277.364 | 5.83 | 1614 |  |  |  | 61.919 | 277.461 | 5.95 | 1620 |  |  |  | 61.92 | 277.35 | 5.85 | 1621 |  |  |  | 61.921 | 533.45 | 0.142 | 76 | 4.64
582.56 | 277.42 | 5.83 | 1613 |  |  |  | 61.92 | 277.364 | 5.95 | 1620 |  |  |  | 61.919 | 277.325 | 5.86 | 1622 |  |  |  | 61.92 | 533.4 | 0.148 | 79 | 4.64
583.06 | 277.42 | 5.83 | 1613 |  |  |  | 61.92 | 277.364 | 5.95 | 1620 |  |  |  | 61.919 | 277.325 | 5.86 | 1622 |  |  |  | 61.92 | 533.4 | 0.148 | 79 | 4.64
583.56 | 277.361 | 5.82 | 1611 |  |  |  | 61.92 | 277.502 | 5.95 | 1619 |  |  |  | 61.92 | 277.287 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.149 | 79 | 4.64
584.07 | 277.361 | 5.82 | 1611 |  |  |  | 61.92 | 277.502 | 5.95 | 1619 |  |  |  | 61.92 | 277.287 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.149 | 79 | 4.64
584.57 | 277.413 | 5.81 | 1608 |  |  |  | 61.92 | 277.394 | 5.93 | 1612 |  |  |  | 61.919 | 277.252 | 5.84 | 1616 |  |  |  | 61.92 | 528.71 | 0.149 | 79 | 4.64
585.06 | 277.413 | 5.81 | 1608 |  |  |  | 61.92 | 277.394 | 5.93 | 1612 |  |  |  | 61.919 | 277.252 | 5.84 | 1616 |  |  |  | 61.92 | 528.71 | 0.149 | 79 | 4.64
585.56 | 277.458 | 5.78 | 1601 |  |  |  | 61.92 | 277.585 | 5.9 | 1605 |  |  |  | 61.922 | 277.362 | 5.81 | 1609 |  |  |  | 61.919 | 526.97 | 0.151 | 79 | 4.64
586.06 | 277.458 | 5.78 | 1601 |  |  |  | 61.92 | 277.585 | 5.9 | 1605 |  |  |  | 61.922 | 277.362 | 5.81 | 1609 |  |  |  | 61.919 | 526.97 | 0.151 | 79 | 4.64
586.56 | 277.393 | 5.83 | 1612 |  |  |  | 61.92 | 277.463 | 5.94 | 1617 |  |  |  | 61.92 | 277.336 | 5.84 | 1619 |  |  |  | 61.92 | 531.87 | 0.15 | 80 | 4.64
587.06 | 277.393 | 5.83 | 1612 |  |  |  | 61.92 | 277.463 | 5.94 | 1617 |  |  |  | 61.92 | 277.336 | 5.84 | 1619 |  |  |  | 61.92 | 531.87 | 0.15 | 80 | 4.64
587.56 | 277.456 | 5.82 | 1611 |  |  |  | 61.921 | 277.309 | 5.95 | 1621 |  |  |  | 61.919 | 277.298 | 5.86 | 1622 |  |  |  | 61.921 | 533.39 | 0.149 | 79 | 4.64
588.06 | 277.456 | 5.82 | 1611 |  |  |  | 61.921 | 277.309 | 5.95 | 1621 |  |  |  | 61.919 | 277.298 | 5.86 | 1622 |  |  |  | 61.921 | 533.39 | 0.149 | 79 | 4.64
588.56 | 277.382 | 5.83 | 1612 |  |  |  | 61.921 | 277.529 | 5.95 | 1620 |  |  |  | 61.919 | 277.264 | 5.86 | 1622 |  |  |  | 61.921 | 533.37 | 0.152 | 81 | 4.64
589.06 | 277.382 | 5.83 | 1612 |  |  |  | 61.921 | 277.529 | 5.95 | 1620 |  |  |  | 61.919 | 277.264 | 5.86 | 1622 |  |  |  | 61.921 | 533.37 | 0.152 | 81 | 4.64
589.56 | 277.454 | 5.83 | 1613 |  |  |  | 61.92 | 277.378 | 5.94 | 1616 |  |  |  | 61.92 | 277.359 | 5.86 | 1623 |  |  |  | 61.921 | 533.39 | 0.149 | 79 | 4.64
590.07 | 277.454 | 5.83 | 1613 |  |  |  | 61.92 | 277.378 | 5.94 | 1616 |  |  |  | 61.92 | 277.359 | 5.86 | 1623 |  |  |  | 61.921 | 533.39 | 0.149 | 79 | 4.64
590.57 | 277.375 | 5.82 | 1611 |  |  |  | 61.92 | 277.559 | 5.93 | 1615 |  |  |  | 61.923 | 277.343 | 5.83 | 1615 |  |  |  | 61.921 | 538.07 | 0.147 | 79 | 4.64
591.06 | 277.375 | 5.82 | 1611 |  |  |  | 61.92 | 277.559 | 5.93 | 1615 |  |  |  | 61.923 | 277.343 | 5.83 | 1615 |  |  |  | 61.921 | 538.07 | 0.147 | 79 | 4.64
591.56 | 277.418 | 5.66 | 1566 |  |  |  | 61.921 | 277.429 | 5.77 | 1570 |  |  |  | 61.919 | 277.298 | 5.67 | 1569 |  |  |  | 61.92 | 539.79 | 0.149 | 80 | 4.64
592.06 | 277.418 | 5.66 | 1566 |  |  |  | 61.921 | 277.429 | 5.77 | 1570 |  |  |  | 61.919 | 277.298 | 5.67 | 1569 |  |  |  | 61.92 | 539.79 | 0.149 | 80 | 4.64
592.56 | 277.359 | 5.82 | 1609 |  |  |  | 61.92 | 277.563 | 5.95 | 1621 |  |  |  | 61.92 | 277.261 | 5.85 | 1620 |  |  |  | 61.921 | 534.9 | 0.149 | 80 | 4.64
593.06 | 277.359 | 5.82 | 1609 |  |  |  | 61.92 | 277.563 | 5.95 | 1621 |  |  |  | 61.92 | 277.261 | 5.85 | 1620 |  |  |  | 61.921 | 534.9 | 0.149 | 80 | 4.64
593.56 | 277.43 | 5.82 | 1610 |  |  |  | 61.919 | 277.476 | 5.95 | 1619 |  |  |  | 61.92 | 277.365 | 5.86 | 1623 |  |  |  | 61.921 | 533.37 | 0.146 | 78 | 4.64
594.06 | 277.43 | 5.82 | 1610 |  |  |  | 61.919 | 277.476 | 5.95 | 1619 |  |  |  | 61.92 | 277.365 | 5.86 | 1623 |  |  |  | 61.921 | 533.37 | 0.146 | 78 | 4.64
594.56 | 277.47 | 5.84 | 1616 |  |  |  | 61.92 | 277.325 | 5.93 | 1614 |  |  |  | 61.919 | 277.345 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
595.06 | 277.47 | 5.84 | 1616 |  |  |  | 61.92 | 277.325 | 5.93 | 1614 |  |  |  | 61.919 | 277.345 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
595.56 | 277.406 | 5.84 | 1616 |  |  |  | 61.921 | 277.536 | 5.94 | 1617 |  |  |  | 61.92 | 277.32 | 5.84 | 1617 |  |  |  | 61.92 | 533.4 | 0.151 | 80 | 4.64
596.07 | 277.406 | 5.84 | 1616 |  |  |  | 61.921 | 277.536 | 5.94 | 1617 |  |  |  | 61.92 | 277.32 | 5.84 | 1617 |  |  |  | 61.92 | 533.4 | 0.151 | 80 | 4.64
596.57 | 277.469 | 5.81 | 1607 |  |  |  | 61.921 | 277.365 | 5.94 | 1616 |  |  |  | 61.92 | 277.282 | 5.83 | 1614 |  |  |  | 61.921 | 528.73 | 0.143 | 75 | 4.64
597.06 | 277.469 | 5.81 | 1607 |  |  |  | 61.921 | 277.365 | 5.94 | 1616 |  |  |  | 61.92 | 277.282 | 5.83 | 1614 |  |  |  | 61.921 | 528.73 | 0.143 | 75 | 4.64
597.56 | 277.374 | 5.78 | 1600 |  |  |  | 61.921 | 277.569 | 5.91 | 1611 |  |  |  | 61.923 | 277.365 | 5.81 | 1608 |  |  |  | 61.92 | 526.94 | 0.148 | 78 | 4.64
598.06 | 277.374 | 5.78 | 1600 |  |  |  | 61.921 | 277.569 | 5.91 | 1611 |  |  |  | 61.923 | 277.365 | 5.81 | 1608 |  |  |  | 61.92 | 526.94 | 0.148 | 78 | 4.64
598.56 | 277.442 | 5.8 | 1605 |  |  |  | 61.921 | 277.434 | 5.93 | 1613 |  |  |  | 61.919 | 277.33 | 5.84 | 1617 |  |  |  | 61.92 | 531.78 | 0.146 | 78 | 4.64
599.06 | 277.442 | 5.8 | 1605 |  |  |  | 61.921 | 277.434 | 5.93 | 1613 |  |  |  | 61.919 | 277.33 | 5.84 | 1617 |  |  |  | 61.92 | 531.78 | 0.146 | 78 | 4.64
599.56 | 277.354 | 5.83 | 1612 |  |  |  | 61.92 | 277.39 | 5.93 | 1614 |  |  |  | 61.92 | 277.308 | 5.86 | 1624 |  |  |  | 61.919 | 533.38 | 0.146 | 78 | 4.64
600.06 | 277.354 | 5.83 | 1612 |  |  |  | 61.92 | 277.39 | 5.93 | 1614 |  |  |  | 61.92 | 277.308 | 5.86 | 1624 |  |  |  | 61.919 | 533.38 | 0.146 | 78 | 4.64
600.56 | 277.419 | 5.83 | 1612 |  |  |  | 61.92 | 277.488 | 5.93 | 1616 |  |  |  | 61.921 | 277.284 | 5.85 | 1621 |  |  |  | 61.921 | 533.42 | 0.15 | 80 | 4.64
601.06 | 277.419 | 5.83 | 1612 |  |  |  | 61.92 | 277.488 | 5.93 | 1616 |  |  |  | 61.921 | 277.284 | 5.85 | 1621 |  |  |  | 61.921 | 533.42 | 0.15 | 80 | 4.64
601.56 | 277.344 | 5.84 | 1614 |  |  |  | 61.92 | 277.336 | 5.95 | 1620 |  |  |  | 61.92 | 277.259 | 5.86 | 1621 |  |  |  | 61.919 | 533.41 | 0.147 | 79 | 4.64
602.07 | 277.344 | 5.84 | 1614 |  |  |  | 61.92 | 277.336 | 5.95 | 1620 |  |  |  | 61.92 | 277.259 | 5.86 | 1621 |  |  |  | 61.919 | 533.41 | 0.147 | 79 | 4.64
602.57 | 277.423 | 5.81 | 1608 |  |  |  | 61.92 | 277.496 | 5.94 | 1619 |  |  |  | 61.92 | 277.352 | 5.83 | 1613 |  |  |  | 61.92 | 538.04 | 0.147 | 79 | 4.64
603.08 | 277.423 | 5.81 | 1608 |  |  |  | 61.92 | 277.496 | 5.94 | 1619 |  |  |  | 61.92 | 277.352 | 5.83 | 1613 |  |  |  | 61.92 | 538.04 | 0.147 | 79 | 4.64
603.58 | 277.471 | 5.65 | 1563 |  |  |  | 61.921 | 277.359 | 5.77 | 1571 |  |  |  | 61.92 | 277.318 | 5.69 | 1575 |  |  |  | 61.92 | 539.79 | 0.146 | 79 | 4.64
604.07 | 277.471 | 5.65 | 1563 |  |  |  | 61.921 | 277.359 | 5.77 | 1571 |  |  |  | 61.92 | 277.318 | 5.69 | 1575 |  |  |  | 61.92 | 539.79 | 0.146 | 79 | 4.64
604.57 | 277.429 | 5.82 | 1611 |  |  |  | 61.921 | 277.551 | 5.94 | 1620 |  |  |  | 61.923 | 277.299 | 5.86 | 1623 |  |  |  | 61.92 | 535.01 | 0.149 | 80 | 4.64
605.06 | 277.429 | 5.82 | 1611 |  |  |  | 61.921 | 277.551 | 5.94 | 1620 |  |  |  | 61.923 | 277.299 | 5.86 | 1623 |  |  |  | 61.92 | 535.01 | 0.149 | 80 | 4.64
605.56 | 277.498 | 5.85 | 1618 |  |  |  | 61.92 | 277.39 | 5.94 | 1618 |  |  |  | 61.919 | 277.258 | 5.84 | 1617 |  |  |  | 61.919 | 533.42 | 0.144 | 77 | 4.64
606.09 | 277.403 | 5.83 | 1612 |  |  |  | 61.921 | 277.299 | 5.95 | 1620 |  |  |  | 61.92 | 277.357 | 5.84 | 1617 |  |  |  | 61.92 | 533.39 | 0.147 | 79 | 4.64
606.59 | 277.403 | 5.83 | 1612 |  |  |  | 61.921 | 277.299 | 5.95 | 1620 |  |  |  | 61.92 | 277.357 | 5.84 | 1617 |  |  |  | 61.92 | 533.39 | 0.147 | 79 | 4.64
607.08 | 277.47 | 5.82 | 1611 |  |  |  | 61.921 | 277.417 | 5.95 | 1619 |  |  |  | 61.92 | 277.32 | 5.86 | 1622 |  |  |  | 61.921 | 533.42 | 0.146 | 78 | 4.64
607.58 | 277.47 | 5.82 | 1611 |  |  |  | 61.921 | 277.417 | 5.95 | 1619 |  |  |  | 61.92 | 277.32 | 5.86 | 1622 |  |  |  | 61.921 | 533.42 | 0.146 | 78 | 4.64
608.07 | 277.387 | 5.8 | 1606 |  |  |  | 61.92 | 277.298 | 5.93 | 1614 |  |  |  | 61.919 | 277.289 | 5.83 | 1614 |  |  |  | 61.92 | 528.83 | 0.147 | 78 | 4.64
608.57 | 277.387 | 5.8 | 1606 |  |  |  | 61.92 | 277.298 | 5.93 | 1614 |  |  |  | 61.919 | 277.289 | 5.83 | 1614 |  |  |  | 61.92 | 528.83 | 0.147 | 78 | 4.64
609.06 | 277.443 | 5.78 | 1601 |  |  |  | 61.92 | 277.501 | 5.9 | 1606 |  |  |  | 61.923 | 277.261 | 5.8 | 1606 |  |  |  | 61.92 | 526.95 | 0.148 | 78 | 4.64
609.56 | 277.443 | 5.78 | 1601 |  |  |  | 61.92 | 277.501 | 5.9 | 1606 |  |  |  | 61.923 | 277.261 | 5.8 | 1606 |  |  |  | 61.92 | 526.95 | 0.148 | 78 | 4.64
610.06 | 277.365 | 5.83 | 1612 |  |  |  | 61.92 | 277.365 | 5.93 | 1615 |  |  |  | 61.92 | 277.367 | 5.82 | 1613 |  |  |  | 61.921 | 531.76 | 0.15 | 80 | 4.64
610.56 | 277.365 | 5.83 | 1612 |  |  |  | 61.92 | 277.365 | 5.93 | 1615 |  |  |  | 61.92 | 277.367 | 5.82 | 1613 |  |  |  | 61.921 | 531.76 | 0.15 | 80 | 4.64
611.06 | 277.442 | 5.83 | 1613 |  |  |  | 61.921 | 277.476 | 5.95 | 1622 |  |  |  | 61.921 | 277.337 | 5.84 | 1617 |  |  |  | 61.921 | 533.36 | 0.153 | 81 | 4.64
611.56 | 277.442 | 5.83 | 1613 |  |  |  | 61.921 | 277.476 | 5.95 | 1622 |  |  |  | 61.921 | 277.337 | 5.84 | 1617 |  |  |  | 61.921 | 533.36 | 0.153 | 81 | 4.64
612.06 | 277.495 | 5.82 | 1611 |  |  |  | 61.92 | 277.411 | 5.94 | 1618 |  |  |  | 61.919 | 277.306 | 5.86 | 1621 |  |  |  | 61.92 | 533.35 | 0.151 | 81 | 4.64
612.56 | 277.495 | 5.82 | 1611 |  |  |  | 61.92 | 277.411 | 5.94 | 1618 |  |  |  | 61.919 | 277.306 | 5.86 | 1621 |  |  |  | 61.92 | 533.35 | 0.151 | 81 | 4.64
613.06 | 277.42 | 5.81 | 1608 |  |  |  | 61.921 | 277.307 | 5.94 | 1619 |  |  |  | 61.921 | 277.284 | 5.86 | 1623 |  |  |  | 61.92 | 533.35 | 0.149 | 79 | 4.64
613.56 | 277.42 | 5.81 | 1608 |  |  |  | 61.921 | 277.307 | 5.94 | 1619 |  |  |  | 61.921 | 277.284 | 5.86 | 1623 |  |  |  | 61.92 | 533.35 | 0.149 | 79 | 4.64
614.07 | 277.49 | 5.8 | 1605 |  |  |  | 61.921 | 277.453 | 5.94 | 1619 |  |  |  | 61.92 | 277.368 | 5.84 | 1616 |  |  |  | 61.92 | 537.92 | 0.15 | 81 | 4.64
614.57 | 277.49 | 5.8 | 1605 |  |  |  | 61.921 | 277.453 | 5.94 | 1619 |  |  |  | 61.92 | 277.368 | 5.84 | 1616 |  |  |  | 61.92 | 537.92 | 0.15 | 81 | 4.64
615.06 | 277.401 | 5.66 | 1564 |  |  |  | 61.919 | 277.341 | 5.78 | 1571 |  |  |  | 61.919 | 277.337 | 5.67 | 1570 |  |  |  | 61.921 | 539.8 | 0.15 | 81 | 4.64
615.56 | 277.401 | 5.66 | 1564 |  |  |  | 61.919 | 277.341 | 5.78 | 1571 |  |  |  | 61.919 | 277.337 | 5.67 | 1570 |  |  |  | 61.921 | 539.8 | 0.15 | 81 | 4.64
616.06 | 277.473 | 5.84 | 1617 |  |  |  | 61.921 | 277.515 | 5.95 | 1621 |  |  |  | 61.923 | 277.305 | 5.85 | 1621 |  |  |  | 61.92 | 535.03 | 0.145 | 78 | 4.64
616.56 | 277.473 | 5.84 | 1617 |  |  |  | 61.921 | 277.515 | 5.95 | 1621 |  |  |  | 61.923 | 277.305 | 5.85 | 1621 |  |  |  | 61.92 | 535.03 | 0.145 | 78 | 4.64
617.06 | 277.368 | 5.82 | 1610 |  |  |  | 61.92 | 277.38 | 5.94 | 1617 |  |  |  | 61.92 | 277.282 | 5.85 | 1619 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
617.56 | 277.368 | 5.82 | 1610 |  |  |  | 61.92 | 277.38 | 5.94 | 1617 |  |  |  | 61.92 | 277.282 | 5.85 | 1619 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
618.06 | 277.427 | 5.81 | 1607 |  |  |  | 61.922 | 277.357 | 5.93 | 1615 |  |  |  | 61.92 | 277.369 | 5.85 | 1621 |  |  |  | 61.923 | 533.39 | 0.152 | 81 | 4.64
618.56 | 277.427 | 5.81 | 1607 |  |  |  | 61.922 | 277.357 | 5.93 | 1615 |  |  |  | 61.92 | 277.369 | 5.85 | 1621 |  |  |  | 61.923 | 533.39 | 0.152 | 81 | 4.64
619.06 | 277.344 | 5.83 | 1612 |  |  |  | 61.921 | 277.469 | 5.96 | 1622 |  |  |  | 61.92 | 277.36 | 5.87 | 1625 |  |  |  | 61.92 | 533.4 | 0.147 | 78 | 4.64
619.56 | 277.344 | 5.83 | 1612 |  |  |  | 61.921 | 277.469 | 5.96 | 1622 |  |  |  | 61.92 | 277.36 | 5.87 | 1625 |  |  |  | 61.92 | 533.4 | 0.147 | 78 | 4.64
620.07 | 277.417 | 5.81 | 1609 |  |  |  | 61.92 | 277.292 | 5.92 | 1610 |  |  |  | 61.92 | 277.319 | 5.83 | 1616 |  |  |  | 61.921 | 528.9 | 0.151 | 80 | 4.64
620.57 | 277.417 | 5.81 | 1609 |  |  |  | 61.92 | 277.292 | 5.92 | 1610 |  |  |  | 61.92 | 277.319 | 5.83 | 1616 |  |  |  | 61.921 | 528.9 | 0.151 | 80 | 4.64
621.06 | 277.471 | 5.78 | 1599 |  |  |  | 61.921 | 277.51 | 5.91 | 1611 |  |  |  | 61.92 | 277.289 | 5.83 | 1613 |  |  |  | 61.92 | 526.96 | 0.149 | 78 | 4.64
621.56 | 277.471 | 5.78 | 1599 |  |  |  | 61.921 | 277.51 | 5.91 | 1611 |  |  |  | 61.92 | 277.289 | 5.83 | 1613 |  |  |  | 61.92 | 526.96 | 0.149 | 78 | 4.64
622.06 | 277.388 | 5.81 | 1607 |  |  |  | 61.92 | 277.399 | 5.93 | 1616 |  |  |  | 61.919 | 277.272 | 5.84 | 1617 |  |  |  | 61.919 | 531.69 | 0.155 | 83 | 4.64
622.56 | 277.388 | 5.81 | 1607 |  |  |  | 61.92 | 277.399 | 5.93 | 1616 |  |  |  | 61.919 | 277.272 | 5.84 | 1617 |  |  |  | 61.919 | 531.69 | 0.155 | 83 | 4.64
623.06 | 277.455 | 5.82 | 1612 |  |  |  | 61.921 | 277.571 | 5.94 | 1619 |  |  |  | 61.923 | 277.357 | 5.86 | 1624 |  |  |  | 61.92 | 533.4 | 0.148 | 79 | 4.64
623.88 | 277.37 | 5.84 | 1615 |  |  |  | 61.92 | 277.451 | 5.94 | 1617 |  |  |  | 61.92 | 277.336 | 5.86 | 1624 |  |  |  | 61.92 | 533.4 | 0.15 | 80 | 4.64
624.06 | 277.37 | 5.84 | 1615 |  |  |  | 61.92 | 277.451 | 5.94 | 1617 |  |  |  | 61.92 | 277.336 | 5.86 | 1624 |  |  |  | 61.92 | 533.4 | 0.15 | 80 | 4.64
624.56 | 277.37 | 5.84 | 1615 |  |  |  | 61.92 | 277.451 | 5.94 | 1617 |  |  |  | 61.92 | 277.336 | 5.86 | 1624 |  |  |  | 61.92 | 533.4 | 0.15 | 80 | 4.64
625.06 | 278.112 | 6.38 | 1613 |  |  |  | 58.581 | 278.039 | 6.5 | 1624 |  |  |  | 58.579 | 277.93 | 6.43 | 1627 |  |  |  | 58.58 | 533.37 | 0.148 | 79 | 4.64
625.56 | 278.112 | 6.38 | 1613 |  |  |  | 58.581 | 278.039 | 6.5 | 1624 |  |  |  | 58.579 | 277.93 | 6.43 | 1627 |  |  |  | 58.58 | 533.37 | 0.148 | 79 | 4.64
626.07 | 278.777 | 6.29 | 1612 |  |  |  | 58.58 | 278.936 | 6.42 | 1624 |  |  |  | 58.579 | 278.629 | 6.32 | 1621 |  |  |  | 58.58 | 537.42 | 0.148 | 79 | 4.64
626.57 | 278.777 | 6.29 | 1612 |  |  |  | 58.58 | 278.936 | 6.42 | 1624 |  |  |  | 58.579 | 278.629 | 6.32 | 1621 |  |  |  | 58.58 | 537.42 | 0.148 | 79 | 4.64
627.06 | 278.129 | 5.86 | 1566 |  |  |  | 58.58 | 278.021 | 5.98 | 1570 |  |  |  | 58.581 | 278.018 | 5.89 | 1575 |  |  |  | 58.58 | 539.83 | 0.153 | 83 | 4.64
627.56 | 278.129 | 5.86 | 1566 |  |  |  | 58.58 | 278.021 | 5.98 | 1570 |  |  |  | 58.581 | 278.018 | 5.89 | 1575 |  |  |  | 58.58 | 539.83 | 0.153 | 83 | 4.64
628.06 | 277.659 | 5.93 | 1614 |  |  |  | 58.58 | 277.885 | 6.05 | 1623 |  |  |  | 58.58 | 277.636 | 5.98 | 1631 |  |  |  | 58.579 | 536.41 | 0.152 | 81 | 4.64
628.56 | 277.659 | 5.93 | 1614 |  |  |  | 58.58 | 277.885 | 6.05 | 1623 |  |  |  | 58.58 | 277.636 | 5.98 | 1631 |  |  |  | 58.579 | 536.41 | 0.152 | 81 | 4.64
629.06 | 277.584 | 5.87 | 1612 |  |  |  | 58.58 | 277.525 | 5.99 | 1619 |  |  |  | 58.581 | 277.44 | 5.91 | 1624 |  |  |  | 58.58 | 533.4 | 0.151 | 81 | 4.64
629.56 | 277.584 | 5.87 | 1612 |  |  |  | 58.58 | 277.525 | 5.99 | 1619 |  |  |  | 58.581 | 277.44 | 5.91 | 1624 |  |  |  | 58.58 | 533.4 | 0.151 | 81 | 4.64
630.06 | 277.519 | 5.86 | 1616 |  |  |  | 58.58 | 277.639 | 5.97 | 1619 |  |  |  | 58.583 | 277.351 | 5.86 | 1616 |  |  |  | 58.581 | 533.41 | 0.148 | 79 | 4.64
630.56 | 277.519 | 5.86 | 1616 |  |  |  | 58.58 | 277.639 | 5.97 | 1619 |  |  |  | 58.583 | 277.351 | 5.86 | 1616 |  |  |  | 58.581 | 533.41 | 0.148 | 79 | 4.64
631.06 | 277.417 | 5.84 | 1614 |  |  |  | 58.58 | 277.47 | 5.96 | 1621 |  |  |  | 58.579 | 277.413 | 5.87 | 1622 |  |  |  | 58.579 | 533.32 | 0.152 | 81 | 4.64
631.56 | 277.417 | 5.84 | 1614 |  |  |  | 58.58 | 277.47 | 5.96 | 1621 |  |  |  | 58.579 | 277.413 | 5.87 | 1622 |  |  |  | 58.579 | 533.32 | 0.152 | 81 | 4.64
632.07 | 277.47 | 5.84 | 1614 |  |  |  | 58.58 | 277.335 | 5.95 | 1619 |  |  |  | 58.579 | 277.384 | 5.86 | 1621 |  |  |  | 58.58 | 531.83 | 0.149 | 79 | 4.64
632.57 | 277.47 | 5.84 | 1614 |  |  |  | 58.58 | 277.335 | 5.95 | 1619 |  |  |  | 58.579 | 277.384 | 5.86 | 1621 |  |  |  | 58.58 | 531.83 | 0.149 | 79 | 4.64
633.06 | 277.374 | 5.78 | 1599 |  |  |  | 58.58 | 277.512 | 5.9 | 1607 |  |  |  | 58.58 | 277.34 | 5.82 | 1612 |  |  |  | 58.58 | 526.95 | 0.148 | 78 | 4.64
633.56 | 277.374 | 5.78 | 1599 |  |  |  | 58.58 | 277.512 | 5.9 | 1607 |  |  |  | 58.58 | 277.34 | 5.82 | 1612 |  |  |  | 58.58 | 526.95 | 0.148 | 78 | 4.64
634.08 | 277.435 | 5.8 | 1605 |  |  |  | 58.581 | 277.375 | 5.92 | 1611 |  |  |  | 58.579 | 277.284 | 5.83 | 1613 |  |  |  | 58.58 | 528.02 | 0.146 | 77 | 4.64
634.56 | 277.435 | 5.8 | 1605 |  |  |  | 58.581 | 277.375 | 5.92 | 1611 |  |  |  | 58.579 | 277.284 | 5.83 | 1613 |  |  |  | 58.58 | 528.02 | 0.146 | 77 | 4.64
635.06 | 275.479 | 6.47 | 1609 |  |  |  | 61.92 | 275.617 | 6.58 | 1617 |  |  |  | 61.924 | 275.514 | 6.48 | 1612 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
635.56 | 275.479 | 6.47 | 1609 |  |  |  | 61.92 | 275.617 | 6.58 | 1617 |  |  |  | 61.924 | 275.514 | 6.48 | 1612 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
636.06 | 276.174 | 6.45 | 1607 |  |  |  | 61.921 | 276.108 | 6.58 | 1616 |  |  |  | 61.92 | 276.141 | 6.48 | 1616 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
636.59 | 276.174 | 6.45 | 1607 |  |  |  | 61.921 | 276.108 | 6.58 | 1616 |  |  |  | 61.92 | 276.141 | 6.48 | 1616 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
637.09 | 276.735 | 6.14 | 1612 |  |  |  | 61.919 | 276.821 | 6.24 | 1615 |  |  |  | 61.92 | 276.754 | 6.14 | 1616 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
637.57 | 276.735 | 6.14 | 1612 |  |  |  | 61.919 | 276.821 | 6.24 | 1615 |  |  |  | 61.92 | 276.754 | 6.14 | 1616 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
638.07 | 277.19 | 5.96 | 1613 |  |  |  | 61.921 | 277.239 | 6.05 | 1612 |  |  |  | 61.919 | 277.051 | 5.99 | 1622 |  |  |  | 61.919 | 533.99 | 0.151 | 80 | 4.64
638.56 | 277.19 | 5.96 | 1613 |  |  |  | 61.921 | 277.239 | 6.05 | 1612 |  |  |  | 61.919 | 277.051 | 5.99 | 1622 |  |  |  | 61.919 | 533.99 | 0.151 | 80 | 4.64
639.06 | 277.349 | 5.69 | 1560 |  |  |  | 61.92 | 277.248 | 5.83 | 1569 |  |  |  | 61.92 | 277.222 | 5.71 | 1567 |  |  |  | 61.92 | 539.83 | 0.147 | 79 | 4.64
639.6 | 277.359 | 5.79 | 1595 |  |  |  | 61.921 | 277.536 | 5.93 | 1609 |  |  |  | 61.92 | 277.333 | 5.8 | 1600 |  |  |  | 61.921 | 539.04 | 0.15 | 81 | 4.64
640.1 | 277.359 | 5.79 | 1595 |  |  |  | 61.921 | 277.536 | 5.93 | 1609 |  |  |  | 61.92 | 277.333 | 5.8 | 1600 |  |  |  | 61.921 | 539.04 | 0.15 | 81 | 4.64
640.58 | 277.461 | 5.83 | 1611 |  |  |  | 61.921 | 277.428 | 5.95 | 1618 |  |  |  | 61.919 | 277.341 | 5.86 | 1619 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
641.08 | 277.461 | 5.83 | 1611 |  |  |  | 61.921 | 277.428 | 5.95 | 1618 |  |  |  | 61.919 | 277.341 | 5.86 | 1619 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
641.57 | 277.387 | 5.82 | 1611 |  |  |  | 61.919 | 277.593 | 5.94 | 1617 |  |  |  | 61.922 | 277.336 | 5.85 | 1620 |  |  |  | 61.921 | 533.4 | 0.148 | 79 | 4.64
642.07 | 277.387 | 5.82 | 1611 |  |  |  | 61.919 | 277.593 | 5.94 | 1617 |  |  |  | 61.922 | 277.336 | 5.85 | 1620 |  |  |  | 61.921 | 533.4 | 0.148 | 79 | 4.64
642.56 | 277.475 | 5.84 | 1618 |  |  |  | 61.921 | 277.47 | 5.95 | 1619 |  |  |  | 61.92 | 277.311 | 5.85 | 1620 |  |  |  | 61.92 | 533.36 | 0.154 | 82 | 4.64
643.06 | 277.475 | 5.84 | 1618 |  |  |  | 61.921 | 277.47 | 5.95 | 1619 |  |  |  | 61.92 | 277.311 | 5.85 | 1620 |  |  |  | 61.92 | 533.36 | 0.154 | 82 | 4.64
643.56 | 277.404 | 5.84 | 1615 |  |  |  | 61.921 | 277.376 | 5.95 | 1620 |  |  |  | 61.921 | 277.365 | 5.84 | 1618 |  |  |  | 61.92 | 532.83 | 0.152 | 81 | 4.64
644.07 | 277.404 | 5.84 | 1615 |  |  |  | 61.921 | 277.376 | 5.95 | 1620 |  |  |  | 61.921 | 277.365 | 5.84 | 1618 |  |  |  | 61.92 | 532.83 | 0.152 | 81 | 4.64
644.57 | 277.493 | 5.76 | 1594 |  |  |  | 61.919 | 277.525 | 5.91 | 1611 |  |  |  | 61.919 | 277.35 | 5.81 | 1609 |  |  |  | 61.92 | 526.98 | 0.143 | 76 | 4.64
645.06 | 277.493 | 5.76 | 1594 |  |  |  | 61.919 | 277.525 | 5.91 | 1611 |  |  |  | 61.919 | 277.35 | 5.81 | 1609 |  |  |  | 61.92 | 526.98 | 0.143 | 76 | 4.64
645.56 | 277.384 | 5.78 | 1599 |  |  |  | 61.921 | 277.384 | 5.9 | 1607 |  |  |  | 61.918 | 277.326 | 5.83 | 1613 |  |  |  | 61.92 | 527.62 | 0.15 | 79 | 4.64
646.06 | 277.384 | 5.78 | 1599 |  |  |  | 61.921 | 277.384 | 5.9 | 1607 |  |  |  | 61.918 | 277.326 | 5.83 | 1613 |  |  |  | 61.92 | 527.62 | 0.15 | 79 | 4.64
646.56 | 277.444 | 5.82 | 1612 |  |  |  | 61.919 | 277.578 | 5.93 | 1616 |  |  |  | 61.923 | 277.291 | 5.86 | 1623 |  |  |  | 61.919 | 533.4 | 0.146 | 78 | 4.64
647.06 | 277.444 | 5.82 | 1612 |  |  |  | 61.919 | 277.578 | 5.93 | 1616 |  |  |  | 61.923 | 277.291 | 5.86 | 1623 |  |  |  | 61.919 | 533.4 | 0.146 | 78 | 4.64
647.56 | 277.503 | 5.83 | 1613 |  |  |  | 61.921 | 277.452 | 5.93 | 1617 |  |  |  | 61.92 | 277.358 | 5.85 | 1620 |  |  |  | 61.921 | 533.36 | 0.147 | 78 | 4.64
648.06 | 277.503 | 5.83 | 1613 |  |  |  | 61.921 | 277.452 | 5.93 | 1617 |  |  |  | 61.92 | 277.358 | 5.85 | 1620 |  |  |  | 61.921 | 533.36 | 0.147 | 78 | 4.64
648.56 | 277.422 | 5.82 | 1610 |  |  |  | 61.921 | 277.452 | 5.95 | 1619 |  |  |  | 61.919 | 277.329 | 5.85 | 1619 |  |  |  | 61.921 | 533.36 | 0.152 | 81 | 4.64
649.06 | 277.422 | 5.82 | 1610 |  |  |  | 61.921 | 277.452 | 5.95 | 1619 |  |  |  | 61.919 | 277.329 | 5.85 | 1619 |  |  |  | 61.921 | 533.36 | 0.152 | 81 | 4.64
649.56 | 277.488 | 5.83 | 1613 |  |  |  | 61.92 | 277.45 | 5.94 | 1616 |  |  |  | 61.92 | 277.299 | 5.86 | 1622 |  |  |  | 61.919 | 533.86 | 0.149 | 80 | 4.64
650.07 | 277.488 | 5.83 | 1613 |  |  |  | 61.92 | 277.45 | 5.94 | 1616 |  |  |  | 61.92 | 277.299 | 5.86 | 1622 |  |  |  | 61.919 | 533.86 | 0.149 | 80 | 4.64
650.57 | 277.415 | 5.66 | 1565 |  |  |  | 61.92 | 277.312 | 5.76 | 1565 |  |  |  | 61.919 | 277.262 | 5.67 | 1570 |  |  |  | 61.92 | 539.85 | 0.149 | 80 | 4.64
651.06 | 277.415 | 5.66 | 1565 |  |  |  | 61.92 | 277.312 | 5.76 | 1565 |  |  |  | 61.919 | 277.262 | 5.67 | 1570 |  |  |  | 61.92 | 539.85 | 0.149 | 80 | 4.64
651.56 | 277.468 | 5.77 | 1596 |  |  |  | 61.92 | 277.477 | 5.89 | 1605 |  |  |  | 61.921 | 277.36 | 5.81 | 1609 |  |  |  | 61.92 | 539.08 | 0.156 | 84 | 4.64
652.06 | 277.468 | 5.77 | 1596 |  |  |  | 61.92 | 277.477 | 5.89 | 1605 |  |  |  | 61.921 | 277.36 | 5.81 | 1609 |  |  |  | 61.92 | 539.08 | 0.156 | 84 | 4.64
652.56 | 277.411 | 5.84 | 1615 |  |  |  | 61.92 | 277.378 | 5.94 | 1617 |  |  |  | 61.92 | 277.339 | 5.86 | 1622 |  |  |  | 61.92 | 533.43 | 0.154 | 82 | 4.64
653.06 | 277.411 | 5.84 | 1615 |  |  |  | 61.92 | 277.378 | 5.94 | 1617 |  |  |  | 61.92 | 277.339 | 5.86 | 1622 |  |  |  | 61.92 | 533.43 | 0.154 | 82 | 4.64
653.56 | 277.476 | 5.82 | 1612 |  |  |  | 61.92 | 277.551 | 5.93 | 1617 |  |  |  | 61.921 | 277.299 | 5.86 | 1623 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 4.64
654.06 | 277.476 | 5.82 | 1612 |  |  |  | 61.92 | 277.551 | 5.93 | 1617 |  |  |  | 61.921 | 277.299 | 5.86 | 1623 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 4.64
654.56 | 277.368 | 5.82 | 1611 |  |  |  | 61.92 | 277.415 | 5.95 | 1620 |  |  |  | 61.921 | 277.269 | 5.85 | 1619 |  |  |  | 61.92 | 533.41 | 0.153 | 82 | 4.64
655.06 | 277.368 | 5.82 | 1611 |  |  |  | 61.92 | 277.415 | 5.95 | 1620 |  |  |  | 61.921 | 277.269 | 5.85 | 1619 |  |  |  | 61.92 | 533.41 | 0.153 | 82 | 4.64
655.56 | 277.443 | 5.83 | 1614 |  |  |  | 61.921 | 277.283 | 5.95 | 1619 |  |  |  | 61.92 | 277.357 | 5.85 | 1620 |  |  |  | 61.922 | 532.9 | 0.156 | 83 | 4.64
656.07 | 277.443 | 5.83 | 1614 |  |  |  | 61.921 | 277.283 | 5.95 | 1619 |  |  |  | 61.92 | 277.357 | 5.85 | 1620 |  |  |  | 61.922 | 532.9 | 0.156 | 83 | 4.64
656.57 | 277.511 | 5.78 | 1600 |  |  |  | 61.921 | 277.509 | 5.9 | 1607 |  |  |  | 61.919 | 277.334 | 5.82 | 1612 |  |  |  | 61.92 | 526.92 | 0.149 | 79 | 4.64
657.06 | 277.511 | 5.78 | 1600 |  |  |  | 61.921 | 277.509 | 5.9 | 1607 |  |  |  | 61.919 | 277.334 | 5.82 | 1612 |  |  |  | 61.92 | 526.92 | 0.149 | 79 | 4.64
657.56 | 277.425 | 5.79 | 1601 |  |  |  | 61.921 | 277.303 | 5.91 | 1608 |  |  |  | 61.92 | 277.294 | 5.81 | 1608 |  |  |  | 61.92 | 527.57 | 0.15 | 79 | 4.64
658.06 | 277.425 | 5.79 | 1601 |  |  |  | 61.921 | 277.303 | 5.91 | 1608 |  |  |  | 61.92 | 277.294 | 5.81 | 1608 |  |  |  | 61.92 | 527.57 | 0.15 | 79 | 4.64
658.56 | 277.492 | 5.83 | 1614 |  |  |  | 61.921 | 277.501 | 5.95 | 1621 |  |  |  | 61.921 | 277.263 | 5.85 | 1621 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 4.64
659.06 | 277.492 | 5.83 | 1614 |  |  |  | 61.921 | 277.501 | 5.95 | 1621 |  |  |  | 61.921 | 277.263 | 5.85 | 1621 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 4.64
659.56 | 277.421 | 5.83 | 1613 |  |  |  | 61.921 | 277.369 | 5.94 | 1616 |  |  |  | 61.919 | 277.242 | 5.85 | 1621 |  |  |  | 61.92 | 533.33 | 0.153 | 82 | 4.64
660.06 | 277.421 | 5.83 | 1613 |  |  |  | 61.921 | 277.369 | 5.94 | 1616 |  |  |  | 61.919 | 277.242 | 5.85 | 1621 |  |  |  | 61.92 | 533.33 | 0.153 | 82 | 4.64
660.56 | 277.478 | 5.83 | 1613 |  |  |  | 61.92 | 277.51 | 5.95 | 1617 |  |  |  | 61.922 | 277.336 | 5.85 | 1620 |  |  |  | 61.921 | 533.4 | 0.148 | 79 | 4.64
661.06 | 277.478 | 5.83 | 1613 |  |  |  | 61.92 | 277.51 | 5.95 | 1617 |  |  |  | 61.922 | 277.336 | 5.85 | 1620 |  |  |  | 61.921 | 533.4 | 0.148 | 79 | 4.64
661.56 | 277.39 | 5.83 | 1614 |  |  |  | 61.92 | 277.422 | 5.97 | 1623 |  |  |  | 61.919 | 277.302 | 5.85 | 1620 |  |  |  | 61.92 | 533.87 | 0.155 | 83 | 4.64
662.07 | 277.39 | 5.83 | 1614 |  |  |  | 61.92 | 277.422 | 5.97 | 1623 |  |  |  | 61.919 | 277.302 | 5.85 | 1620 |  |  |  | 61.92 | 533.87 | 0.155 | 83 | 4.64
662.57 | 277.457 | 5.65 | 1563 |  |  |  | 61.919 | 277.294 | 5.77 | 1570 |  |  |  | 61.919 | 277.268 | 5.67 | 1570 |  |  |  | 61.92 | 539.82 | 0.155 | 83 | 4.64
663.06 | 277.457 | 5.65 | 1563 |  |  |  | 61.919 | 277.294 | 5.77 | 1570 |  |  |  | 61.919 | 277.268 | 5.67 | 1570 |  |  |  | 61.92 | 539.82 | 0.155 | 83 | 4.64
663.56 | 277.363 | 5.77 | 1596 |  |  |  | 61.92 | 277.493 | 5.88 | 1600 |  |  |  | 61.919 | 277.249 | 5.77 | 1598 |  |  |  | 61.92 | 539.25 | 0.152 | 82 | 4.64
664.06 | 277.363 | 5.77 | 1596 |  |  |  | 61.92 | 277.493 | 5.88 | 1600 |  |  |  | 61.919 | 277.249 | 5.77 | 1598 |  |  |  | 61.92 | 539.25 | 0.152 | 82 | 4.64
664.56 | 277.444 | 5.83 | 1612 |  |  |  | 61.92 | 277.341 | 5.97 | 1626 |  |  |  | 61.92 | 277.345 | 5.85 | 1620 |  |  |  | 61.918 | 533.42 | 0.154 | 82 | 4.64
665.06 | 277.444 | 5.83 | 1612 |  |  |  | 61.92 | 277.341 | 5.97 | 1626 |  |  |  | 61.92 | 277.345 | 5.85 | 1620 |  |  |  | 61.918 | 533.42 | 0.154 | 82 | 4.64
665.56 | 277.513 | 5.83 | 1615 |  |  |  | 61.921 | 277.557 | 5.95 | 1622 |  |  |  | 61.923 | 277.318 | 5.87 | 1626 |  |  |  | 61.92 | 533.41 | 0.15 | 80 | 4.64
666.06 | 277.513 | 5.83 | 1615 |  |  |  | 61.921 | 277.557 | 5.95 | 1622 |  |  |  | 61.923 | 277.318 | 5.87 | 1626 |  |  |  | 61.92 | 533.41 | 0.15 | 80 | 4.64
666.56 | 277.432 | 5.83 | 1614 |  |  |  | 61.92 | 277.394 | 5.94 | 1617 |  |  |  | 61.919 | 277.278 | 5.85 | 1621 |  |  |  | 61.919 | 533.47 | 0.149 | 79 | 4.64
667.06 | 277.432 | 5.83 | 1614 |  |  |  | 61.92 | 277.394 | 5.94 | 1617 |  |  |  | 61.919 | 277.278 | 5.85 | 1621 |  |  |  | 61.919 | 533.47 | 0.149 | 79 | 4.64
667.56 | 277.487 | 5.84 | 1616 |  |  |  | 61.92 | 277.372 | 5.94 | 1617 |  |  |  | 61.921 | 277.249 | 5.85 | 1619 |  |  |  | 61.92 | 532.95 | 0.157 | 84 | 4.64
668.09 | 277.487 | 5.84 | 1616 |  |  |  | 61.92 | 277.372 | 5.94 | 1617 |  |  |  | 61.921 | 277.249 | 5.85 | 1619 |  |  |  | 61.92 | 532.95 | 0.157 | 84 | 4.64
668.59 | 277.425 | 5.78 | 1598 |  |  |  | 61.921 | 277.46 | 5.9 | 1608 |  |  |  | 61.92 | 277.351 | 5.8 | 1607 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 4.64
669.07 | 277.425 | 5.78 | 1598 |  |  |  | 61.921 | 277.46 | 5.9 | 1608 |  |  |  | 61.92 | 277.351 | 5.8 | 1607 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 4.64
669.57 | 277.483 | 5.78 | 1599 |  |  |  | 61.92 | 277.322 | 5.9 | 1608 |  |  |  | 61.92 | 277.335 | 5.8 | 1607 |  |  |  | 61.921 | 527.54 | 0.147 | 78 | 4.64
670.06 | 277.483 | 5.78 | 1599 |  |  |  | 61.92 | 277.322 | 5.9 | 1608 |  |  |  | 61.92 | 277.335 | 5.8 | 1607 |  |  |  | 61.921 | 527.54 | 0.147 | 78 | 4.64
670.56 | 277.365 | 5.83 | 1613 |  |  |  | 61.921 | 277.52 | 5.94 | 1618 |  |  |  | 61.918 | 277.299 | 5.86 | 1624 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 4.64
671.1 | 277.442 | 5.84 | 1616 |  |  |  | 61.921 | 277.371 | 5.95 | 1620 |  |  |  | 61.92 | 277.258 | 5.84 | 1617 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 4.64
671.6 | 277.442 | 5.84 | 1616 |  |  |  | 61.921 | 277.371 | 5.95 | 1620 |  |  |  | 61.92 | 277.258 | 5.84 | 1617 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 4.64
672.08 | 277.312 | 5.83 | 1612 |  |  |  | 61.92 | 277.552 | 5.93 | 1615 |  |  |  | 61.922 | 277.36 | 5.85 | 1620 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
672.58 | 277.312 | 5.83 | 1612 |  |  |  | 61.92 | 277.552 | 5.93 | 1615 |  |  |  | 61.922 | 277.36 | 5.85 | 1620 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
673.06 | 277.384 | 5.81 | 1608 |  |  |  | 61.921 | 277.444 | 5.94 | 1618 |  |  |  | 61.919 | 277.34 | 5.84 | 1619 |  |  |  | 61.919 | 533.74 | 0.153 | 81 | 4.64
673.56 | 277.384 | 5.81 | 1608 |  |  |  | 61.921 | 277.444 | 5.94 | 1618 |  |  |  | 61.919 | 277.34 | 5.84 | 1619 |  |  |  | 61.919 | 533.74 | 0.153 | 81 | 4.64
674.07 | 277.448 | 5.63 | 1559 |  |  |  | 61.92 | 277.323 | 5.75 | 1565 |  |  |  | 61.92 | 277.306 | 5.66 | 1567 |  |  |  | 61.919 | 539.87 | 0.15 | 81 | 4.64
674.57 | 277.448 | 5.63 | 1559 |  |  |  | 61.92 | 277.323 | 5.75 | 1565 |  |  |  | 61.92 | 277.306 | 5.66 | 1567 |  |  |  | 61.919 | 539.87 | 0.15 | 81 | 4.64
675.06 | 277.37 | 5.75 | 1590 |  |  |  | 61.921 | 277.494 | 5.87 | 1600 |  |  |  | 61.921 | 277.265 | 5.78 | 1601 |  |  |  | 61.92 | 539.29 | 0.157 | 85 | 4.64
675.56 | 277.37 | 5.75 | 1590 |  |  |  | 61.921 | 277.494 | 5.87 | 1600 |  |  |  | 61.921 | 277.265 | 5.78 | 1601 |  |  |  | 61.92 | 539.29 | 0.157 | 85 | 4.64
676.06 | 277.425 | 5.83 | 1614 |  |  |  | 61.92 | 277.384 | 5.94 | 1618 |  |  |  | 61.919 | 277.358 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.152 | 81 | 4.64
676.56 | 277.425 | 5.83 | 1614 |  |  |  | 61.92 | 277.384 | 5.94 | 1618 |  |  |  | 61.919 | 277.358 | 5.86 | 1623 |  |  |  | 61.921 | 533.42 | 0.152 | 81 | 4.64
677.06 | 277.374 | 5.82 | 1611 |  |  |  | 61.921 | 277.555 | 5.94 | 1618 |  |  |  | 61.922 | 277.326 | 5.84 | 1618 |  |  |  | 61.92 | 533.36 | 0.152 | 81 | 4.64
677.56 | 277.374 | 5.82 | 1611 |  |  |  | 61.921 | 277.555 | 5.94 | 1618 |  |  |  | 61.922 | 277.326 | 5.84 | 1618 |  |  |  | 61.92 | 533.36 | 0.152 | 81 | 4.64
678.06 | 277.429 | 5.82 | 1609 |  |  |  | 61.92 | 277.417 | 5.95 | 1619 |  |  |  | 61.92 | 277.312 | 5.85 | 1620 |  |  |  | 61.919 | 533.4 | 0.155 | 83 | 4.64
678.56 | 277.429 | 5.82 | 1609 |  |  |  | 61.92 | 277.417 | 5.95 | 1619 |  |  |  | 61.92 | 277.312 | 5.85 | 1620 |  |  |  | 61.919 | 533.4 | 0.155 | 83 | 4.64
679.06 | 277.347 | 5.83 | 1612 |  |  |  | 61.921 | 277.455 | 5.95 | 1622 |  |  |  | 61.919 | 277.273 | 5.86 | 1623 |  |  |  | 61.921 | 533.06 | 0.153 | 82 | 4.64
679.56 | 277.347 | 5.83 | 1612 |  |  |  | 61.921 | 277.455 | 5.95 | 1622 |  |  |  | 61.919 | 277.273 | 5.86 | 1623 |  |  |  | 61.921 | 533.06 | 0.153 | 82 | 4.64
680.07 | 277.414 | 5.78 | 1599 |  |  |  | 61.92 | 277.48 | 5.9 | 1606 |  |  |  | 61.919 | 277.288 | 5.82 | 1611 |  |  |  | 61.92 | 526.99 | 0.151 | 79 | 4.64
680.57 | 277.414 | 5.78 | 1599 |  |  |  | 61.92 | 277.48 | 5.9 | 1606 |  |  |  | 61.919 | 277.288 | 5.82 | 1611 |  |  |  | 61.92 | 526.99 | 0.151 | 79 | 4.64
681.06 | 277.32 | 5.78 | 1598 |  |  |  | 61.919 | 277.336 | 5.92 | 1611 |  |  |  | 61.919 | 277.333 | 5.82 | 1612 |  |  |  | 61.921 | 527.49 | 0.151 | 80 | 4.64
681.56 | 277.32 | 5.78 | 1598 |  |  |  | 61.919 | 277.336 | 5.92 | 1611 |  |  |  | 61.919 | 277.333 | 5.82 | 1612 |  |  |  | 61.921 | 527.49 | 0.151 | 80 | 4.64
682.06 | 277.381 | 5.82 | 1611 |  |  |  | 61.92 | 277.498 | 5.95 | 1618 |  |  |  | 61.92 | 277.306 | 5.85 | 1619 |  |  |  | 61.92 | 533.35 | 0.152 | 81 | 4.64
682.56 | 277.381 | 5.82 | 1611 |  |  |  | 61.92 | 277.498 | 5.95 | 1618 |  |  |  | 61.92 | 277.306 | 5.85 | 1619 |  |  |  | 61.92 | 533.35 | 0.152 | 81 | 4.64
683.06 | 277.443 | 5.82 | 1611 |  |  |  | 61.92 | 277.384 | 5.96 | 1623 |  |  |  | 61.92 | 277.278 | 5.85 | 1621 |  |  |  | 61.921 | 533.42 | 0.155 | 83 | 4.64
683.56 | 277.443 | 5.82 | 1611 |  |  |  | 61.92 | 277.384 | 5.96 | 1623 |  |  |  | 61.92 | 277.278 | 5.85 | 1621 |  |  |  | 61.921 | 533.42 | 0.155 | 83 | 4.64
684.06 | 277.38 | 5.84 | 1617 |  |  |  | 61.921 | 277.571 | 5.94 | 1618 |  |  |  | 61.922 | 277.24 | 5.85 | 1621 |  |  |  | 61.919 | 533.38 | 0.151 | 81 | 4.64
684.56 | 277.38 | 5.84 | 1617 |  |  |  | 61.921 | 277.571 | 5.94 | 1618 |  |  |  | 61.922 | 277.24 | 5.85 | 1621 |  |  |  | 61.919 | 533.38 | 0.151 | 81 | 4.64
685.06 | 277.427 | 5.82 | 1612 |  |  |  | 61.92 | 277.439 | 5.95 | 1618 |  |  |  | 61.919 | 277.344 | 5.85 | 1620 |  |  |  | 61.919 | 533.75 | 0.15 | 80 | 4.64
685.56 | 277.427 | 5.82 | 1612 |  |  |  | 61.92 | 277.439 | 5.95 | 1618 |  |  |  | 61.919 | 277.344 | 5.85 | 1620 |  |  |  | 61.919 | 533.75 | 0.15 | 80 | 4.64
686.07 | 277.37 | 5.66 | 1565 |  |  |  | 61.921 | 277.307 | 5.78 | 1570 |  |  |  | 61.92 | 277.299 | 5.68 | 1572 |  |  |  | 61.92 | 539.85 | 0.156 | 84 | 4.64
686.57 | 277.37 | 5.66 | 1565 |  |  |  | 61.921 | 277.307 | 5.78 | 1570 |  |  |  | 61.92 | 277.299 | 5.68 | 1572 |  |  |  | 61.92 | 539.85 | 0.156 | 84 | 4.64
687.06 | 277.434 | 5.74 | 1587 |  |  |  | 61.921 | 277.531 | 5.86 | 1595 |  |  |  | 61.92 | 277.28 | 5.78 | 1600 |  |  |  | 61.921 | 539.29 | 0.154 | 83 | 4.64
687.56 | 277.434 | 5.74 | 1587 |  |  |  | 61.921 | 277.531 | 5.86 | 1595 |  |  |  | 61.92 | 277.28 | 5.78 | 1600 |  |  |  | 61.921 | 539.29 | 0.154 | 83 | 4.64
688.06 | 277.339 | 5.82 | 1611 |  |  |  | 61.919 | 277.346 | 5.95 | 1617 |  |  |  | 61.92 | 277.247 | 5.86 | 1622 |  |  |  | 61.919 | 533.4 | 0.153 | 81 | 4.64
688.56 | 277.339 | 5.82 | 1611 |  |  |  | 61.919 | 277.346 | 5.95 | 1617 |  |  |  | 61.92 | 277.247 | 5.86 | 1622 |  |  |  | 61.919 | 533.4 | 0.153 | 81 | 4.64
689.06 | 277.426 | 5.84 | 1615 |  |  |  | 61.921 | 277.536 | 5.94 | 1617 |  |  |  | 61.92 | 277.345 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.152 | 81 | 4.64
689.56 | 277.426 | 5.84 | 1615 |  |  |  | 61.921 | 277.536 | 5.94 | 1617 |  |  |  | 61.92 | 277.345 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.152 | 81 | 4.64
690.06 | 277.318 | 5.83 | 1613 |  |  |  | 61.917 | 277.412 | 5.94 | 1617 |  |  |  | 61.92 | 277.317 | 5.85 | 1620 |  |  |  | 61.92 | 533.37 | 0.151 | 80 | 4.64
690.56 | 277.318 | 5.83 | 1613 |  |  |  | 61.917 | 277.412 | 5.94 | 1617 |  |  |  | 61.92 | 277.317 | 5.85 | 1620 |  |  |  | 61.92 | 533.37 | 0.151 | 80 | 4.64
691.06 | 277.391 | 5.83 | 1612 |  |  |  | 61.921 | 277.512 | 5.96 | 1622 |  |  |  | 61.92 | 277.293 | 5.85 | 1620 |  |  |  | 61.92 | 533.12 | 0.146 | 78 | 4.64
691.56 | 277.391 | 5.83 | 1612 |  |  |  | 61.921 | 277.512 | 5.96 | 1622 |  |  |  | 61.92 | 277.293 | 5.85 | 1620 |  |  |  | 61.92 | 533.12 | 0.146 | 78 | 4.64
692.07 | 277.45 | 5.77 | 1597 |  |  |  | 61.92 | 277.429 | 5.92 | 1610 |  |  |  | 61.92 | 277.265 | 5.8 | 1607 |  |  |  | 61.92 | 526.97 | 0.15 | 79 | 4.64
692.57 | 277.45 | 5.77 | 1597 |  |  |  | 61.92 | 277.429 | 5.92 | 1610 |  |  |  | 61.92 | 277.265 | 5.8 | 1607 |  |  |  | 61.92 | 526.97 | 0.15 | 79 | 4.64
693.06 | 277.373 | 5.78 | 1600 |  |  |  | 61.921 | 277.302 | 5.91 | 1608 |  |  |  | 61.92 | 277.341 | 5.81 | 1610 |  |  |  | 61.92 | 527.45 | 0.152 | 80 | 4.64
693.56 | 277.373 | 5.78 | 1600 |  |  |  | 61.921 | 277.302 | 5.91 | 1608 |  |  |  | 61.92 | 277.341 | 5.81 | 1610 |  |  |  | 61.92 | 527.45 | 0.152 | 80 | 4.64
694.06 | 277.439 | 5.82 | 1612 |  |  |  | 61.92 | 277.497 | 5.95 | 1618 |  |  |  | 61.92 | 277.322 | 5.84 | 1619 |  |  |  | 61.921 | 533.44 | 0.154 | 82 | 4.64
694.56 | 277.439 | 5.82 | 1612 |  |  |  | 61.92 | 277.497 | 5.95 | 1618 |  |  |  | 61.92 | 277.322 | 5.84 | 1619 |  |  |  | 61.921 | 533.44 | 0.154 | 82 | 4.64
695.06 | 277.356 | 5.83 | 1613 |  |  |  | 61.921 | 277.319 | 5.96 | 1622 |  |  |  | 61.919 | 277.291 | 5.83 | 1615 |  |  |  | 61.92 | 533.44 | 0.147 | 79 | 4.64
695.56 | 277.356 | 5.83 | 1613 |  |  |  | 61.921 | 277.319 | 5.96 | 1622 |  |  |  | 61.919 | 277.291 | 5.83 | 1615 |  |  |  | 61.92 | 533.44 | 0.147 | 79 | 4.64
696.06 | 277.433 | 5.82 | 1611 |  |  |  | 61.92 | 277.528 | 5.95 | 1620 |  |  |  | 61.922 | 277.266 | 5.86 | 1621 |  |  |  | 61.919 | 533.43 | 0.151 | 81 | 4.64
696.56 | 277.433 | 5.82 | 1611 |  |  |  | 61.92 | 277.528 | 5.95 | 1620 |  |  |  | 61.922 | 277.266 | 5.86 | 1621 |  |  |  | 61.919 | 533.43 | 0.151 | 81 | 4.64
697.06 | 277.367 | 5.84 | 1615 |  |  |  | 61.92 | 277.365 | 5.95 | 1619 |  |  |  | 61.919 | 277.36 | 5.86 | 1624 |  |  |  | 61.919 | 533.68 | 0.149 | 80 | 4.64
697.56 | 277.367 | 5.84 | 1615 |  |  |  | 61.92 | 277.365 | 5.95 | 1619 |  |  |  | 61.919 | 277.36 | 5.86 | 1624 |  |  |  | 61.919 | 533.68 | 0.149 | 80 | 4.64
698.07 | 277.429 | 5.65 | 1563 |  |  |  | 61.921 | 277.257 | 5.77 | 1566 |  |  |  | 61.92 | 277.335 | 5.66 | 1568 |  |  |  | 61.92 | 539.84 | 0.149 | 80 | 4.64
698.6 | 277.429 | 5.65 | 1563 |  |  |  | 61.921 | 277.257 | 5.77 | 1566 |  |  |  | 61.92 | 277.335 | 5.66 | 1568 |  |  |  | 61.92 | 539.84 | 0.149 | 80 | 4.64
699.09 | 277.354 | 5.72 | 1583 |  |  |  | 61.918 | 277.449 | 5.85 | 1593 |  |  |  | 61.92 | 277.301 | 5.76 | 1596 |  |  |  | 61.92 | 539.37 | 0.151 | 82 | 4.64
699.59 | 277.354 | 5.72 | 1583 |  |  |  | 61.918 | 277.449 | 5.85 | 1593 |  |  |  | 61.92 | 277.301 | 5.76 | 1596 |  |  |  | 61.92 | 539.37 | 0.151 | 82 | 4.64
700.09 | 277.417 | 5.82 | 1610 |  |  |  | 61.921 | 277.33 | 5.94 | 1618 |  |  |  | 61.92 | 277.274 | 5.85 | 1621 |  |  |  | 61.921 | 533.47 | 0.149 | 79 | 4.64
700.57 | 277.417 | 5.82 | 1610 |  |  |  | 61.921 | 277.33 | 5.94 | 1618 |  |  |  | 61.92 | 277.274 | 5.85 | 1621 |  |  |  | 61.921 | 533.47 | 0.149 | 79 | 4.64
701.07 | 277.471 | 5.81 | 1609 |  |  |  | 61.919 | 277.491 | 5.93 | 1614 |  |  |  | 61.919 | 277.363 | 5.86 | 1622 |  |  |  | 61.923 | 533.45 | 0.149 | 79 | 4.64
701.56 | 277.471 | 5.81 | 1609 |  |  |  | 61.919 | 277.491 | 5.93 | 1614 |  |  |  | 61.919 | 277.363 | 5.86 | 1622 |  |  |  | 61.923 | 533.45 | 0.149 | 79 | 4.64
702.06 | 277.426 | 5.84 | 1617 |  |  |  | 61.921 | 277.348 | 5.94 | 1616 |  |  |  | 61.92 | 277.341 | 5.85 | 1619 |  |  |  | 61.92 | 533.44 | 0.144 | 77 | 4.64
702.59 | 277.464 | 5.83 | 1615 |  |  |  | 61.92 | 277.492 | 5.97 | 1624 |  |  |  | 61.92 | 277.303 | 5.84 | 1619 |  |  |  | 61.921 | 533.27 | 0.151 | 80 | 4.64
703.09 | 277.464 | 5.83 | 1615 |  |  |  | 61.92 | 277.492 | 5.97 | 1624 |  |  |  | 61.92 | 277.303 | 5.84 | 1619 |  |  |  | 61.921 | 533.27 | 0.151 | 80 | 4.64
703.58 | 277.392 | 5.78 | 1598 |  |  |  | 61.921 | 277.425 | 5.91 | 1610 |  |  |  | 61.92 | 277.263 | 5.81 | 1610 |  |  |  | 61.92 | 527.01 | 0.148 | 78 | 4.64
704.08 | 277.392 | 5.78 | 1598 |  |  |  | 61.921 | 277.425 | 5.91 | 1610 |  |  |  | 61.92 | 277.263 | 5.81 | 1610 |  |  |  | 61.92 | 527.01 | 0.148 | 78 | 4.64
704.56 | 277.468 | 5.78 | 1600 |  |  |  | 61.92 | 277.317 | 5.9 | 1606 |  |  |  | 61.92 | 277.23 | 5.82 | 1612 |  |  |  | 61.92 | 527.37 | 0.15 | 79 | 4.64
705.06 | 277.468 | 5.78 | 1600 |  |  |  | 61.92 | 277.317 | 5.9 | 1606 |  |  |  | 61.92 | 277.23 | 5.82 | 1612 |  |  |  | 61.92 | 527.37 | 0.15 | 79 | 4.64
705.56 | 277.364 | 5.83 | 1613 |  |  |  | 61.92 | 277.487 | 5.94 | 1618 |  |  |  | 61.92 | 277.343 | 5.85 | 1622 |  |  |  | 61.92 | 533.44 | 0.149 | 79 | 4.64
706.06 | 277.364 | 5.83 | 1613 |  |  |  | 61.92 | 277.487 | 5.94 | 1618 |  |  |  | 61.92 | 277.343 | 5.85 | 1622 |  |  |  | 61.92 | 533.44 | 0.149 | 79 | 4.64
706.56 | 277.433 | 5.83 | 1612 |  |  |  | 61.921 | 277.345 | 5.95 | 1621 |  |  |  | 61.921 | 277.319 | 5.84 | 1618 |  |  |  | 61.92 | 533.41 | 0.155 | 83 | 4.64
707.06 | 277.433 | 5.83 | 1612 |  |  |  | 61.921 | 277.345 | 5.95 | 1621 |  |  |  | 61.921 | 277.319 | 5.84 | 1618 |  |  |  | 61.92 | 533.41 | 0.155 | 83 | 4.64
707.56 | 277.354 | 5.82 | 1610 |  |  |  | 61.917 | 277.556 | 5.96 | 1625 |  |  |  | 61.922 | 277.285 | 5.85 | 1620 |  |  |  | 61.921 | 533.42 | 0.153 | 82 | 4.64
708.06 | 277.354 | 5.82 | 1610 |  |  |  | 61.917 | 277.556 | 5.96 | 1625 |  |  |  | 61.922 | 277.285 | 5.85 | 1620 |  |  |  | 61.921 | 533.42 | 0.153 | 82 | 4.64
708.56 | 277.42 | 5.82 | 1612 |  |  |  | 61.92 | 277.442 | 5.94 | 1620 |  |  |  | 61.92 | 277.243 | 5.85 | 1621 |  |  |  | 61.921 | 533.59 | 0.151 | 81 | 4.64
709.06 | 277.42 | 5.82 | 1612 |  |  |  | 61.92 | 277.442 | 5.94 | 1620 |  |  |  | 61.92 | 277.243 | 5.85 | 1621 |  |  |  | 61.921 | 533.59 | 0.151 | 81 | 4.64
709.56 | 277.472 | 5.65 | 1562 |  |  |  | 61.92 | 277.272 | 5.76 | 1565 |  |  |  | 61.921 | 277.329 | 5.66 | 1567 |  |  |  | 61.92 | 539.85 | 0.15 | 81 | 4.64
710.06 | 277.472 | 5.65 | 1562 |  |  |  | 61.92 | 277.272 | 5.76 | 1565 |  |  |  | 61.921 | 277.329 | 5.66 | 1567 |  |  |  | 61.92 | 539.85 | 0.15 | 81 | 4.64
710.56 | 277.415 | 5.72 | 1583 |  |  |  | 61.921 | 277.42 | 5.85 | 1594 |  |  |  | 61.92 | 277.317 | 5.75 | 1591 |  |  |  | 61.921 | 539.41 | 0.154 | 83 | 4.64
711.06 | 277.415 | 5.72 | 1583 |  |  |  | 61.921 | 277.42 | 5.85 | 1594 |  |  |  | 61.92 | 277.317 | 5.75 | 1591 |  |  |  | 61.921 | 539.41 | 0.154 | 83 | 4.64
711.56 | 277.468 | 5.81 | 1609 |  |  |  | 61.92 | 277.32 | 5.97 | 1625 |  |  |  | 61.92 | 277.289 | 5.85 | 1621 |  |  |  | 61.921 | 533.39 | 0.144 | 77 | 4.64
712.06 | 277.468 | 5.81 | 1609 |  |  |  | 61.92 | 277.32 | 5.97 | 1625 |  |  |  | 61.92 | 277.289 | 5.85 | 1621 |  |  |  | 61.921 | 533.39 | 0.144 | 77 | 4.64
712.56 | 277.386 | 5.83 | 1614 |  |  |  | 61.92 | 277.495 | 5.94 | 1617 |  |  |  | 61.923 | 277.241 | 5.86 | 1621 |  |  |  | 61.919 | 533.43 | 0.148 | 79 | 4.64
713.06 | 277.386 | 5.83 | 1614 |  |  |  | 61.92 | 277.495 | 5.94 | 1617 |  |  |  | 61.923 | 277.241 | 5.86 | 1621 |  |  |  | 61.919 | 533.43 | 0.148 | 79 | 4.64
713.56 | 277.468 | 5.84 | 1616 |  |  |  | 61.92 | 277.38 | 5.93 | 1616 |  |  |  | 61.92 | 277.345 | 5.85 | 1621 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
714.06 | 277.468 | 5.84 | 1616 |  |  |  | 61.92 | 277.38 | 5.93 | 1616 |  |  |  | 61.92 | 277.345 | 5.85 | 1621 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
714.56 | 277.331 | 5.83 | 1613 |  |  |  | 61.92 | 277.49 | 5.94 | 1619 |  |  |  | 61.92 | 277.328 | 5.85 | 1619 |  |  |  | 61.921 | 533.22 | 0.146 | 78 | 4.64
715.06 | 277.331 | 5.83 | 1613 |  |  |  | 61.92 | 277.49 | 5.94 | 1619 |  |  |  | 61.92 | 277.328 | 5.85 | 1619 |  |  |  | 61.921 | 533.22 | 0.146 | 78 | 4.64
715.56 | 277.398 | 5.8 | 1603 |  |  |  | 61.921 | 277.46 | 5.91 | 1610 |  |  |  | 61.921 | 277.305 | 5.81 | 1610 |  |  |  | 61.92 | 527.01 | 0.149 | 79 | 4.64
716.06 | 277.398 | 5.8 | 1603 |  |  |  | 61.921 | 277.46 | 5.91 | 1610 |  |  |  | 61.921 | 277.305 | 5.81 | 1610 |  |  |  | 61.92 | 527.01 | 0.149 | 79 | 4.64
716.56 | 277.338 | 5.79 | 1601 |  |  |  | 61.918 | 277.298 | 5.9 | 1605 |  |  |  | 61.919 | 277.269 | 5.82 | 1610 |  |  |  | 61.92 | 527.37 | 0.15 | 79 | 4.64
717.06 | 277.338 | 5.79 | 1601 |  |  |  | 61.918 | 277.298 | 5.9 | 1605 |  |  |  | 61.919 | 277.269 | 5.82 | 1610 |  |  |  | 61.92 | 527.37 | 0.15 | 79 | 4.64
717.56 | 277.402 | 5.83 | 1613 |  |  |  | 61.921 | 277.531 | 5.93 | 1615 |  |  |  | 61.921 | 277.351 | 5.85 | 1622 |  |  |  | 61.921 | 533.38 | 0.147 | 79 | 4.64
718.06 | 277.402 | 5.83 | 1613 |  |  |  | 61.921 | 277.531 | 5.93 | 1615 |  |  |  | 61.921 | 277.351 | 5.85 | 1622 |  |  |  | 61.921 | 533.38 | 0.147 | 79 | 4.64
718.56 | 277.442 | 5.83 | 1614 |  |  |  | 61.921 | 277.382 | 5.96 | 1622 |  |  |  | 61.919 | 277.324 | 5.84 | 1617 |  |  |  | 61.921 | 533.47 | 0.146 | 78 | 4.64
719.06 | 277.442 | 5.83 | 1614 |  |  |  | 61.921 | 277.382 | 5.96 | 1622 |  |  |  | 61.919 | 277.324 | 5.84 | 1617 |  |  |  | 61.921 | 533.47 | 0.146 | 78 | 4.64
719.56 | 277.393 | 5.82 | 1611 |  |  |  | 61.92 | 277.557 | 5.94 | 1619 |  |  |  | 61.923 | 277.301 | 5.85 | 1621 |  |  |  | 61.919 | 533.47 | 0.147 | 78 | 4.64
720.06 | 277.393 | 5.82 | 1611 |  |  |  | 61.92 | 277.557 | 5.94 | 1619 |  |  |  | 61.923 | 277.301 | 5.85 | 1621 |  |  |  | 61.919 | 533.47 | 0.147 | 78 | 4.64
720.56 | 277.452 | 5.81 | 1609 |  |  |  | 61.92 | 277.46 | 5.95 | 1621 |  |  |  | 61.92 | 277.274 | 5.85 | 1619 |  |  |  | 61.921 | 533.55 | 0.148 | 79 | 4.64
721.06 | 277.452 | 5.81 | 1609 |  |  |  | 61.92 | 277.46 | 5.95 | 1621 |  |  |  | 61.92 | 277.274 | 5.85 | 1619 |  |  |  | 61.921 | 533.55 | 0.148 | 79 | 4.64
721.56 | 277.358 | 5.64 | 1560 |  |  |  | 61.921 | 277.325 | 5.74 | 1562 |  |  |  | 61.919 | 277.373 | 5.66 | 1567 |  |  |  | 61.919 | 539.86 | 0.149 | 80 | 4.64
722.06 | 277.358 | 5.64 | 1560 |  |  |  | 61.921 | 277.325 | 5.74 | 1562 |  |  |  | 61.919 | 277.373 | 5.66 | 1567 |  |  |  | 61.919 | 539.86 | 0.149 | 80 | 4.64
722.56 | 277.443 | 5.71 | 1580 |  |  |  | 61.921 | 277.513 | 5.84 | 1589 |  |  |  | 61.919 | 277.338 | 5.73 | 1587 |  |  |  | 61.92 | 539.51 | 0.151 | 82 | 4.64
723.06 | 277.443 | 5.71 | 1580 |  |  |  | 61.921 | 277.513 | 5.84 | 1589 |  |  |  | 61.919 | 277.338 | 5.73 | 1587 |  |  |  | 61.92 | 539.51 | 0.151 | 82 | 4.64
723.56 | 277.335 | 5.83 | 1614 |  |  |  | 61.92 | 277.363 | 5.96 | 1624 |  |  |  | 61.921 | 277.304 | 5.83 | 1615 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 4.64
724.06 | 277.335 | 5.83 | 1614 |  |  |  | 61.92 | 277.363 | 5.96 | 1624 |  |  |  | 61.921 | 277.304 | 5.83 | 1615 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 4.64
724.56 | 277.404 | 5.84 | 1616 |  |  |  | 61.921 | 277.557 | 5.95 | 1620 |  |  |  | 61.922 | 277.286 | 5.85 | 1619 |  |  |  | 61.921 | 533.47 | 0.15 | 80 | 4.64
725.06 | 277.404 | 5.84 | 1616 |  |  |  | 61.921 | 277.557 | 5.95 | 1620 |  |  |  | 61.922 | 277.286 | 5.85 | 1619 |  |  |  | 61.921 | 533.47 | 0.15 | 80 | 4.64
725.56 | 277.338 | 5.83 | 1613 |  |  |  | 61.919 | 277.376 | 5.94 | 1619 |  |  |  | 61.919 | 277.265 | 5.86 | 1622 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
726.06 | 277.338 | 5.83 | 1613 |  |  |  | 61.919 | 277.376 | 5.94 | 1619 |  |  |  | 61.919 | 277.265 | 5.86 | 1622 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 4.64
726.56 | 277.389 | 5.84 | 1617 |  |  |  | 61.921 | 277.507 | 5.96 | 1623 |  |  |  | 61.92 | 277.349 | 5.85 | 1621 |  |  |  | 61.92 | 533.31 | 0.146 | 78 | 4.64
727.06 | 277.389 | 5.84 | 1617 |  |  |  | 61.921 | 277.507 | 5.96 | 1623 |  |  |  | 61.92 | 277.349 | 5.85 | 1621 |  |  |  | 61.92 | 533.31 | 0.146 | 78 | 4.64
727.56 | 277.438 | 5.79 | 1602 |  |  |  | 61.92 | 277.496 | 5.91 | 1607 |  |  |  | 61.921 | 277.311 | 5.79 | 1604 |  |  |  | 61.921 | 526.97 | 0.147 | 77 | 4.64
728.06 | 277.438 | 5.79 | 1602 |  |  |  | 61.92 | 277.496 | 5.91 | 1607 |  |  |  | 61.921 | 277.311 | 5.79 | 1604 |  |  |  | 61.921 | 526.97 | 0.147 | 77 | 4.64
728.56 | 277.379 | 5.78 | 1601 |  |  |  | 61.92 | 277.356 | 5.9 | 1604 |  |  |  | 61.92 | 277.273 | 5.81 | 1608 |  |  |  | 61.921 | 527.26 | 0.15 | 79 | 4.64
729.06 | 277.379 | 5.78 | 1601 |  |  |  | 61.92 | 277.356 | 5.9 | 1604 |  |  |  | 61.92 | 277.273 | 5.81 | 1608 |  |  |  | 61.921 | 527.26 | 0.15 | 79 | 4.64
729.56 | 277.448 | 5.83 | 1613 |  |  |  | 61.921 | 277.533 | 5.95 | 1621 |  |  |  | 61.92 | 277.252 | 5.84 | 1615 |  |  |  | 61.92 | 533.38 | 0.151 | 80 | 4.64
730.06 | 277.448 | 5.83 | 1613 |  |  |  | 61.921 | 277.533 | 5.95 | 1621 |  |  |  | 61.92 | 277.252 | 5.84 | 1615 |  |  |  | 61.92 | 533.38 | 0.151 | 80 | 4.64
730.56 | 277.389 | 5.83 | 1612 |  |  |  | 61.921 | 277.364 | 5.95 | 1618 |  |  |  | 61.919 | 277.354 | 5.85 | 1621 |  |  |  | 61.919 | 533.41 | 0.149 | 80 | 4.64
731.09 | 277.389 | 5.83 | 1612 |  |  |  | 61.921 | 277.364 | 5.95 | 1618 |  |  |  | 61.919 | 277.354 | 5.85 | 1621 |  |  |  | 61.919 | 533.41 | 0.149 | 80 | 4.64
731.59 | 277.46 | 5.83 | 1614 |  |  |  | 61.921 | 277.543 | 5.94 | 1617 |  |  |  | 61.923 | 277.327 | 5.85 | 1621 |  |  |  | 61.921 | 533.37 | 0.146 | 78 | 4.64
732.07 | 277.46 | 5.83 | 1614 |  |  |  | 61.921 | 277.543 | 5.94 | 1617 |  |  |  | 61.923 | 277.327 | 5.85 | 1621 |  |  |  | 61.921 | 533.37 | 0.146 | 78 | 4.64
732.57 | 277.376 | 5.84 | 1615 |  |  |  | 61.92 | 277.395 | 5.94 | 1617 |  |  |  | 61.919 | 277.282 | 5.84 | 1618 |  |  |  | 61.92 | 533.46 | 0.153 | 82 | 4.64
733.06 | 277.376 | 5.84 | 1615 |  |  |  | 61.92 | 277.395 | 5.94 | 1617 |  |  |  | 61.919 | 277.282 | 5.84 | 1618 |  |  |  | 61.92 | 533.46 | 0.153 | 82 | 4.64
733.56 | 277.427 | 5.66 | 1565 |  |  |  | 61.921 | 277.308 | 5.79 | 1574 |  |  |  | 61.92 | 277.256 | 5.67 | 1570 |  |  |  | 61.92 | 539.83 | 0.148 | 80 | 4.64
734.1 | 277.362 | 5.71 | 1580 |  |  |  | 61.918 | 277.469 | 5.84 | 1588 |  |  |  | 61.92 | 277.346 | 5.74 | 1588 |  |  |  | 61.921 | 539.56 | 0.153 | 83 | 4.64
734.61 | 277.362 | 5.71 | 1580 |  |  |  | 61.918 | 277.469 | 5.84 | 1588 |  |  |  | 61.92 | 277.346 | 5.74 | 1588 |  |  |  | 61.921 | 539.56 | 0.153 | 83 | 4.64
735.08 | 277.43 | 5.83 | 1613 |  |  |  | 61.92 | 277.325 | 5.94 | 1615 |  |  |  | 61.919 | 277.324 | 5.86 | 1622 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
735.58 | 277.43 | 5.83 | 1613 |  |  |  | 61.92 | 277.325 | 5.94 | 1615 |  |  |  | 61.919 | 277.324 | 5.86 | 1622 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 4.64
736.06 | 277.458 | 5.82 | 1612 |  |  |  | 61.92 | 277.54 | 5.96 | 1621 |  |  |  | 61.923 | 277.284 | 5.84 | 1616 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
736.56 | 277.458 | 5.82 | 1612 |  |  |  | 61.92 | 277.54 | 5.96 | 1621 |  |  |  | 61.923 | 277.284 | 5.84 | 1616 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 4.64
737.06 | 277.406 | 5.84 | 1617 |  |  |  | 61.92 | 277.392 | 5.95 | 1618 |  |  |  | 61.92 | 277.251 | 5.84 | 1616 |  |  |  | 61.921 | 533.38 | 0.149 | 80 | 4.64
737.56 | 277.406 | 5.84 | 1617 |  |  |  | 61.92 | 277.392 | 5.95 | 1618 |  |  |  | 61.92 | 277.251 | 5.84 | 1616 |  |  |  | 61.921 | 533.38 | 0.149 | 80 | 4.64
738.06 | 277.47 | 5.82 | 1611 |  |  |  | 61.921 | 277.4 | 5.95 | 1619 |  |  |  | 61.919 | 277.351 | 5.85 | 1620 |  |  |  | 61.921 | 533.36 | 0.149 | 80 | 4.64
738.56 | 277.47 | 5.82 | 1611 |  |  |  | 61.921 | 277.4 | 5.95 | 1619 |  |  |  | 61.919 | 277.351 | 5.85 | 1620 |  |  |  | 61.921 | 533.36 | 0.149 | 80 | 4.64
739.06 | 277.392 | 5.78 | 1600 |  |  |  | 61.92 | 277.375 | 5.93 | 1614 |  |  |  | 61.92 | 277.333 | 5.81 | 1610 |  |  |  | 61.921 | 526.96 | 0.153 | 81 | 4.64
739.56 | 277.392 | 5.78 | 1600 |  |  |  | 61.92 | 277.375 | 5.93 | 1614 |  |  |  | 61.92 | 277.333 | 5.81 | 1610 |  |  |  | 61.921 | 526.96 | 0.153 | 81 | 4.64
740.06 | 277.469 | 5.77 | 1597 |  |  |  | 61.92 | 277.276 | 5.89 | 1603 |  |  |  | 61.92 | 277.298 | 5.82 | 1613 |  |  |  | 61.92 | 527.14 | 0.148 | 78 | 4.64
740.56 | 277.469 | 5.77 | 1597 |  |  |  | 61.92 | 277.276 | 5.89 | 1603 |  |  |  | 61.92 | 277.298 | 5.82 | 1613 |  |  |  | 61.92 | 527.14 | 0.148 | 78 | 4.64
741.06 | 277.386 | 5.84 | 1615 |  |  |  | 61.92 | 277.442 | 5.95 | 1621 |  |  |  | 61.921 | 277.258 | 5.86 | 1622 |  |  |  | 61.92 | 533.37 | 0.149 | 79 | 4.64
741.56 | 277.386 | 5.84 | 1615 |  |  |  | 61.92 | 277.442 | 5.95 | 1621 |  |  |  | 61.921 | 277.258 | 5.86 | 1622 |  |  |  | 61.92 | 533.37 | 0.149 | 79 | 4.64
742.06 | 277.445 | 5.84 | 1617 |  |  |  | 61.92 | 277.335 | 5.94 | 1619 |  |  |  | 61.92 | 277.356 | 5.84 | 1618 |  |  |  | 61.921 | 533.42 | 0.151 | 81 | 4.64
742.56 | 277.445 | 5.84 | 1617 |  |  |  | 61.92 | 277.335 | 5.94 | 1619 |  |  |  | 61.92 | 277.356 | 5.84 | 1618 |  |  |  | 61.921 | 533.42 | 0.151 | 81 | 4.64
743.06 | 277.365 | 5.83 | 1613 |  |  |  | 61.917 | 277.512 | 5.96 | 1623 |  |  |  | 61.923 | 277.334 | 5.85 | 1620 |  |  |  | 61.919 | 533.42 | 0.144 | 77 | 4.64
743.56 | 277.365 | 5.83 | 1613 |  |  |  | 61.917 | 277.512 | 5.96 | 1623 |  |  |  | 61.923 | 277.334 | 5.85 | 1620 |  |  |  | 61.919 | 533.42 | 0.144 | 77 | 4.64
744.06 | 277.426 | 5.83 | 1613 |  |  |  | 61.921 | 277.383 | 5.93 | 1614 |  |  |  | 61.92 | 277.305 | 5.86 | 1621 |  |  |  | 61.92 | 533.47 | 0.151 | 81 | 4.64
744.56 | 277.426 | 5.83 | 1613 |  |  |  | 61.921 | 277.383 | 5.93 | 1614 |  |  |  | 61.92 | 277.305 | 5.86 | 1621 |  |  |  | 61.92 | 533.47 | 0.151 | 81 | 4.64
745.06 | 277.477 | 5.66 | 1567 |  |  |  | 61.921 | 277.253 | 5.77 | 1568 |  |  |  | 61.921 | 277.26 | 5.68 | 1572 |  |  |  | 61.92 | 539.8 | 0.15 | 81 | 4.64
745.56 | 277.477 | 5.66 | 1567 |  |  |  | 61.921 | 277.253 | 5.77 | 1568 |  |  |  | 61.921 | 277.26 | 5.68 | 1572 |  |  |  | 61.92 | 539.8 | 0.15 | 81 | 4.64
746.06 | 277.388 | 5.69 | 1574 |  |  |  | 61.92 | 277.461 | 5.81 | 1579 |  |  |  | 61.919 | 277.306 | 5.7 | 1579 |  |  |  | 61.921 | 539.61 | 0.153 | 82 | 4.64
746.56 | 277.388 | 5.69 | 1574 |  |  |  | 61.92 | 277.461 | 5.81 | 1579 |  |  |  | 61.919 | 277.306 | 5.7 | 1579 |  |  |  | 61.921 | 539.61 | 0.153 | 82 | 4.64
747.06 | 277.48 | 5.84 | 1615 |  |  |  | 61.92 | 277.323 | 5.96 | 1623 |  |  |  | 61.92 | 277.337 | 5.85 | 1621 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
747.56 | 277.48 | 5.84 | 1615 |  |  |  | 61.92 | 277.323 | 5.96 | 1623 |  |  |  | 61.92 | 277.337 | 5.85 | 1621 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
748.06 | 277.376 | 5.82 | 1610 |  |  |  | 61.92 | 277.505 | 5.94 | 1619 |  |  |  | 61.92 | 277.322 | 5.86 | 1622 |  |  |  | 61.921 | 533.4 | 0.148 | 79 | 4.64
748.56 | 277.376 | 5.82 | 1610 |  |  |  | 61.92 | 277.505 | 5.94 | 1619 |  |  |  | 61.92 | 277.322 | 5.86 | 1622 |  |  |  | 61.921 | 533.4 | 0.148 | 79 | 4.64
749.06 | 277.44 | 5.82 | 1611 |  |  |  | 61.92 | 277.376 | 5.94 | 1617 |  |  |  | 61.92 | 277.29 | 5.85 | 1620 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 4.64
749.56 | 277.44 | 5.82 | 1611 |  |  |  | 61.92 | 277.376 | 5.94 | 1617 |  |  |  | 61.92 | 277.29 | 5.85 | 1620 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 4.64
750.06 | 277.374 | 5.85 | 1617 |  |  |  | 61.92 | 277.514 | 5.94 | 1618 |  |  |  | 61.923 | 277.245 | 5.85 | 1620 |  |  |  | 61.921 | 533.34 | 0.15 | 80 | 4.64
750.56 | 277.374 | 5.85 | 1617 |  |  |  | 61.92 | 277.514 | 5.94 | 1618 |  |  |  | 61.923 | 277.245 | 5.85 | 1620 |  |  |  | 61.921 | 533.34 | 0.15 | 80 | 4.64
751.06 | 277.425 | 5.79 | 1601 |  |  |  | 61.921 | 277.421 | 5.91 | 1609 |  |  |  | 61.919 | 277.345 | 5.8 | 1607 |  |  |  | 61.92 | 526.93 | 0.151 | 79 | 4.64
751.56 | 277.425 | 5.79 | 1601 |  |  |  | 61.921 | 277.421 | 5.91 | 1609 |  |  |  | 61.919 | 277.345 | 5.8 | 1607 |  |  |  | 61.92 | 526.93 | 0.151 | 79 | 4.64
752.06 | 277.358 | 5.78 | 1600 |  |  |  | 61.917 | 277.295 | 5.9 | 1607 |  |  |  | 61.92 | 277.32 | 5.82 | 1611 |  |  |  | 61.921 | 527.15 | 0.149 | 79 | 4.64
752.56 | 277.358 | 5.78 | 1600 |  |  |  | 61.917 | 277.295 | 5.9 | 1607 |  |  |  | 61.92 | 277.32 | 5.82 | 1611 |  |  |  | 61.921 | 527.15 | 0.149 | 79 | 4.64
753.06 | 277.431 | 5.83 | 1612 |  |  |  | 61.921 | 277.508 | 5.94 | 1620 |  |  |  | 61.92 | 277.294 | 5.85 | 1619 |  |  |  | 61.921 | 533.4 | 0.153 | 82 | 4.64
753.56 | 277.431 | 5.83 | 1612 |  |  |  | 61.921 | 277.508 | 5.94 | 1620 |  |  |  | 61.92 | 277.294 | 5.85 | 1619 |  |  |  | 61.921 | 533.4 | 0.153 | 82 | 4.64
754.06 | 277.481 | 5.84 | 1617 |  |  |  | 61.919 | 277.339 | 5.95 | 1619 |  |  |  | 61.92 | 277.248 | 5.85 | 1620 |  |  |  | 61.921 | 533.41 | 0.149 | 80 | 4.64
754.56 | 277.481 | 5.84 | 1617 |  |  |  | 61.919 | 277.339 | 5.95 | 1619 |  |  |  | 61.92 | 277.248 | 5.85 | 1620 |  |  |  | 61.921 | 533.41 | 0.149 | 80 | 4.64
755.06 | 277.376 | 5.83 | 1612 |  |  |  | 61.921 | 277.559 | 5.95 | 1621 |  |  |  | 61.923 | 277.356 | 5.85 | 1621 |  |  |  | 61.919 | 533.41 | 0.146 | 78 | 4.64
755.56 | 277.376 | 5.83 | 1612 |  |  |  | 61.921 | 277.559 | 5.95 | 1621 |  |  |  | 61.923 | 277.356 | 5.85 | 1621 |  |  |  | 61.919 | 533.41 | 0.146 | 78 | 4.64
756.06 | 277.441 | 5.82 | 1612 |  |  |  | 61.92 | 277.427 | 5.95 | 1620 |  |  |  | 61.919 | 277.322 | 5.87 | 1625 |  |  |  | 61.919 | 533.47 | 0.145 | 77 | 4.64
756.56 | 277.441 | 5.82 | 1612 |  |  |  | 61.92 | 277.427 | 5.95 | 1620 |  |  |  | 61.919 | 277.322 | 5.87 | 1625 |  |  |  | 61.919 | 533.47 | 0.145 | 77 | 4.64
757.06 | 277.344 | 5.65 | 1564 |  |  |  | 61.92 | 277.308 | 5.75 | 1564 |  |  |  | 61.92 | 277.286 | 5.67 | 1571 |  |  |  | 61.919 | 539.84 | 0.148 | 80 | 4.64
757.56 | 277.344 | 5.65 | 1564 |  |  |  | 61.92 | 277.308 | 5.75 | 1564 |  |  |  | 61.92 | 277.286 | 5.67 | 1571 |  |  |  | 61.919 | 539.84 | 0.148 | 80 | 4.64
758.06 | 277.406 | 5.69 | 1574 |  |  |  | 61.921 | 277.499 | 5.81 | 1582 |  |  |  | 61.921 | 277.261 | 5.7 | 1578 |  |  |  | 61.921 | 539.64 | 0.151 | 82 | 4.64
758.56 | 277.406 | 5.69 | 1574 |  |  |  | 61.921 | 277.499 | 5.81 | 1582 |  |  |  | 61.921 | 277.261 | 5.7 | 1578 |  |  |  | 61.921 | 539.64 | 0.151 | 82 | 4.64
759.06 | 277.351 | 5.83 | 1612 |  |  |  | 61.92 | 277.37 | 5.94 | 1616 |  |  |  | 61.919 | 277.363 | 5.85 | 1619 |  |  |  | 61.919 | 533.39 | 0.152 | 81 | 4.64
759.56 | 277.351 | 5.83 | 1612 |  |  |  | 61.92 | 277.37 | 5.94 | 1616 |  |  |  | 61.919 | 277.363 | 5.85 | 1619 |  |  |  | 61.919 | 533.39 | 0.152 | 81 | 4.64
760.06 | 277.417 | 5.83 | 1612 |  |  |  | 61.92 | 277.577 | 5.94 | 1617 |  |  |  | 61.919 | 277.32 | 5.85 | 1621 |  |  |  | 61.92 | 533.39 | 0.148 | 79 | 4.64
760.56 | 277.417 | 5.83 | 1612 |  |  |  | 61.92 | 277.577 | 5.94 | 1617 |  |  |  | 61.919 | 277.32 | 5.85 | 1621 |  |  |  | 61.92 | 533.39 | 0.148 | 79 | 4.64
761.06 | 277.327 | 5.84 | 1615 |  |  |  | 61.916 | 277.394 | 5.96 | 1622 |  |  |  | 61.92 | 277.286 | 5.86 | 1623 |  |  |  | 61.92 | 533.43 | 0.15 | 80 | 4.64
761.56 | 277.327 | 5.84 | 1615 |  |  |  | 61.916 | 277.394 | 5.96 | 1622 |  |  |  | 61.92 | 277.286 | 5.86 | 1623 |  |  |  | 61.92 | 533.43 | 0.15 | 80 | 4.64
762.06 | 277.406 | 5.82 | 1610 |  |  |  | 61.92 | 277.54 | 5.95 | 1621 |  |  |  | 61.922 | 277.27 | 5.84 | 1618 |  |  |  | 61.921 | 533.39 | 0.152 | 81 | 4.64
762.59 | 277.406 | 5.82 | 1610 |  |  |  | 61.92 | 277.54 | 5.95 | 1621 |  |  |  | 61.922 | 277.27 | 5.84 | 1618 |  |  |  | 61.921 | 533.39 | 0.152 | 81 | 4.64
763.09 | 277.46 | 5.79 | 1602 |  |  |  | 61.921 | 277.428 | 5.9 | 1608 |  |  |  | 61.919 | 277.346 | 5.81 | 1608 |  |  |  | 61.922 | 527 | 0.149 | 79 | 4.64
763.57 | 277.46 | 5.79 | 1602 |  |  |  | 61.921 | 277.428 | 5.9 | 1608 |  |  |  | 61.919 | 277.346 | 5.81 | 1608 |  |  |  | 61.922 | 527 | 0.149 | 79 | 4.64
764.07 | 277.366 | 5.79 | 1602 |  |  |  | 61.92 | 277.334 | 5.91 | 1609 |  |  |  | 61.92 | 277.327 | 5.83 | 1615 |  |  |  | 61.921 | 527.08 | 0.146 | 77 | 4.64
764.56 | 277.366 | 5.79 | 1602 |  |  |  | 61.92 | 277.334 | 5.91 | 1609 |  |  |  | 61.92 | 277.327 | 5.83 | 1615 |  |  |  | 61.921 | 527.08 | 0.146 | 77 | 4.64
765.06 | 277.435 | 5.82 | 1612 |  |  |  | 61.921 | 277.544 | 5.94 | 1618 |  |  |  | 61.92 | 277.3 | 5.85 | 1619 |  |  |  | 61.921 | 533.4 | 0.148 | 79 | 4.64
765.6 | 277.347 | 5.83 | 1613 |  |  |  | 61.92 | 277.405 | 5.95 | 1619 |  |  |  | 61.919 | 277.275 | 5.85 | 1619 |  |  |  | 61.92 | 533.43 | 0.151 | 80 | 4.64
766.1 | 277.347 | 5.83 | 1613 |  |  |  | 61.92 | 277.405 | 5.95 | 1619 |  |  |  | 61.919 | 277.275 | 5.85 | 1619 |  |  |  | 61.92 | 533.43 | 0.151 | 80 | 4.64
766.58 | 277.417 | 5.83 | 1612 |  |  |  | 61.921 | 277.569 | 5.95 | 1622 |  |  |  | 61.921 | 277.261 | 5.85 | 1619 |  |  |  | 61.921 | 533.41 | 0.146 | 78 | 4.64
767.09 | 277.417 | 5.83 | 1612 |  |  |  | 61.921 | 277.569 | 5.95 | 1622 |  |  |  | 61.921 | 277.261 | 5.85 | 1619 |  |  |  | 61.921 | 533.41 | 0.146 | 78 | 4.64
767.56 | 277.356 | 5.83 | 1614 |  |  |  | 61.919 | 277.407 | 5.96 | 1621 |  |  |  | 61.92 | 277.346 | 5.86 | 1622 |  |  |  | 61.919 | 533.4 | 0.15 | 80 | 4.64
768.06 | 277.356 | 5.83 | 1614 |  |  |  | 61.919 | 277.407 | 5.96 | 1621 |  |  |  | 61.92 | 277.346 | 5.86 | 1622 |  |  |  | 61.919 | 533.4 | 0.15 | 80 | 4.64
768.56 | 277.412 | 5.66 | 1565 |  |  |  | 61.921 | 277.303 | 5.77 | 1565 |  |  |  | 61.92 | 277.312 | 5.69 | 1576 |  |  |  | 61.92 | 539.82 | 0.143 | 77 | 4.64
769.06 | 277.412 | 5.66 | 1565 |  |  |  | 61.921 | 277.303 | 5.77 | 1565 |  |  |  | 61.92 | 277.312 | 5.69 | 1576 |  |  |  | 61.92 | 539.82 | 0.143 | 77 | 4.64
769.56 | 277.321 | 5.69 | 1573 |  |  |  | 61.918 | 277.458 | 5.8 | 1577 |  |  |  | 61.919 | 277.277 | 5.7 | 1577 |  |  |  | 61.92 | 539.71 | 0.151 | 81 | 4.64
770.06 | 277.321 | 5.69 | 1573 |  |  |  | 61.918 | 277.458 | 5.8 | 1577 |  |  |  | 61.919 | 277.277 | 5.7 | 1577 |  |  |  | 61.92 | 539.71 | 0.151 | 81 | 4.64
770.56 | 277.402 | 5.83 | 1611 |  |  |  | 61.921 | 277.334 | 5.95 | 1620 |  |  |  | 61.92 | 277.267 | 5.86 | 1621 |  |  |  | 61.919 | 533.4 | 0.15 | 80 | 4.64
771.06 | 277.402 | 5.83 | 1611 |  |  |  | 61.921 | 277.334 | 5.95 | 1620 |  |  |  | 61.92 | 277.267 | 5.86 | 1621 |  |  |  | 61.919 | 533.4 | 0.15 | 80 | 4.64
771.56 | 277.46 | 5.83 | 1612 |  |  |  | 61.92 | 277.52 | 5.93 | 1617 |  |  |  | 61.92 | 277.354 | 5.86 | 1622 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
772.06 | 277.46 | 5.83 | 1612 |  |  |  | 61.92 | 277.52 | 5.93 | 1617 |  |  |  | 61.92 | 277.354 | 5.86 | 1622 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
772.56 | 277.386 | 5.83 | 1614 |  |  |  | 61.921 | 277.388 | 5.93 | 1614 |  |  |  | 61.92 | 277.328 | 5.84 | 1618 |  |  |  | 61.921 | 533.37 | 0.143 | 76 | 4.64
773.06 | 277.386 | 5.83 | 1614 |  |  |  | 61.921 | 277.388 | 5.93 | 1614 |  |  |  | 61.92 | 277.328 | 5.84 | 1618 |  |  |  | 61.921 | 533.37 | 0.143 | 76 | 4.64
773.56 | 277.463 | 5.83 | 1613 |  |  |  | 61.921 | 277.522 | 5.95 | 1621 |  |  |  | 61.923 | 277.284 | 5.85 | 1618 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
774.06 | 277.463 | 5.83 | 1613 |  |  |  | 61.921 | 277.522 | 5.95 | 1621 |  |  |  | 61.923 | 277.284 | 5.85 | 1618 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
774.56 | 277.385 | 5.78 | 1600 |  |  |  | 61.919 | 277.451 | 5.91 | 1610 |  |  |  | 61.918 | 277.251 | 5.81 | 1609 |  |  |  | 61.921 | 526.94 | 0.151 | 80 | 4.64
775.06 | 277.385 | 5.78 | 1600 |  |  |  | 61.919 | 277.451 | 5.91 | 1610 |  |  |  | 61.918 | 277.251 | 5.81 | 1609 |  |  |  | 61.921 | 526.94 | 0.151 | 80 | 4.64
775.56 | 277.44 | 5.78 | 1600 |  |  |  | 61.921 | 277.281 | 5.9 | 1605 |  |  |  | 61.92 | 277.358 | 5.8 | 1606 |  |  |  | 61.92 | 527.01 | 0.15 | 79 | 4.64
776.06 | 277.44 | 5.78 | 1600 |  |  |  | 61.921 | 277.281 | 5.9 | 1605 |  |  |  | 61.92 | 277.358 | 5.8 | 1606 |  |  |  | 61.92 | 527.01 | 0.15 | 79 | 4.64
776.56 | 277.371 | 5.85 | 1618 |  |  |  | 61.92 | 277.45 | 5.94 | 1616 |  |  |  | 61.92 | 277.339 | 5.83 | 1614 |  |  |  | 61.921 | 533.4 | 0.152 | 81 | 4.64
777.06 | 277.371 | 5.85 | 1618 |  |  |  | 61.92 | 277.45 | 5.94 | 1616 |  |  |  | 61.92 | 277.339 | 5.83 | 1614 |  |  |  | 61.921 | 533.4 | 0.152 | 81 | 4.64
777.56 | 277.437 | 5.84 | 1616 |  |  |  | 61.92 | 277.356 | 5.94 | 1617 |  |  |  | 61.92 | 277.297 | 5.82 | 1613 |  |  |  | 61.921 | 533.41 | 0.15 | 80 | 4.64
778.06 | 277.437 | 5.84 | 1616 |  |  |  | 61.92 | 277.356 | 5.94 | 1617 |  |  |  | 61.92 | 277.297 | 5.82 | 1613 |  |  |  | 61.921 | 533.41 | 0.15 | 80 | 4.64
778.56 | 277.349 | 5.82 | 1609 |  |  |  | 61.918 | 277.533 | 5.96 | 1623 |  |  |  | 61.922 | 277.253 | 5.87 | 1625 |  |  |  | 61.919 | 533.42 | 0.154 | 82 | 4.64
779.06 | 277.349 | 5.82 | 1609 |  |  |  | 61.918 | 277.533 | 5.96 | 1623 |  |  |  | 61.922 | 277.253 | 5.87 | 1625 |  |  |  | 61.919 | 533.42 | 0.154 | 82 | 4.64
779.56 | 277.422 | 5.83 | 1613 |  |  |  | 61.92 | 277.389 | 5.95 | 1620 |  |  |  | 61.92 | 277.348 | 5.85 | 1620 |  |  |  | 61.921 | 533.4 | 0.152 | 81 | 4.64
780.06 | 277.422 | 5.83 | 1613 |  |  |  | 61.92 | 277.389 | 5.95 | 1620 |  |  |  | 61.92 | 277.348 | 5.85 | 1620 |  |  |  | 61.921 | 533.4 | 0.152 | 81 | 4.64
780.56 | 277.474 | 5.66 | 1567 |  |  |  | 61.921 | 277.305 | 5.75 | 1564 |  |  |  | 61.919 | 277.327 | 5.65 | 1565 |  |  |  | 61.92 | 539.82 | 0.152 | 82 | 4.64
781.06 | 277.474 | 5.66 | 1567 |  |  |  | 61.921 | 277.305 | 5.75 | 1564 |  |  |  | 61.919 | 277.327 | 5.65 | 1565 |  |  |  | 61.92 | 539.82 | 0.152 | 82 | 4.64
781.56 | 277.39 | 5.67 | 1568 |  |  |  | 61.92 | 277.448 | 5.79 | 1575 |  |  |  | 61.92 | 277.304 | 5.7 | 1577 |  |  |  | 61.92 | 539.73 | 0.148 | 80 | 4.64
782.06 | 277.39 | 5.67 | 1568 |  |  |  | 61.92 | 277.448 | 5.79 | 1575 |  |  |  | 61.92 | 277.304 | 5.7 | 1577 |  |  |  | 61.92 | 539.73 | 0.148 | 80 | 4.64
782.56 | 277.461 | 5.82 | 1610 |  |  |  | 61.921 | 277.273 | 5.95 | 1619 |  |  |  | 61.92 | 277.269 | 5.85 | 1620 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 4.64
783.06 | 277.461 | 5.82 | 1610 |  |  |  | 61.921 | 277.273 | 5.95 | 1619 |  |  |  | 61.92 | 277.269 | 5.85 | 1620 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 4.64
783.56 | 277.393 | 5.81 | 1608 |  |  |  | 61.921 | 277.489 | 5.95 | 1619 |  |  |  | 61.921 | 277.23 | 5.86 | 1622 |  |  |  | 61.919 | 533.35 | 0.147 | 78 | 4.64
784.06 | 277.393 | 5.81 | 1608 |  |  |  | 61.921 | 277.489 | 5.95 | 1619 |  |  |  | 61.921 | 277.23 | 5.86 | 1622 |  |  |  | 61.919 | 533.35 | 0.147 | 78 | 4.64
784.56 | 277.442 | 5.82 | 1611 |  |  |  | 61.921 | 277.368 | 5.95 | 1620 |  |  |  | 61.92 | 277.336 | 5.83 | 1615 |  |  |  | 61.919 | 533.35 | 0.149 | 80 | 4.64
785.06 | 277.442 | 5.82 | 1611 |  |  |  | 61.921 | 277.368 | 5.95 | 1620 |  |  |  | 61.92 | 277.336 | 5.83 | 1615 |  |  |  | 61.919 | 533.35 | 0.149 | 80 | 4.64
785.56 | 277.373 | 5.85 | 1618 |  |  |  | 61.92 | 277.491 | 5.94 | 1618 |  |  |  | 61.923 | 277.323 | 5.84 | 1618 |  |  |  | 61.92 | 533.34 | 0.146 | 78 | 4.64
786.06 | 277.373 | 5.85 | 1618 |  |  |  | 61.92 | 277.491 | 5.94 | 1618 |  |  |  | 61.923 | 277.323 | 5.84 | 1618 |  |  |  | 61.92 | 533.34 | 0.146 | 78 | 4.64
786.56 | 277.444 | 5.78 | 1598 |  |  |  | 61.921 | 277.427 | 5.91 | 1610 |  |  |  | 61.92 | 277.296 | 5.79 | 1604 |  |  |  | 61.92 | 526.96 | 0.15 | 79 | 4.64
787.06 | 277.444 | 5.78 | 1598 |  |  |  | 61.921 | 277.427 | 5.91 | 1610 |  |  |  | 61.92 | 277.296 | 5.79 | 1604 |  |  |  | 61.92 | 526.96 | 0.15 | 79 | 4.64
787.56 | 277.344 | 5.77 | 1597 |  |  |  | 61.917 | 277.298 | 5.9 | 1606 |  |  |  | 61.92 | 277.262 | 5.81 | 1608 |  |  |  | 61.92 | 527.02 | 0.148 | 78 | 4.64
788.06 | 277.344 | 5.77 | 1597 |  |  |  | 61.917 | 277.298 | 5.9 | 1606 |  |  |  | 61.92 | 277.262 | 5.81 | 1608 |  |  |  | 61.92 | 527.02 | 0.148 | 78 | 4.64
788.56 | 277.431 | 5.83 | 1613 |  |  |  | 61.921 | 277.453 | 5.93 | 1615 |  |  |  | 61.919 | 277.333 | 5.84 | 1619 |  |  |  | 61.921 | 533.39 | 0.151 | 81 | 4.64
789.06 | 277.431 | 5.83 | 1613 |  |  |  | 61.921 | 277.453 | 5.93 | 1615 |  |  |  | 61.919 | 277.333 | 5.84 | 1619 |  |  |  | 61.921 | 533.39 | 0.151 | 81 | 4.64
789.56 | 277.5 | 5.83 | 1615 |  |  |  | 61.921 | 277.315 | 5.95 | 1621 |  |  |  | 61.92 | 277.312 | 5.85 | 1621 |  |  |  | 61.921 | 533.38 | 0.149 | 79 | 4.64
790.06 | 277.5 | 5.83 | 1615 |  |  |  | 61.921 | 277.315 | 5.95 | 1621 |  |  |  | 61.92 | 277.312 | 5.85 | 1621 |  |  |  | 61.921 | 533.38 | 0.149 | 79 | 4.64
790.56 | 277.408 | 5.84 | 1616 |  |  |  | 61.92 | 277.539 | 5.94 | 1618 |  |  |  | 61.922 | 277.296 | 5.85 | 1620 |  |  |  | 61.92 | 533.36 | 0.15 | 80 | 4.64
791.06 | 277.408 | 5.84 | 1616 |  |  |  | 61.92 | 277.539 | 5.94 | 1618 |  |  |  | 61.922 | 277.296 | 5.85 | 1620 |  |  |  | 61.92 | 533.36 | 0.15 | 80 | 4.64
791.56 | 277.466 | 5.82 | 1611 |  |  |  | 61.921 | 277.379 | 5.94 | 1617 |  |  |  | 61.92 | 277.26 | 5.85 | 1620 |  |  |  | 61.921 | 533.37 | 0.148 | 79 | 4.64
792.06 | 277.466 | 5.82 | 1611 |  |  |  | 61.921 | 277.379 | 5.94 | 1617 |  |  |  | 61.92 | 277.26 | 5.85 | 1620 |  |  |  | 61.921 | 533.37 | 0.148 | 79 | 4.64
792.56 | 277.384 | 5.66 | 1566 |  |  |  | 61.919 | 277.326 | 5.8 | 1576 |  |  |  | 61.921 | 277.354 | 5.68 | 1573 |  |  |  | 61.92 | 539.77 | 0.15 | 81 | 4.64
793.06 | 277.384 | 5.66 | 1566 |  |  |  | 61.919 | 277.326 | 5.8 | 1576 |  |  |  | 61.921 | 277.354 | 5.68 | 1573 |  |  |  | 61.92 | 539.77 | 0.15 | 81 | 4.64
793.56 | 277.444 | 5.66 | 1566 |  |  |  | 61.921 | 277.449 | 5.79 | 1577 |  |  |  | 61.92 | 277.322 | 5.7 | 1579 |  |  |  | 61.919 | 539.72 | 0.152 | 82 | 4.64
794.09 | 277.444 | 5.66 | 1566 |  |  |  | 61.921 | 277.449 | 5.79 | 1577 |  |  |  | 61.92 | 277.322 | 5.7 | 1579 |  |  |  | 61.919 | 539.72 | 0.152 | 82 | 4.64
794.59 | 277.359 | 5.82 | 1611 |  |  |  | 61.92 | 277.319 | 5.93 | 1614 |  |  |  | 61.92 | 277.308 | 5.85 | 1621 |  |  |  | 61.92 | 533.38 | 0.15 | 80 | 4.64
795.07 | 277.359 | 5.82 | 1611 |  |  |  | 61.92 | 277.319 | 5.93 | 1614 |  |  |  | 61.92 | 277.308 | 5.85 | 1621 |  |  |  | 61.92 | 533.38 | 0.15 | 80 | 4.64
795.57 | 277.444 | 5.84 | 1615 |  |  |  | 61.92 | 277.537 | 5.95 | 1623 |  |  |  | 61.919 | 277.275 | 5.85 | 1620 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
796.06 | 277.444 | 5.84 | 1615 |  |  |  | 61.92 | 277.537 | 5.95 | 1623 |  |  |  | 61.919 | 277.275 | 5.85 | 1620 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
796.56 | 277.319 | 5.83 | 1613 |  |  |  | 61.917 | 277.398 | 5.96 | 1622 |  |  |  | 61.921 | 277.363 | 5.86 | 1623 |  |  |  | 61.921 | 533.37 | 0.148 | 79 | 4.64
797.1 | 277.388 | 5.83 | 1613 |  |  |  | 61.92 | 277.546 | 5.95 | 1619 |  |  |  | 61.922 | 277.338 | 5.84 | 1617 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
797.6 | 277.388 | 5.83 | 1613 |  |  |  | 61.92 | 277.546 | 5.95 | 1619 |  |  |  | 61.922 | 277.338 | 5.84 | 1617 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
798.09 | 277.46 | 5.77 | 1596 |  |  |  | 61.921 | 277.42 | 5.93 | 1612 |  |  |  | 61.919 | 277.31 | 5.84 | 1616 |  |  |  | 61.921 | 526.93 | 0.147 | 77 | 4.64
798.59 | 277.46 | 5.77 | 1596 |  |  |  | 61.921 | 277.42 | 5.93 | 1612 |  |  |  | 61.919 | 277.31 | 5.84 | 1616 |  |  |  | 61.921 | 526.93 | 0.147 | 77 | 4.64
799.07 | 277.374 | 5.79 | 1603 |  |  |  | 61.921 | 277.321 | 5.91 | 1607 |  |  |  | 61.92 | 277.282 | 5.81 | 1610 |  |  |  | 61.92 | 526.96 | 0.15 | 79 | 4.64
799.57 | 277.374 | 5.79 | 1603 |  |  |  | 61.921 | 277.321 | 5.91 | 1607 |  |  |  | 61.92 | 277.282 | 5.81 | 1610 |  |  |  | 61.92 | 526.96 | 0.15 | 79 | 4.64
800.06 | 277.438 | 5.83 | 1612 |  |  |  | 61.92 | 277.472 | 5.94 | 1618 |  |  |  | 61.921 | 277.249 | 5.85 | 1619 |  |  |  | 61.92 | 533.36 | 0.15 | 80 | 4.64
800.56 | 277.438 | 5.83 | 1612 |  |  |  | 61.92 | 277.472 | 5.94 | 1618 |  |  |  | 61.921 | 277.249 | 5.85 | 1619 |  |  |  | 61.92 | 533.36 | 0.15 | 80 | 4.64
801.06 | 277.362 | 5.84 | 1614 |  |  |  | 61.92 | 277.346 | 5.94 | 1617 |  |  |  | 61.919 | 277.348 | 5.84 | 1616 |  |  |  | 61.922 | 533.4 | 0.151 | 80 | 4.64
801.56 | 277.362 | 5.84 | 1614 |  |  |  | 61.92 | 277.346 | 5.94 | 1617 |  |  |  | 61.919 | 277.348 | 5.84 | 1616 |  |  |  | 61.922 | 533.4 | 0.151 | 80 | 4.64
802.06 | 277.429 | 5.82 | 1610 |  |  |  | 61.921 | 277.593 | 5.94 | 1619 |  |  |  | 61.923 | 277.315 | 5.84 | 1619 |  |  |  | 61.92 | 533.36 | 0.149 | 80 | 4.64
802.56 | 277.429 | 5.82 | 1610 |  |  |  | 61.921 | 277.593 | 5.94 | 1619 |  |  |  | 61.923 | 277.315 | 5.84 | 1619 |  |  |  | 61.92 | 533.36 | 0.149 | 80 | 4.64
803.06 | 277.344 | 5.82 | 1610 |  |  |  | 61.92 | 277.47 | 5.96 | 1622 |  |  |  | 61.92 | 277.288 | 5.85 | 1621 |  |  |  | 61.919 | 533.4 | 0.146 | 78 | 4.64
803.56 | 277.344 | 5.82 | 1610 |  |  |  | 61.92 | 277.47 | 5.96 | 1622 |  |  |  | 61.92 | 277.288 | 5.85 | 1621 |  |  |  | 61.919 | 533.4 | 0.146 | 78 | 4.64
804.06 | 277.418 | 5.66 | 1565 |  |  |  | 61.921 | 277.372 | 5.79 | 1574 |  |  |  | 61.92 | 277.262 | 5.69 | 1576 |  |  |  | 61.921 | 539.79 | 0.146 | 79 | 4.64
804.56 | 277.418 | 5.66 | 1565 |  |  |  | 61.921 | 277.372 | 5.79 | 1574 |  |  |  | 61.92 | 277.262 | 5.69 | 1576 |  |  |  | 61.921 | 539.79 | 0.146 | 79 | 4.64
805.06 | 277.328 | 5.68 | 1572 |  |  |  | 61.918 | 277.476 | 5.78 | 1572 |  |  |  | 61.92 | 277.355 | 5.7 | 1579 |  |  |  | 61.92 | 539.7 | 0.145 | 78 | 4.64
805.56 | 277.328 | 5.68 | 1572 |  |  |  | 61.918 | 277.476 | 5.78 | 1572 |  |  |  | 61.92 | 277.355 | 5.7 | 1579 |  |  |  | 61.92 | 539.7 | 0.145 | 78 | 4.64
806.06 | 277.394 | 5.85 | 1618 |  |  |  | 61.921 | 277.355 | 5.95 | 1620 |  |  |  | 61.919 | 277.322 | 5.85 | 1619 |  |  |  | 61.92 | 533.36 | 0.144 | 77 | 4.64
806.56 | 277.394 | 5.85 | 1618 |  |  |  | 61.921 | 277.355 | 5.95 | 1620 |  |  |  | 61.919 | 277.322 | 5.85 | 1619 |  |  |  | 61.92 | 533.36 | 0.144 | 77 | 4.64
807.06 | 277.46 | 5.83 | 1614 |  |  |  | 61.921 | 277.512 | 5.96 | 1622 |  |  |  | 61.921 | 277.284 | 5.84 | 1618 |  |  |  | 61.92 | 533.37 | 0.149 | 79 | 4.64
807.56 | 277.46 | 5.83 | 1614 |  |  |  | 61.921 | 277.512 | 5.96 | 1622 |  |  |  | 61.921 | 277.284 | 5.84 | 1618 |  |  |  | 61.92 | 533.37 | 0.149 | 79 | 4.64
808.06 | 277.381 | 5.83 | 1613 |  |  |  | 61.921 | 277.4 | 5.95 | 1621 |  |  |  | 61.92 | 277.263 | 5.84 | 1618 |  |  |  | 61.92 | 533.4 | 0.146 | 78 | 4.64
808.56 | 277.381 | 5.83 | 1613 |  |  |  | 61.921 | 277.4 | 5.95 | 1621 |  |  |  | 61.92 | 277.263 | 5.84 | 1618 |  |  |  | 61.92 | 533.4 | 0.146 | 78 | 4.64
809.06 | 277.436 | 5.82 | 1609 |  |  |  | 61.921 | 277.544 | 5.95 | 1620 |  |  |  | 61.923 | 277.367 | 5.86 | 1624 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
809.56 | 277.436 | 5.82 | 1609 |  |  |  | 61.921 | 277.544 | 5.95 | 1620 |  |  |  | 61.923 | 277.367 | 5.86 | 1624 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
810.06 | 277.364 | 5.77 | 1596 |  |  |  | 61.919 | 277.447 | 5.9 | 1607 |  |  |  | 61.919 | 277.347 | 5.81 | 1610 |  |  |  | 61.92 | 526.93 | 0.147 | 78 | 4.64
810.56 | 277.364 | 5.77 | 1596 |  |  |  | 61.919 | 277.447 | 5.9 | 1607 |  |  |  | 61.919 | 277.347 | 5.81 | 1610 |  |  |  | 61.92 | 526.93 | 0.147 | 78 | 4.64
811.06 | 277.426 | 5.8 | 1606 |  |  |  | 61.921 | 277.288 | 5.9 | 1605 |  |  |  | 61.92 | 277.307 | 5.82 | 1613 |  |  |  | 61.921 | 526.94 | 0.151 | 80 | 4.64
811.56 | 277.426 | 5.8 | 1606 |  |  |  | 61.921 | 277.288 | 5.9 | 1605 |  |  |  | 61.92 | 277.307 | 5.82 | 1613 |  |  |  | 61.921 | 526.94 | 0.151 | 80 | 4.64
812.06 | 277.328 | 5.85 | 1617 |  |  |  | 61.921 | 277.515 | 5.93 | 1615 |  |  |  | 61.92 | 277.268 | 5.85 | 1619 |  |  |  | 61.921 | 533.32 | 0.147 | 79 | 4.64
812.56 | 277.328 | 5.85 | 1617 |  |  |  | 61.921 | 277.515 | 5.93 | 1615 |  |  |  | 61.92 | 277.268 | 5.85 | 1619 |  |  |  | 61.921 | 533.32 | 0.147 | 79 | 4.64
813.06 | 277.409 | 5.83 | 1614 |  |  |  | 61.92 | 277.34 | 5.96 | 1624 |  |  |  | 61.92 | 277.327 | 5.84 | 1617 |  |  |  | 61.922 | 533.36 | 0.149 | 80 | 4.64
813.56 | 277.409 | 5.83 | 1614 |  |  |  | 61.92 | 277.34 | 5.96 | 1624 |  |  |  | 61.92 | 277.327 | 5.84 | 1617 |  |  |  | 61.922 | 533.36 | 0.149 | 80 | 4.64
814.06 | 277.327 | 5.82 | 1611 |  |  |  | 61.918 | 277.531 | 5.95 | 1622 |  |  |  | 61.923 | 277.346 | 5.86 | 1624 |  |  |  | 61.919 | 533.39 | 0.148 | 79 | 4.64
814.56 | 277.327 | 5.82 | 1611 |  |  |  | 61.918 | 277.531 | 5.95 | 1622 |  |  |  | 61.923 | 277.346 | 5.86 | 1624 |  |  |  | 61.919 | 533.39 | 0.148 | 79 | 4.64
815.06 | 277.424 | 5.81 | 1608 |  |  |  | 61.92 | 277.408 | 5.93 | 1616 |  |  |  | 61.921 | 277.315 | 5.86 | 1622 |  |  |  | 61.921 | 533.37 | 0.152 | 81 | 4.64
815.56 | 277.424 | 5.81 | 1608 |  |  |  | 61.92 | 277.408 | 5.93 | 1616 |  |  |  | 61.921 | 277.315 | 5.86 | 1622 |  |  |  | 61.921 | 533.37 | 0.152 | 81 | 4.64
816.06 | 277.475 | 5.67 | 1569 |  |  |  | 61.921 | 277.365 | 5.78 | 1572 |  |  |  | 61.92 | 277.265 | 5.69 | 1574 |  |  |  | 61.92 | 539.76 | 0.153 | 83 | 4.64
816.56 | 277.475 | 5.67 | 1569 |  |  |  | 61.921 | 277.365 | 5.78 | 1572 |  |  |  | 61.92 | 277.265 | 5.69 | 1574 |  |  |  | 61.92 | 539.76 | 0.153 | 83 | 4.64
817.06 | 277.406 | 5.66 | 1567 |  |  |  | 61.92 | 277.458 | 5.76 | 1567 |  |  |  | 61.921 | 277.237 | 5.67 | 1569 |  |  |  | 61.92 | 539.78 | 0.154 | 83 | 4.64
817.56 | 277.406 | 5.66 | 1567 |  |  |  | 61.92 | 277.458 | 5.76 | 1567 |  |  |  | 61.921 | 277.237 | 5.67 | 1569 |  |  |  | 61.92 | 539.78 | 0.154 | 83 | 4.64
818.06 | 277.462 | 5.82 | 1612 |  |  |  | 61.921 | 277.3 | 5.96 | 1623 |  |  |  | 61.919 | 277.349 | 5.85 | 1620 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
818.56 | 277.462 | 5.82 | 1612 |  |  |  | 61.921 | 277.3 | 5.96 | 1623 |  |  |  | 61.919 | 277.349 | 5.85 | 1620 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
819.06 | 277.391 | 5.81 | 1609 |  |  |  | 61.919 | 277.463 | 5.94 | 1617 |  |  |  | 61.919 | 277.329 | 5.86 | 1622 |  |  |  | 61.92 | 533.37 | 0.15 | 80 | 4.64
819.56 | 277.391 | 5.81 | 1609 |  |  |  | 61.919 | 277.463 | 5.94 | 1617 |  |  |  | 61.919 | 277.329 | 5.86 | 1622 |  |  |  | 61.92 | 533.37 | 0.15 | 80 | 4.64
820.06 | 277.459 | 5.82 | 1612 |  |  |  | 61.921 | 277.337 | 5.95 | 1619 |  |  |  | 61.92 | 277.284 | 5.87 | 1626 |  |  |  | 61.92 | 533.38 | 0.153 | 81 | 4.64
820.56 | 277.459 | 5.82 | 1612 |  |  |  | 61.921 | 277.337 | 5.95 | 1619 |  |  |  | 61.92 | 277.284 | 5.87 | 1626 |  |  |  | 61.92 | 533.38 | 0.153 | 81 | 4.64
821.06 | 277.361 | 5.83 | 1613 |  |  |  | 61.92 | 277.542 | 5.94 | 1617 |  |  |  | 61.922 | 277.252 | 5.84 | 1616 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 4.64
821.56 | 277.361 | 5.83 | 1613 |  |  |  | 61.92 | 277.542 | 5.94 | 1617 |  |  |  | 61.922 | 277.252 | 5.84 | 1616 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 4.64
822.06 | 277.436 | 5.78 | 1601 |  |  |  | 61.92 | 277.391 | 5.93 | 1612 |  |  |  | 61.92 | 277.347 | 5.81 | 1609 |  |  |  | 61.921 | 526.95 | 0.151 | 80 | 4.64
822.56 | 277.436 | 5.78 | 1601 |  |  |  | 61.92 | 277.391 | 5.93 | 1612 |  |  |  | 61.92 | 277.347 | 5.81 | 1609 |  |  |  | 61.921 | 526.95 | 0.151 | 80 | 4.64
823.06 | 277.362 | 5.78 | 1599 |  |  |  | 61.918 | 277.253 | 5.91 | 1608 |  |  |  | 61.918 | 277.325 | 5.8 | 1606 |  |  |  | 61.92 | 526.91 | 0.15 | 79 | 4.64
823.56 | 277.362 | 5.78 | 1599 |  |  |  | 61.918 | 277.253 | 5.91 | 1608 |  |  |  | 61.918 | 277.325 | 5.8 | 1606 |  |  |  | 61.92 | 526.91 | 0.15 | 79 | 4.64
824.06 | 277.416 | 5.84 | 1616 |  |  |  | 61.92 | 277.479 | 5.95 | 1619 |  |  |  | 61.918 | 277.298 | 5.86 | 1624 |  |  |  | 61.921 | 533.35 | 0.149 | 79 | 4.64
824.56 | 277.416 | 5.84 | 1616 |  |  |  | 61.92 | 277.479 | 5.95 | 1619 |  |  |  | 61.918 | 277.298 | 5.86 | 1624 |  |  |  | 61.921 | 533.35 | 0.149 | 79 | 4.64
825.06 | 277.467 | 5.83 | 1614 |  |  |  | 61.921 | 277.329 | 5.95 | 1619 |  |  |  | 61.921 | 277.26 | 5.85 | 1619 |  |  |  | 61.921 | 533.35 | 0.149 | 80 | 4.64
825.59 | 277.467 | 5.83 | 1614 |  |  |  | 61.921 | 277.329 | 5.95 | 1619 |  |  |  | 61.921 | 277.26 | 5.85 | 1619 |  |  |  | 61.921 | 533.35 | 0.149 | 80 | 4.64
826.09 | 277.417 | 5.81 | 1609 |  |  |  | 61.92 | 277.497 | 5.95 | 1620 |  |  |  | 61.922 | 277.355 | 5.85 | 1621 |  |  |  | 61.921 | 533.4 | 0.154 | 82 | 4.64
826.58 | 277.417 | 5.81 | 1609 |  |  |  | 61.92 | 277.497 | 5.95 | 1620 |  |  |  | 61.922 | 277.355 | 5.85 | 1621 |  |  |  | 61.921 | 533.4 | 0.154 | 82 | 4.64
827.08 | 277.477 | 5.81 | 1608 |  |  |  | 61.92 | 277.373 | 5.94 | 1617 |  |  |  | 61.919 | 277.331 | 5.86 | 1624 |  |  |  | 61.919 | 533.32 | 0.15 | 80 | 4.64
827.56 | 277.477 | 5.81 | 1608 |  |  |  | 61.92 | 277.373 | 5.94 | 1617 |  |  |  | 61.919 | 277.331 | 5.86 | 1624 |  |  |  | 61.919 | 533.32 | 0.15 | 80 | 4.64
828.06 | 277.393 | 5.69 | 1574 |  |  |  | 61.921 | 277.417 | 5.8 | 1576 |  |  |  | 61.92 | 277.31 | 5.69 | 1575 |  |  |  | 61.921 | 539.72 | 0.148 | 80 | 4.64
828.6 | 277.467 | 5.67 | 1568 |  |  |  | 61.921 | 277.399 | 5.78 | 1573 |  |  |  | 61.919 | 277.273 | 5.67 | 1570 |  |  |  | 61.921 | 539.81 | 0.154 | 83 | 4.64
829.1 | 277.467 | 5.67 | 1568 |  |  |  | 61.921 | 277.399 | 5.78 | 1573 |  |  |  | 61.919 | 277.273 | 5.67 | 1570 |  |  |  | 61.921 | 539.81 | 0.154 | 83 | 4.64
829.59 | 277.37 | 5.82 | 1610 |  |  |  | 61.92 | 277.311 | 5.96 | 1620 |  |  |  | 61.92 | 277.251 | 5.85 | 1620 |  |  |  | 61.921 | 533.34 | 0.153 | 82 | 4.64
830.09 | 277.37 | 5.82 | 1610 |  |  |  | 61.92 | 277.311 | 5.96 | 1620 |  |  |  | 61.92 | 277.251 | 5.85 | 1620 |  |  |  | 61.921 | 533.34 | 0.153 | 82 | 4.64
830.57 | 277.434 | 5.81 | 1607 |  |  |  | 61.92 | 277.465 | 5.94 | 1616 |  |  |  | 61.919 | 277.343 | 5.86 | 1624 |  |  |  | 61.919 | 533.37 | 0.151 | 80 | 4.64
831.07 | 277.434 | 5.81 | 1607 |  |  |  | 61.92 | 277.465 | 5.94 | 1616 |  |  |  | 61.919 | 277.343 | 5.86 | 1624 |  |  |  | 61.919 | 533.37 | 0.151 | 80 | 4.64
831.56 | 277.328 | 5.84 | 1615 |  |  |  | 61.918 | 277.325 | 5.94 | 1616 |  |  |  | 61.921 | 277.314 | 5.85 | 1620 |  |  |  | 61.921 | 533.31 | 0.152 | 81 | 4.64
832.06 | 277.328 | 5.84 | 1615 |  |  |  | 61.918 | 277.325 | 5.94 | 1616 |  |  |  | 61.921 | 277.314 | 5.85 | 1620 |  |  |  | 61.921 | 533.31 | 0.152 | 81 | 4.64
832.56 | 277.395 | 5.83 | 1614 |  |  |  | 61.919 | 277.565 | 5.95 | 1619 |  |  |  | 61.923 | 277.289 | 5.86 | 1622 |  |  |  | 61.919 | 533.39 | 0.151 | 81 | 4.64
833.06 | 277.395 | 5.83 | 1614 |  |  |  | 61.919 | 277.565 | 5.95 | 1619 |  |  |  | 61.923 | 277.289 | 5.86 | 1622 |  |  |  | 61.919 | 533.39 | 0.151 | 81 | 4.64
833.56 | 277.458 | 5.78 | 1599 |  |  |  | 61.921 | 277.432 | 5.9 | 1602 |  |  |  | 61.92 | 277.252 | 5.82 | 1611 |  |  |  | 61.921 | 526.94 | 0.152 | 80 | 4.64
834.06 | 277.458 | 5.78 | 1599 |  |  |  | 61.921 | 277.432 | 5.9 | 1602 |  |  |  | 61.92 | 277.252 | 5.82 | 1611 |  |  |  | 61.921 | 526.94 | 0.152 | 80 | 4.64
834.56 | 277.387 | 5.78 | 1599 |  |  |  | 61.92 | 277.291 | 5.91 | 1606 |  |  |  | 61.92 | 277.352 | 5.82 | 1611 |  |  |  | 61.92 | 526.91 | 0.153 | 81 | 4.64
835.06 | 277.387 | 5.78 | 1599 |  |  |  | 61.92 | 277.291 | 5.91 | 1606 |  |  |  | 61.92 | 277.352 | 5.82 | 1611 |  |  |  | 61.92 | 526.91 | 0.153 | 81 | 4.64
835.56 | 277.448 | 5.82 | 1610 |  |  |  | 61.921 | 277.493 | 5.97 | 1623 |  |  |  | 61.919 | 277.329 | 5.85 | 1620 |  |  |  | 61.92 | 533.35 | 0.154 | 82 | 4.64
836.06 | 277.448 | 5.82 | 1610 |  |  |  | 61.921 | 277.493 | 5.97 | 1623 |  |  |  | 61.919 | 277.329 | 5.85 | 1620 |  |  |  | 61.92 | 533.35 | 0.154 | 82 | 4.64
836.56 | 277.361 | 5.81 | 1608 |  |  |  | 61.921 | 277.375 | 5.97 | 1623 |  |  |  | 61.92 | 277.301 | 5.84 | 1618 |  |  |  | 61.919 | 533.3 | 0.153 | 81 | 4.64
837.06 | 277.361 | 5.81 | 1608 |  |  |  | 61.921 | 277.375 | 5.97 | 1623 |  |  |  | 61.92 | 277.301 | 5.84 | 1618 |  |  |  | 61.919 | 533.3 | 0.153 | 81 | 4.64
837.56 | 277.427 | 5.83 | 1613 |  |  |  | 61.92 | 277.517 | 5.96 | 1621 |  |  |  | 61.923 | 277.264 | 5.86 | 1622 |  |  |  | 61.92 | 533.37 | 0.15 | 80 | 4.64
838.06 | 277.427 | 5.83 | 1613 |  |  |  | 61.92 | 277.517 | 5.96 | 1621 |  |  |  | 61.923 | 277.264 | 5.86 | 1622 |  |  |  | 61.92 | 533.37 | 0.15 | 80 | 4.64
838.56 | 277.338 | 5.83 | 1612 |  |  |  | 61.921 | 277.428 | 5.95 | 1618 |  |  |  | 61.92 | 277.358 | 5.84 | 1618 |  |  |  | 61.919 | 533.36 | 0.154 | 82 | 4.64
839.06 | 277.338 | 5.83 | 1612 |  |  |  | 61.921 | 277.428 | 5.95 | 1618 |  |  |  | 61.92 | 277.358 | 5.84 | 1618 |  |  |  | 61.919 | 533.36 | 0.154 | 82 | 4.64
839.56 | 277.393 | 5.65 | 1564 |  |  |  | 61.92 | 277.523 | 5.79 | 1574 |  |  |  | 61.918 | 277.327 | 5.68 | 1573 |  |  |  | 61.92 | 539.77 | 0.151 | 82 | 4.64
840.06 | 277.393 | 5.65 | 1564 |  |  |  | 61.92 | 277.523 | 5.79 | 1574 |  |  |  | 61.918 | 277.327 | 5.68 | 1573 |  |  |  | 61.92 | 539.77 | 0.151 | 82 | 4.64
840.56 | 277.338 | 5.64 | 1561 |  |  |  | 61.919 | 277.46 | 5.77 | 1571 |  |  |  | 61.92 | 277.295 | 5.69 | 1576 |  |  |  | 61.921 | 539.8 | 0.15 | 81 | 4.64
841.06 | 277.338 | 5.64 | 1561 |  |  |  | 61.919 | 277.46 | 5.77 | 1571 |  |  |  | 61.92 | 277.295 | 5.69 | 1576 |  |  |  | 61.921 | 539.8 | 0.15 | 81 | 4.64
841.56 | 277.413 | 5.82 | 1610 |  |  |  | 61.92 | 277.302 | 5.93 | 1614 |  |  |  | 61.92 | 277.277 | 5.86 | 1621 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
842.06 | 277.413 | 5.82 | 1610 |  |  |  | 61.92 | 277.302 | 5.93 | 1614 |  |  |  | 61.92 | 277.277 | 5.86 | 1621 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
842.56 | 277.455 | 5.81 | 1609 |  |  |  | 61.921 | 277.531 | 5.93 | 1616 |  |  |  | 61.919 | 277.237 | 5.85 | 1621 |  |  |  | 61.921 | 533.37 | 0.147 | 79 | 4.64
843.06 | 277.455 | 5.81 | 1609 |  |  |  | 61.921 | 277.531 | 5.93 | 1616 |  |  |  | 61.919 | 277.237 | 5.85 | 1621 |  |  |  | 61.921 | 533.37 | 0.147 | 79 | 4.64
843.56 | 277.405 | 5.82 | 1612 |  |  |  | 61.919 | 277.365 | 5.95 | 1621 |  |  |  | 61.92 | 277.342 | 5.84 | 1618 |  |  |  | 61.92 | 533.39 | 0.149 | 80 | 4.64
844.06 | 277.405 | 5.82 | 1612 |  |  |  | 61.919 | 277.365 | 5.95 | 1621 |  |  |  | 61.92 | 277.342 | 5.84 | 1618 |  |  |  | 61.92 | 533.39 | 0.149 | 80 | 4.64
844.56 | 277.453 | 5.83 | 1613 |  |  |  | 61.92 | 277.557 | 5.96 | 1625 |  |  |  | 61.923 | 277.316 | 5.86 | 1622 |  |  |  | 61.92 | 533.35 | 0.155 | 82 | 4.64
845.06 | 277.453 | 5.83 | 1613 |  |  |  | 61.92 | 277.557 | 5.96 | 1625 |  |  |  | 61.923 | 277.316 | 5.86 | 1622 |  |  |  | 61.92 | 533.35 | 0.155 | 82 | 4.64
845.56 | 277.346 | 5.78 | 1598 |  |  |  | 61.921 | 277.44 | 5.9 | 1607 |  |  |  | 61.921 | 277.287 | 5.83 | 1615 |  |  |  | 61.92 | 527.01 | 0.153 | 80 | 4.64
846.06 | 277.346 | 5.78 | 1598 |  |  |  | 61.921 | 277.44 | 5.9 | 1607 |  |  |  | 61.921 | 277.287 | 5.83 | 1615 |  |  |  | 61.92 | 527.01 | 0.153 | 80 | 4.64
846.56 | 277.435 | 5.79 | 1601 |  |  |  | 61.92 | 277.304 | 5.9 | 1606 |  |  |  | 61.919 | 277.258 | 5.82 | 1612 |  |  |  | 61.921 | 526.93 | 0.151 | 79 | 4.64
847.06 | 277.435 | 5.79 | 1601 |  |  |  | 61.92 | 277.304 | 5.9 | 1606 |  |  |  | 61.919 | 277.258 | 5.82 | 1612 |  |  |  | 61.921 | 526.93 | 0.151 | 79 | 4.64
847.56 | 277.322 | 5.83 | 1613 |  |  |  | 61.921 | 277.484 | 5.95 | 1621 |  |  |  | 61.92 | 277.35 | 5.85 | 1621 |  |  |  | 61.919 | 533.33 | 0.148 | 79 | 4.64
848.06 | 277.322 | 5.83 | 1613 |  |  |  | 61.921 | 277.484 | 5.95 | 1621 |  |  |  | 61.92 | 277.35 | 5.85 | 1621 |  |  |  | 61.919 | 533.33 | 0.148 | 79 | 4.64
848.56 | 277.403 | 5.83 | 1611 |  |  |  | 61.919 | 277.334 | 5.97 | 1623 |  |  |  | 61.92 | 277.323 | 5.85 | 1619 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
849.06 | 277.403 | 5.83 | 1611 |  |  |  | 61.919 | 277.334 | 5.97 | 1623 |  |  |  | 61.92 | 277.323 | 5.85 | 1619 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
849.56 | 277.344 | 5.81 | 1607 |  |  |  | 61.918 | 277.548 | 5.94 | 1618 |  |  |  | 61.92 | 277.292 | 5.87 | 1624 |  |  |  | 61.92 | 533.31 | 0.151 | 80 | 4.64
850.06 | 277.344 | 5.81 | 1607 |  |  |  | 61.918 | 277.548 | 5.94 | 1618 |  |  |  | 61.92 | 277.292 | 5.87 | 1624 |  |  |  | 61.92 | 533.31 | 0.151 | 80 | 4.64
850.56 | 277.395 | 5.83 | 1613 |  |  |  | 61.92 | 277.369 | 5.94 | 1616 |  |  |  | 61.918 | 277.272 | 5.86 | 1622 |  |  |  | 61.92 | 533.39 | 0.147 | 79 | 4.64
851.06 | 277.395 | 5.83 | 1613 |  |  |  | 61.92 | 277.369 | 5.94 | 1616 |  |  |  | 61.918 | 277.272 | 5.86 | 1622 |  |  |  | 61.92 | 533.39 | 0.147 | 79 | 4.64
851.56 | 277.436 | 5.65 | 1563 |  |  |  | 61.921 | 277.539 | 5.77 | 1569 |  |  |  | 61.922 | 277.358 | 5.67 | 1571 |  |  |  | 61.92 | 539.78 | 0.154 | 83 | 4.64
852.06 | 277.436 | 5.65 | 1563 |  |  |  | 61.921 | 277.539 | 5.77 | 1569 |  |  |  | 61.922 | 277.358 | 5.67 | 1571 |  |  |  | 61.92 | 539.78 | 0.154 | 83 | 4.64
852.56 | 277.373 | 5.66 | 1565 |  |  |  | 61.921 | 277.483 | 5.76 | 1567 |  |  |  | 61.92 | 277.33 | 5.67 | 1571 |  |  |  | 61.92 | 539.82 | 0.154 | 83 | 4.64
853.06 | 277.373 | 5.66 | 1565 |  |  |  | 61.921 | 277.483 | 5.76 | 1567 |  |  |  | 61.92 | 277.33 | 5.67 | 1571 |  |  |  | 61.92 | 539.82 | 0.154 | 83 | 4.64
853.56 | 277.445 | 5.81 | 1608 |  |  |  | 61.921 | 277.368 | 5.97 | 1626 |  |  |  | 61.92 | 277.3 | 5.85 | 1618 |  |  |  | 61.92 | 533.45 | 0.151 | 81 | 4.64
854.06 | 277.445 | 5.81 | 1608 |  |  |  | 61.921 | 277.368 | 5.97 | 1626 |  |  |  | 61.92 | 277.3 | 5.85 | 1618 |  |  |  | 61.92 | 533.45 | 0.151 | 81 | 4.64
854.56 | 277.354 | 5.83 | 1613 |  |  |  | 61.921 | 277.495 | 5.97 | 1624 |  |  |  | 61.921 | 277.281 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.147 | 79 | 4.64
855.06 | 277.354 | 5.83 | 1613 |  |  |  | 61.921 | 277.495 | 5.97 | 1624 |  |  |  | 61.921 | 277.281 | 5.86 | 1622 |  |  |  | 61.92 | 533.42 | 0.147 | 79 | 4.64
855.56 | 277.432 | 5.82 | 1611 |  |  |  | 61.921 | 277.34 | 5.95 | 1621 |  |  |  | 61.919 | 277.273 | 5.86 | 1622 |  |  |  | 61.92 | 533.32 | 0.153 | 82 | 4.64
856.06 | 277.432 | 5.82 | 1611 |  |  |  | 61.921 | 277.34 | 5.95 | 1621 |  |  |  | 61.919 | 277.273 | 5.86 | 1622 |  |  |  | 61.92 | 533.32 | 0.153 | 82 | 4.64
856.56 | 277.38 | 5.82 | 1609 |  |  |  | 61.921 | 277.585 | 5.94 | 1619 |  |  |  | 61.922 | 277.35 | 5.83 | 1616 |  |  |  | 61.919 | 533.4 | 0.151 | 81 | 4.64
857.09 | 277.38 | 5.82 | 1609 |  |  |  | 61.921 | 277.585 | 5.94 | 1619 |  |  |  | 61.922 | 277.35 | 5.83 | 1616 |  |  |  | 61.919 | 533.4 | 0.151 | 81 | 4.64
857.59 | 277.439 | 5.8 | 1604 |  |  |  | 61.921 | 277.414 | 5.91 | 1607 |  |  |  | 61.92 | 277.319 | 5.82 | 1611 |  |  |  | 61.921 | 526.99 | 0.153 | 81 | 4.64
858.08 | 277.439 | 5.8 | 1604 |  |  |  | 61.921 | 277.414 | 5.91 | 1607 |  |  |  | 61.92 | 277.319 | 5.82 | 1611 |  |  |  | 61.921 | 526.99 | 0.153 | 81 | 4.64
858.58 | 277.376 | 5.8 | 1604 |  |  |  | 61.917 | 277.334 | 5.91 | 1608 |  |  |  | 61.921 | 277.279 | 5.8 | 1606 |  |  |  | 61.921 | 526.96 | 0.149 | 79 | 4.64
859.06 | 277.376 | 5.8 | 1604 |  |  |  | 61.917 | 277.334 | 5.91 | 1608 |  |  |  | 61.921 | 277.279 | 5.8 | 1606 |  |  |  | 61.921 | 526.96 | 0.149 | 79 | 4.64
859.56 | 277.436 | 5.82 | 1612 |  |  |  | 61.919 | 277.425 | 5.96 | 1622 |  |  |  | 61.92 | 277.258 | 5.85 | 1619 |  |  |  | 61.921 | 533.36 | 0.153 | 81 | 4.64
860.11 | 277.479 | 5.82 | 1612 |  |  |  | 61.921 | 277.307 | 5.96 | 1621 |  |  |  | 61.919 | 277.365 | 5.85 | 1620 |  |  |  | 61.919 | 533.42 | 0.152 | 81 | 4.64
860.61 | 277.479 | 5.82 | 1612 |  |  |  | 61.921 | 277.307 | 5.96 | 1621 |  |  |  | 61.919 | 277.365 | 5.85 | 1620 |  |  |  | 61.919 | 533.42 | 0.152 | 81 | 4.64
861.09 | 277.409 | 5.82 | 1611 |  |  |  | 61.921 | 277.53 | 5.96 | 1623 |  |  |  | 61.92 | 277.343 | 5.87 | 1625 |  |  |  | 61.92 | 533.4 | 0.147 | 79 | 4.64
861.59 | 277.409 | 5.82 | 1611 |  |  |  | 61.921 | 277.53 | 5.96 | 1623 |  |  |  | 61.92 | 277.343 | 5.87 | 1625 |  |  |  | 61.92 | 533.4 | 0.147 | 79 | 4.64
862.07 | 277.47 | 5.83 | 1615 |  |  |  | 61.919 | 277.405 | 5.95 | 1619 |  |  |  | 61.92 | 277.293 | 5.84 | 1618 |  |  |  | 61.921 | 533.39 | 0.152 | 81 | 4.64
862.57 | 277.47 | 5.83 | 1615 |  |  |  | 61.919 | 277.405 | 5.95 | 1619 |  |  |  | 61.92 | 277.293 | 5.84 | 1618 |  |  |  | 61.921 | 533.39 | 0.152 | 81 | 4.64
863.06 | 277.376 | 5.67 | 1569 |  |  |  | 61.921 | 277.51 | 5.78 | 1572 |  |  |  | 61.922 | 277.261 | 5.69 | 1575 |  |  |  | 61.921 | 539.73 | 0.152 | 82 | 4.64
863.56 | 277.376 | 5.67 | 1569 |  |  |  | 61.921 | 277.51 | 5.78 | 1572 |  |  |  | 61.922 | 277.261 | 5.69 | 1575 |  |  |  | 61.921 | 539.73 | 0.152 | 82 | 4.64
864.06 | 277.441 | 5.66 | 1567 |  |  |  | 61.919 | 277.4 | 5.77 | 1569 |  |  |  | 61.919 | 277.348 | 5.66 | 1568 |  |  |  | 61.92 | 539.81 | 0.15 | 81 | 4.64
864.56 | 277.441 | 5.66 | 1567 |  |  |  | 61.919 | 277.4 | 5.77 | 1569 |  |  |  | 61.919 | 277.348 | 5.66 | 1568 |  |  |  | 61.92 | 539.81 | 0.15 | 81 | 4.64
865.06 | 277.378 | 5.83 | 1614 |  |  |  | 61.92 | 277.294 | 5.96 | 1622 |  |  |  | 61.92 | 277.347 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
865.56 | 277.378 | 5.83 | 1614 |  |  |  | 61.92 | 277.294 | 5.96 | 1622 |  |  |  | 61.92 | 277.347 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 4.64
866.06 | 277.444 | 5.83 | 1613 |  |  |  | 61.92 | 277.462 | 5.96 | 1622 |  |  |  | 61.921 | 277.316 | 5.86 | 1622 |  |  |  | 61.919 | 533.41 | 0.152 | 81 | 4.64
866.56 | 277.444 | 5.83 | 1613 |  |  |  | 61.92 | 277.462 | 5.96 | 1622 |  |  |  | 61.921 | 277.316 | 5.86 | 1622 |  |  |  | 61.919 | 533.41 | 0.152 | 81 | 4.64
867.06 | 277.388 | 5.81 | 1607 |  |  |  | 61.921 | 277.356 | 5.94 | 1616 |  |  |  | 61.919 | 277.28 | 5.85 | 1621 |  |  |  | 61.92 | 533.41 | 0.151 | 80 | 4.64
867.56 | 277.388 | 5.81 | 1607 |  |  |  | 61.921 | 277.356 | 5.94 | 1616 |  |  |  | 61.919 | 277.28 | 5.85 | 1621 |  |  |  | 61.92 | 533.41 | 0.151 | 80 | 4.64
868.06 | 277.455 | 5.84 | 1617 |  |  |  | 61.92 | 277.56 | 5.93 | 1615 |  |  |  | 61.924 | 277.246 | 5.85 | 1620 |  |  |  | 61.92 | 533.37 | 0.151 | 81 | 4.64
868.56 | 277.455 | 5.84 | 1617 |  |  |  | 61.92 | 277.56 | 5.93 | 1615 |  |  |  | 61.924 | 277.246 | 5.85 | 1620 |  |  |  | 61.92 | 533.37 | 0.151 | 81 | 4.64
869.06 | 277.502 | 5.8 | 1604 |  |  |  | 61.92 | 277.424 | 5.91 | 1608 |  |  |  | 61.919 | 277.351 | 5.8 | 1606 |  |  |  | 61.92 | 527.02 | 0.15 | 79 | 4.64
869.56 | 277.502 | 5.8 | 1604 |  |  |  | 61.92 | 277.424 | 5.91 | 1608 |  |  |  | 61.919 | 277.351 | 5.8 | 1606 |  |  |  | 61.92 | 527.02 | 0.15 | 79 | 4.64
870.06 | 277.417 | 5.79 | 1603 |  |  |  | 61.92 | 277.297 | 5.91 | 1610 |  |  |  | 61.92 | 277.326 | 5.81 | 1609 |  |  |  | 61.921 | 526.91 | 0.153 | 80 | 4.64
870.56 | 277.417 | 5.79 | 1603 |  |  |  | 61.92 | 277.297 | 5.91 | 1610 |  |  |  | 61.92 | 277.326 | 5.81 | 1609 |  |  |  | 61.921 | 526.91 | 0.153 | 80 | 4.64
871.06 | 277.488 | 5.82 | 1610 |  |  |  | 61.921 | 277.481 | 5.95 | 1620 |  |  |  | 61.92 | 277.291 | 5.84 | 1617 |  |  |  | 61.921 | 533.31 | 0.152 | 81 | 4.64
871.56 | 277.488 | 5.82 | 1610 |  |  |  | 61.921 | 277.481 | 5.95 | 1620 |  |  |  | 61.92 | 277.291 | 5.84 | 1617 |  |  |  | 61.921 | 533.31 | 0.152 | 81 | 4.64
872.06 | 277.384 | 5.81 | 1608 |  |  |  | 61.921 | 277.304 | 5.95 | 1620 |  |  |  | 61.92 | 277.252 | 5.87 | 1625 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
872.56 | 277.384 | 5.81 | 1608 |  |  |  | 61.921 | 277.304 | 5.95 | 1620 |  |  |  | 61.92 | 277.252 | 5.87 | 1625 |  |  |  | 61.921 | 533.37 | 0.15 | 80 | 4.64
873.06 | 277.446 | 5.82 | 1612 |  |  |  | 61.92 | 277.496 | 5.95 | 1620 |  |  |  | 61.924 | 277.354 | 5.86 | 1624 |  |  |  | 61.92 | 533.4 | 0.15 | 80 | 4.64
873.56 | 277.446 | 5.82 | 1612 |  |  |  | 61.92 | 277.496 | 5.95 | 1620 |  |  |  | 61.924 | 277.354 | 5.86 | 1624 |  |  |  | 61.92 | 533.4 | 0.15 | 80 | 4.64
874.06 | 277.338 | 5.83 | 1614 |  |  |  | 61.92 | 277.399 | 5.95 | 1622 |  |  |  | 61.919 | 277.334 | 5.84 | 1618 |  |  |  | 61.921 | 533.4 | 0.151 | 81 | 4.64
874.56 | 277.338 | 5.83 | 1614 |  |  |  | 61.92 | 277.399 | 5.95 | 1622 |  |  |  | 61.919 | 277.334 | 5.84 | 1618 |  |  |  | 61.921 | 533.4 | 0.151 | 81 | 4.64
875.06 | 277.403 | 5.66 | 1567 |  |  |  | 61.921 | 277.54 | 5.78 | 1576 |  |  |  | 61.923 | 277.298 | 5.68 | 1573 |  |  |  | 61.92 | 539.75 | 0.153 | 83 | 4.64
875.56 | 277.403 | 5.66 | 1567 |  |  |  | 61.921 | 277.54 | 5.78 | 1576 |  |  |  | 61.923 | 277.298 | 5.68 | 1573 |  |  |  | 61.92 | 539.75 | 0.153 | 83 | 4.64
876.06 | 277.328 | 5.64 | 1560 |  |  |  | 61.921 | 277.448 | 5.76 | 1567 |  |  |  | 61.921 | 277.251 | 5.67 | 1569 |  |  |  | 61.92 | 539.82 | 0.149 | 80 | 4.64
876.56 | 277.328 | 5.64 | 1560 |  |  |  | 61.921 | 277.448 | 5.76 | 1567 |  |  |  | 61.921 | 277.251 | 5.67 | 1569 |  |  |  | 61.92 | 539.82 | 0.149 | 80 | 4.64
877.06 | 277.418 | 5.83 | 1612 |  |  |  | 61.921 | 277.318 | 5.93 | 1617 |  |  |  | 61.919 | 277.366 | 5.86 | 1623 |  |  |  | 61.92 | 533.46 | 0.153 | 82 | 4.64
877.56 | 277.418 | 5.83 | 1612 |  |  |  | 61.921 | 277.318 | 5.93 | 1617 |  |  |  | 61.919 | 277.366 | 5.86 | 1623 |  |  |  | 61.92 | 533.46 | 0.153 | 82 | 4.64
878.06 | 277.455 | 5.84 | 1616 |  |  |  | 61.921 | 277.537 | 5.94 | 1619 |  |  |  | 61.919 | 277.344 | 5.85 | 1620 |  |  |  | 61.92 | 533.35 | 0.149 | 80 | 4.64
878.56 | 277.455 | 5.84 | 1616 |  |  |  | 61.921 | 277.537 | 5.94 | 1619 |  |  |  | 61.919 | 277.344 | 5.85 | 1620 |  |  |  | 61.92 | 533.35 | 0.149 | 80 | 4.64
879.06 | 277.377 | 5.84 | 1615 |  |  |  | 61.921 | 277.353 | 5.94 | 1617 |  |  |  | 61.921 | 277.317 | 5.85 | 1620 |  |  |  | 61.921 | 533.39 | 0.149 | 80 | 4.64
879.56 | 277.377 | 5.84 | 1615 |  |  |  | 61.921 | 277.353 | 5.94 | 1617 |  |  |  | 61.921 | 277.317 | 5.85 | 1620 |  |  |  | 61.921 | 533.39 | 0.149 | 80 | 4.64
880.06 | 277.445 | 5.85 | 1618 |  |  |  | 61.92 | 277.583 | 5.95 | 1621 |  |  |  | 61.923 | 277.278 | 5.84 | 1617 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
880.56 | 277.445 | 5.85 | 1618 |  |  |  | 61.92 | 277.583 | 5.95 | 1621 |  |  |  | 61.923 | 277.278 | 5.84 | 1617 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 4.64
881.06 | 277.357 | 5.8 | 1605 |  |  |  | 61.921 | 277.475 | 5.92 | 1612 |  |  |  | 61.919 | 277.237 | 5.8 | 1607 |  |  |  | 61.92 | 527.01 | 0.155 | 81 | 4.64
881.56 | 277.357 | 5.8 | 1605 |  |  |  | 61.921 | 277.475 | 5.92 | 1612 |  |  |  | 61.919 | 277.237 | 5.8 | 1607 |  |  |  | 61.92 | 527.01 | 0.155 | 81 | 4.64
882.06 | 277.421 | 5.78 | 1601 |  |  |  | 61.92 | 277.39 | 5.89 | 1604 |  |  |  | 61.92 | 277.329 | 5.82 | 1611 |  |  |  | 61.919 | 526.92 | 0.152 | 80 | 4.64
882.56 | 277.421 | 5.78 | 1601 |  |  |  | 61.92 | 277.39 | 5.89 | 1604 |  |  |  | 61.92 | 277.329 | 5.82 | 1611 |  |  |  | 61.919 | 526.92 | 0.152 | 80 | 4.64
883.06 | 277.365 | 5.82 | 1609 |  |  |  | 61.921 | 277.498 | 5.94 | 1617 |  |  |  | 61.92 | 277.309 | 5.86 | 1623 |  |  |  | 61.921 | 533.35 | 0.149 | 79 | 4.64
883.56 | 277.365 | 5.82 | 1609 |  |  |  | 61.921 | 277.498 | 5.94 | 1617 |  |  |  | 61.92 | 277.309 | 5.86 | 1623 |  |  |  | 61.921 | 533.35 | 0.149 | 79 | 4.64
884.06 | 277.422 | 5.84 | 1616 |  |  |  | 61.92 | 277.359 | 5.93 | 1614 |  |  |  | 61.919 | 277.284 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 4.64
884.56 | 277.422 | 5.84 | 1616 |  |  |  | 61.92 | 277.359 | 5.93 | 1614 |  |  |  | 61.919 | 277.284 | 5.85 | 1620 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 4.64
885.06 | 277.34 | 5.84 | 1615 |  |  |  | 61.92 | 277.535 | 5.95 | 1621 |  |  |  | 61.919 | 277.248 | 5.86 | 1623 |  |  |  | 61.92 | 533.35 | 0.151 | 81 | 4.64
885.56 | 277.34 | 5.84 | 1615 |  |  |  | 61.92 | 277.535 | 5.95 | 1621 |  |  |  | 61.919 | 277.248 | 5.86 | 1623 |  |  |  | 61.92 | 533.35 | 0.151 | 81 | 4.64
886.06 | 277.416 | 5.81 | 1609 |  |  |  | 61.921 | 277.389 | 5.96 | 1623 |  |  |  | 61.921 | 277.343 | 5.85 | 1619 |  |  |  | 61.921 | 533.36 | 0.156 | 83 | 4.64
886.56 | 277.416 | 5.81 | 1609 |  |  |  | 61.921 | 277.389 | 5.96 | 1623 |  |  |  | 61.921 | 277.343 | 5.85 | 1619 |  |  |  | 61.921 | 533.36 | 0.156 | 83 | 4.64
887.06 | 277.439 | 5.65 | 1565 |  |  |  | 61.921 | 277.581 | 5.79 | 1575 |  |  |  | 61.922 | 277.314 | 5.7 | 1578 |  |  |  | 61.92 | 539.74 | 0.151 | 81 | 4.64
887.56 | 277.439 | 5.65 | 1565 |  |  |  | 61.921 | 277.581 | 5.79 | 1575 |  |  |  | 61.922 | 277.314 | 5.7 | 1578 |  |  |  | 61.92 | 539.74 | 0.151 | 81 | 4.64
888.06 | 277.375 | 5.66 | 1565 |  |  |  | 61.921 | 277.426 | 5.78 | 1571 |  |  |  | 61.921 | 277.295 | 5.69 | 1575 |  |  |  | 61.918 | 539.79 | 0.153 | 83 | 4.64
888.56 | 277.375 | 5.66 | 1565 |  |  |  | 61.921 | 277.426 | 5.78 | 1571 |  |  |  | 61.921 | 277.295 | 5.69 | 1575 |  |  |  | 61.918 | 539.79 | 0.153 | 83 | 4.64
889.06 | 277.445 | 5.83 | 1615 |  |  |  | 61.921 | 277.319 | 5.94 | 1618 |  |  |  | 61.918 | 277.265 | 5.86 | 1623 |  |  |  | 61.919 | 533.41 | 0.149 | 80 | 4.64
889.59 | 277.445 | 5.83 | 1615 |  |  |  | 61.921 | 277.319 | 5.94 | 1618 |  |  |  | 61.918 | 277.265 | 5.86 | 1623 |  |  |  | 61.919 | 533.41 | 0.149 | 80 | 4.64
890.09 | 277.369 | 5.84 | 1615 |  |  |  | 61.921 | 277.528 | 5.93 | 1615 |  |  |  | 61.92 | 277.358 | 5.85 | 1621 |  |  |  | 61.921 | 533.39 | 0.15 | 80 | 4.64
890.58 | 277.369 | 5.84 | 1615 |  |  |  | 61.921 | 277.528 | 5.93 | 1615 |  |  |  | 61.92 | 277.358 | 5.85 | 1621 |  |  |  | 61.921 | 533.39 | 0.15 | 80 | 4.64
891.08 | 277.428 | 5.82 | 1612 |  |  |  | 61.92 | 277.391 | 5.95 | 1621 |  |  |  | 61.919 | 277.33 | 5.85 | 1619 |  |  |  | 61.921 | 533.36 | 0.157 | 84 | 4.64
891.56 | 277.428 | 5.82 | 1612 |  |  |  | 61.92 | 277.391 | 5.95 | 1621 |  |  |  | 61.919 | 277.33 | 5.85 | 1619 |  |  |  | 61.921 | 533.36 | 0.157 | 84 | 4.64
892.06 | 277.367 | 5.82 | 1611 |  |  |  | 61.92 | 277.529 | 5.95 | 1621 |  |  |  | 61.923 | 277.297 | 5.84 | 1616 |  |  |  | 61.92 | 533.38 | 0.147 | 78 | 4.64
892.6 | 277.367 | 5.82 | 1611 |  |  |  | 61.92 | 277.529 | 5.95 | 1621 |  |  |  | 61.923 | 277.297 | 5.84 | 1616 |  |  |  | 61.92 | 533.38 | 0.147 | 78 | 4.64
893.1 | 277.437 | 5.78 | 1599 |  |  |  | 61.921 | 277.389 | 5.9 | 1605 |  |  |  | 61.92 | 277.27 | 5.82 | 1610 |  |  |  | 61.921 | 527.01 | 0.151 | 80 | 4.64
893.59 | 277.367 | 5.78 | 1600 |  |  |  | 61.921 | 277.431 | 5.9 | 1607 |  |  |  | 61.919 | 277.233 | 5.82 | 1612 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 4.64
894.09 | 277.367 | 5.78 | 1600 |  |  |  | 61.921 | 277.431 | 5.9 | 1607 |  |  |  | 61.919 | 277.233 | 5.82 | 1612 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 4.64
894.57 | 277.458 | 5.83 | 1613 |  |  |  | 61.921 | 277.463 | 5.93 | 1617 |  |  |  | 61.92 | 277.347 | 5.84 | 1617 |  |  |  | 61.919 | 533.35 | 0.155 | 83 | 4.64
895.07 | 277.458 | 5.83 | 1613 |  |  |  | 61.921 | 277.463 | 5.93 | 1617 |  |  |  | 61.92 | 277.347 | 5.84 | 1617 |  |  |  | 61.919 | 533.35 | 0.155 | 83 | 4.64
895.56 | 277.431 | 5.84 | 1615 |  |  |  | 61.921 | 277.366 | 5.95 | 1621 |  |  |  | 61.919 | 277.323 | 5.86 | 1622 |  |  |  | 61.921 | 533.35 | 0.154 | 82 | 4.64
896.06 | 277.431 | 5.84 | 1615 |  |  |  | 61.921 | 277.366 | 5.95 | 1621 |  |  |  | 61.919 | 277.323 | 5.86 | 1622 |  |  |  | 61.921 | 533.35 | 0.154 | 82 | 4.64
896.56 | 277.403 | 5.81 | 1609 |  |  |  | 61.919 | 277.467 | 5.96 | 1624 |  |  |  | 61.919 | 277.297 | 5.85 | 1620 |  |  |  | 61.92 | 533.36 | 0.155 | 83 | 4.64
897.06 | 277.403 | 5.81 | 1609 |  |  |  | 61.919 | 277.467 | 5.96 | 1624 |  |  |  | 61.919 | 277.297 | 5.85 | 1620 |  |  |  | 61.92 | 533.36 | 0.155 | 83 | 4.64
897.56 | 277.47 | 5.81 | 1609 |  |  |  | 61.921 | 277.349 | 5.94 | 1617 |  |  |  | 61.92 | 277.27 | 5.85 | 1621 |  |  |  | 61.92 | 533.35 | 0.157 | 84 | 4.64
898.06 | 277.47 | 5.81 | 1609 |  |  |  | 61.921 | 277.349 | 5.94 | 1617 |  |  |  | 61.92 | 277.27 | 5.85 | 1621 |  |  |  | 61.92 | 533.35 | 0.157 | 84 | 4.64
898.56 | 277.372 | 5.66 | 1567 |  |  |  | 61.92 | 277.551 | 5.78 | 1575 |  |  |  | 61.922 | 277.344 | 5.69 | 1575 |  |  |  | 61.92 | 539.77 | 0.144 | 78 | 4.64
899.06 | 277.372 | 5.66 | 1567 |  |  |  | 61.92 | 277.551 | 5.78 | 1575 |  |  |  | 61.922 | 277.344 | 5.69 | 1575 |  |  |  | 61.92 | 539.77 | 0.144 | 78 | 4.64
899.56 | 277.445 | 5.66 | 1565 |  |  |  | 61.921 | 277.437 | 5.78 | 1573 |  |  |  | 61.92 | 277.318 | 5.66 | 1568 |  |  |  | 61.921 | 539.83 | 0.153 | 82 | 4.64
900.06 | 277.445 | 5.66 | 1565 |  |  |  | 61.921 | 277.437 | 5.78 | 1573 |  |  |  | 61.92 | 277.318 | 5.66 | 1568 |  |  |  | 61.921 | 539.83 | 0.153 | 82 | 4.64
900.56 | 277.385 | 5.81 | 1607 |  |  |  | 61.92 | 277.26 | 5.94 | 1619 |  |  |  | 61.921 | 277.3 | 5.85 | 1619 |  |  |  | 61.919 | 533.42 | 0.149 | 79 | 4.64
901.06 | 277.385 | 5.81 | 1607 |  |  |  | 61.92 | 277.26 | 5.94 | 1619 |  |  |  | 61.921 | 277.3 | 5.85 | 1619 |  |  |  | 61.919 | 533.42 | 0.149 | 79 | 4.64
901.56 | 277.456 | 5.82 | 1610 |  |  |  | 61.92 | 277.433 | 5.94 | 1619 |  |  |  | 61.919 | 277.276 | 5.87 | 1625 |  |  |  | 61.921 | 533.39 | 0.157 | 84 | 4.64
902.06 | 277.456 | 5.82 | 1610 |  |  |  | 61.92 | 277.433 | 5.94 | 1619 |  |  |  | 61.919 | 277.276 | 5.87 | 1625 |  |  |  | 61.921 | 533.39 | 0.157 | 84 | 4.64
902.56 | 277.371 | 5.84 | 1615 |  |  |  | 61.921 | 277.342 | 5.94 | 1618 |  |  |  | 61.919 | 277.374 | 5.83 | 1616 |  |  |  | 61.921 | 533.38 | 0.152 | 81 | 4.64
903.06 | 277.371 | 5.84 | 1615 |  |  |  | 61.921 | 277.342 | 5.94 | 1618 |  |  |  | 61.919 | 277.374 | 5.83 | 1616 |  |  |  | 61.921 | 533.38 | 0.152 | 81 | 4.64
903.56 | 277.437 | 5.83 | 1614 |  |  |  | 61.921 | 277.51 | 5.94 | 1619 |  |  |  | 61.923 | 277.345 | 5.84 | 1619 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 4.64
904.06 | 277.437 | 5.83 | 1614 |  |  |  | 61.921 | 277.51 | 5.94 | 1619 |  |  |  | 61.923 | 277.345 | 5.84 | 1619 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 4.64
904.56 | 277.386 | 5.78 | 1599 |  |  |  | 61.92 | 277.39 | 5.91 | 1609 |  |  |  | 61.919 | 277.311 | 5.81 | 1609 |  |  |  | 61.921 | 527.05 | 0.152 | 80 | 4.64
905.06 | 277.386 | 5.78 | 1599 |  |  |  | 61.92 | 277.39 | 5.91 | 1609 |  |  |  | 61.919 | 277.311 | 5.81 | 1609 |  |  |  | 61.921 | 527.05 | 0.152 | 80 | 4.64
905.56 | 277.407 | 5.78 | 1600 |  |  |  | 61.921 | 277.408 | 5.91 | 1610 |  |  |  | 61.92 | 277.29 | 5.81 | 1609 |  |  |  | 61.92 | 526.97 | 0.156 | 82 | 4.64
906.06 | 277.407 | 5.78 | 1600 |  |  |  | 61.921 | 277.408 | 5.91 | 1610 |  |  |  | 61.92 | 277.29 | 5.81 | 1609 |  |  |  | 61.92 | 526.97 | 0.156 | 82 | 4.64
906.56 | 277.476 | 5.83 | 1613 |  |  |  | 61.921 | 277.447 | 5.95 | 1620 |  |  |  | 61.92 | 277.264 | 5.85 | 1619 |  |  |  | 61.92 | 533.33 | 0.154 | 82 | 4.64
907.06 | 277.476 | 5.83 | 1613 |  |  |  | 61.921 | 277.447 | 5.95 | 1620 |  |  |  | 61.92 | 277.264 | 5.85 | 1619 |  |  |  | 61.92 | 533.33 | 0.154 | 82 | 4.64
907.56 | 277.409 | 5.83 | 1615 |  |  |  | 61.92 | 277.273 | 5.94 | 1618 |  |  |  | 61.92 | 277.36 | 5.86 | 1624 |  |  |  | 61.919 | 533.45 | 0.155 | 83 | 4.64
908.06 | 277.409 | 5.83 | 1615 |  |  |  | 61.92 | 277.273 | 5.94 | 1618 |  |  |  | 61.92 | 277.36 | 5.86 | 1624 |  |  |  | 61.919 | 533.45 | 0.155 | 83 | 4.64
908.56 | 277.456 | 5.82 | 1610 |  |  |  | 61.92 | 277.528 | 5.92 | 1613 |  |  |  | 61.92 | 277.319 | 5.85 | 1620 |  |  |  | 61.921 | 533.39 | 0.155 | 83 | 4.64
909.06 | 277.456 | 5.82 | 1610 |  |  |  | 61.92 | 277.528 | 5.92 | 1613 |  |  |  | 61.92 | 277.319 | 5.85 | 1620 |  |  |  | 61.921 | 533.39 | 0.155 | 83 | 4.64
909.56 | 277.364 | 5.84 | 1617 |  |  |  | 61.92 | 277.331 | 5.95 | 1622 |  |  |  | 61.92 | 277.279 | 5.86 | 1623 |  |  |  | 61.92 | 533.37 | 0.156 | 83 | 4.64
910.06 | 277.364 | 5.84 | 1617 |  |  |  | 61.92 | 277.331 | 5.95 | 1622 |  |  |  | 61.92 | 277.279 | 5.86 | 1623 |  |  |  | 61.92 | 533.37 | 0.156 | 83 | 4.64
910.56 | 277.425 | 5.68 | 1572 |  |  |  | 61.92 | 277.497 | 5.79 | 1577 |  |  |  | 61.921 | 277.253 | 5.7 | 1578 |  |  |  | 61.919 | 539.67 | 0.154 | 83 | 4.64
911.06 | 277.425 | 5.68 | 1572 |  |  |  | 61.92 | 277.497 | 5.79 | 1577 |  |  |  | 61.921 | 277.253 | 5.7 | 1578 |  |  |  | 61.919 | 539.67 | 0.154 | 83 | 4.64
911.56 | 277.327 | 5.66 | 1565 |  |  |  | 61.92 | 277.418 | 5.77 | 1571 |  |  |  | 61.919 | 277.362 | 5.69 | 1575 |  |  |  | 61.921 | 539.77 | 0.155 | 84 | 4.64
912.06 | 277.327 | 5.66 | 1565 |  |  |  | 61.92 | 277.418 | 5.77 | 1571 |  |  |  | 61.919 | 277.362 | 5.69 | 1575 |  |  |  | 61.921 | 539.77 | 0.155 | 84 | 4.64
912.56 | 277.408 | 5.84 | 1615 |  |  |  | 61.92 | 277.304 | 5.94 | 1618 |  |  |  | 61.919 | 277.348 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.158 | 84 | 4.64
913.06 | 277.408 | 5.84 | 1615 |  |  |  | 61.92 | 277.304 | 5.94 | 1618 |  |  |  | 61.919 | 277.348 | 5.85 | 1621 |  |  |  | 61.921 | 533.41 | 0.158 | 84 | 4.64
913.56 | 277.362 | 5.85 | 1618 |  |  |  | 61.921 | 277.483 | 5.95 | 1620 |  |  |  | 61.92 | 277.298 | 5.84 | 1617 |  |  |  | 61.92 | 533.38 | 0.155 | 83 | 4.64
914.06 | 277.362 | 5.85 | 1618 |  |  |  | 61.921 | 277.483 | 5.95 | 1620 |  |  |  | 61.92 | 277.298 | 5.84 | 1617 |  |  |  | 61.92 | 533.38 | 0.155 | 83 | 4.64
914.56 | 277.379 | 5.83 | 1613 |  |  |  | 61.921 | 277.352 | 5.93 | 1616 |  |  |  | 61.919 | 277.274 | 5.85 | 1619 |  |  |  | 61.921 | 533.37 | 0.155 | 83 | 4.64
915.06 | 277.379 | 5.83 | 1613 |  |  |  | 61.921 | 277.352 | 5.93 | 1616 |  |  |  | 61.919 | 277.274 | 5.85 | 1619 |  |  |  | 61.921 | 533.37 | 0.155 | 83 | 4.64
915.56 | 277.442 | 5.81 | 1609 |  |  |  | 61.919 | 277.554 | 5.95 | 1621 |  |  |  | 61.922 | 277.349 | 5.84 | 1618 |  |  |  | 61.922 | 533.41 | 0.155 | 83 | 4.64
916.06 | 277.442 | 5.81 | 1609 |  |  |  | 61.919 | 277.554 | 5.95 | 1621 |  |  |  | 61.922 | 277.349 | 5.84 | 1618 |  |  |  | 61.922 | 533.41 | 0.155 | 83 | 4.64
916.56 | 277.379 | 5.78 | 1600 |  |  |  | 61.92 | 277.374 | 5.9 | 1607 |  |  |  | 61.919 | 277.338 | 5.82 | 1612 |  |  |  | 61.92 | 527.11 | 0.156 | 82 | 4.64
917.06 | 277.379 | 5.78 | 1600 |  |  |  | 61.92 | 277.374 | 5.9 | 1607 |  |  |  | 61.919 | 277.338 | 5.82 | 1612 |  |  |  | 61.92 | 527.11 | 0.156 | 82 | 4.64
917.56 | 277.435 | 5.79 | 1602 |  |  |  | 61.92 | 277.468 | 5.89 | 1605 |  |  |  | 61.919 | 277.306 | 5.81 | 1608 |  |  |  | 61.92 | 526.97 | 0.155 | 82 | 4.64
918.06 | 277.435 | 5.79 | 1602 |  |  |  | 61.92 | 277.468 | 5.89 | 1605 |  |  |  | 61.919 | 277.306 | 5.81 | 1608 |  |  |  | 61.92 | 526.97 | 0.155 | 82 | 4.64
918.56 | 277.361 | 5.82 | 1610 |  |  |  | 61.921 | 277.476 | 5.94 | 1619 |  |  |  | 61.92 | 277.272 | 5.84 | 1618 |  |  |  | 61.92 | 533.33 | 0.151 | 80 | 4.64
919.06 | 277.361 | 5.82 | 1610 |  |  |  | 61.921 | 277.476 | 5.94 | 1619 |  |  |  | 61.92 | 277.272 | 5.84 | 1618 |  |  |  | 61.92 | 533.33 | 0.151 | 80 | 4.64
919.56 | 277.434 | 5.81 | 1608 |  |  |  | 61.92 | 277.342 | 5.95 | 1619 |  |  |  | 61.919 | 277.244 | 5.85 | 1620 |  |  |  | 61.919 | 533.37 | 0.153 | 82 | 4.64
920.06 | 277.434 | 5.81 | 1608 |  |  |  | 61.92 | 277.342 | 5.95 | 1619 |  |  |  | 61.919 | 277.244 | 5.85 | 1620 |  |  |  | 61.919 | 533.37 | 0.153 | 82 | 4.64
920.56 | 277.327 | 5.82 | 1610 |  |  |  | 61.92 | 277.539 | 5.94 | 1619 |  |  |  | 61.919 | 277.343 | 5.86 | 1623 |  |  |  | 61.92 | 533.38 | 0.151 | 80 | 4.64
921.09 | 277.327 | 5.82 | 1610 |  |  |  | 61.92 | 277.539 | 5.94 | 1619 |  |  |  | 61.919 | 277.343 | 5.86 | 1623 |  |  |  | 61.92 | 533.38 | 0.151 | 80 | 4.64
921.59 | 277.396 | 5.83 | 1614 |  |  |  | 61.921 | 277.394 | 5.93 | 1616 |  |  |  | 61.921 | 277.318 | 5.86 | 1622 |  |  |  | 61.92 | 533.38 | 0.149 | 80 | 4.64
922.08 | 277.396 | 5.83 | 1614 |  |  |  | 61.921 | 277.394 | 5.93 | 1616 |  |  |  | 61.921 | 277.318 | 5.86 | 1622 |  |  |  | 61.92 | 533.38 | 0.149 | 80 | 4.64
922.58 | 277.339 | 5.68 | 1572 |  |  |  | 61.92 | 277.585 | 5.79 | 1578 |  |  |  | 61.924 | 277.279 | 5.71 | 1581 |  |  |  | 61.921 | 539.66 | 0.151 | 81 | 4.64
923.06 | 277.339 | 5.68 | 1572 |  |  |  | 61.92 | 277.585 | 5.79 | 1578 |  |  |  | 61.924 | 277.279 | 5.71 | 1581 |  |  |  | 61.921 | 539.66 | 0.151 | 81 | 4.64
923.56 | 277.374 | 5.64 | 1561 |  |  |  | 61.921 | 277.468 | 5.76 | 1570 |  |  |  | 61.92 | 277.254 | 5.65 | 1564 |  |  |  | 61.92 | 539.85 | 0.149 | 81 | 4.64
924.1 | 277.374 | 5.64 | 1561 |  |  |  | 61.921 | 277.468 | 5.76 | 1570 |  |  |  | 61.92 | 277.254 | 5.65 | 1564 |  |  |  | 61.92 | 539.85 | 0.149 | 81 | 4.64
924.6 | 277.44 | 5.82 | 1611 |  |  |  | 61.919 | 277.384 | 5.97 | 1626 |  |  |  | 61.92 | 277.344 | 5.86 | 1623 |  |  |  | 61.92 | 533.5 | 0.151 | 80 | 4.64
925.08 | 277.377 | 5.83 | 1612 |  |  |  | 61.921 | 277.48 | 5.94 | 1621 |  |  |  | 61.921 | 277.327 | 5.86 | 1622 |  |  |  | 61.921 | 533.41 | 0.15 | 80 | 4.64
925.58 | 277.377 | 5.83 | 1612 |  |  |  | 61.921 | 277.48 | 5.94 | 1621 |  |  |  | 61.921 | 277.327 | 5.86 | 1622 |  |  |  | 61.921 | 533.41 | 0.15 | 80 | 4.64
926.07 | 277.437 | 5.83 | 1614 |  |  |  | 61.92 | 277.374 | 5.94 | 1620 |  |  |  | 61.92 | 277.294 | 5.85 | 1620 |  |  |  | 61.921 | 533.43 | 0.155 | 83 | 4.64
926.57 | 277.437 | 5.83 | 1614 |  |  |  | 61.92 | 277.374 | 5.94 | 1620 |  |  |  | 61.92 | 277.294 | 5.85 | 1620 |  |  |  | 61.921 | 533.43 | 0.155 | 83 | 4.64
927.06 | 277.36 | 5.84 | 1615 |  |  |  | 61.92 | 277.577 | 5.94 | 1620 |  |  |  | 61.92 | 277.257 | 5.84 | 1618 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 4.64
927.56 | 277.36 | 5.84 | 1615 |  |  |  | 61.92 | 277.577 | 5.94 | 1620 |  |  |  | 61.92 | 277.257 | 5.84 | 1618 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 4.64
928.06 | 277.432 | 5.79 | 1604 |  |  |  | 61.921 | 277.433 | 5.9 | 1607 |  |  |  | 61.921 | 277.353 | 5.81 | 1608 |  |  |  | 61.919 | 527.13 | 0.156 | 82 | 4.64
928.56 | 277.432 | 5.79 | 1604 |  |  |  | 61.921 | 277.433 | 5.9 | 1607 |  |  |  | 61.921 | 277.353 | 5.81 | 1608 |  |  |  | 61.919 | 527.13 | 0.156 | 82 | 4.64
929.06 | 277.359 | 5.78 | 1599 |  |  |  | 61.921 | 277.531 | 5.91 | 1609 |  |  |  | 61.922 | 277.34 | 5.8 | 1606 |  |  |  | 61.921 | 526.96 | 0.151 | 80 | 4.64
929.56 | 277.359 | 5.78 | 1599 |  |  |  | 61.921 | 277.531 | 5.91 | 1609 |  |  |  | 61.922 | 277.34 | 5.8 | 1606 |  |  |  | 61.921 | 526.96 | 0.151 | 80 | 4.64
930.06 | 277.43 | 5.83 | 1613 |  |  |  | 61.921 | 277.462 | 5.95 | 1621 |  |  |  | 61.92 | 277.317 | 5.84 | 1617 |  |  |  | 61.919 | 533.33 | 0.156 | 83 | 4.64
930.56 | 277.43 | 5.83 | 1613 |  |  |  | 61.921 | 277.462 | 5.95 | 1621 |  |  |  | 61.92 | 277.317 | 5.84 | 1617 |  |  |  | 61.919 | 533.33 | 0.156 | 83 | 4.64
931.06 | 277.397 | 5.82 | 1611 |  |  |  | 61.919 | 277.347 | 5.93 | 1617 |  |  |  | 61.919 | 277.277 | 5.86 | 1622 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
931.56 | 277.397 | 5.82 | 1611 |  |  |  | 61.919 | 277.347 | 5.93 | 1617 |  |  |  | 61.919 | 277.277 | 5.86 | 1622 |  |  |  | 61.92 | 533.39 | 0.151 | 81 | 4.64
932.06 | 277.417 | 5.85 | 1618 |  |  |  | 61.921 | 277.517 | 5.94 | 1619 |  |  |  | 61.921 | 277.24 | 5.85 | 1621 |  |  |  | 61.919 | 533.39 | 0.157 | 84 | 4.64
932.56 | 277.417 | 5.85 | 1618 |  |  |  | 61.921 | 277.517 | 5.94 | 1619 |  |  |  | 61.921 | 277.24 | 5.85 | 1621 |  |  |  | 61.919 | 533.39 | 0.157 | 84 | 4.64
933.38 | 277.472 | 5.84 | 1616 |  |  |  | 61.919 | 277.415 | 5.93 | 1618 |  |  |  | 61.92 | 277.335 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.153 | 82 | 4.64
933.56 | 277.472 | 5.84 | 1616 |  |  |  | 61.919 | 277.415 | 5.93 | 1618 |  |  |  | 61.92 | 277.335 | 5.86 | 1622 |  |  |  | 61.92 | 533.41 | 0.153 | 82 | 4.64
934.06 | 278.055 | 6.25 | 1580 |  |  |  | 58.58 | 278.221 | 6.34 | 1583 |  |  |  | 58.583 | 277.947 | 6.28 | 1589 |  |  |  | 58.581 | 539.59 | 0.149 | 80 | 4.64
934.56 | 278.055 | 6.25 | 1580 |  |  |  | 58.58 | 278.221 | 6.34 | 1583 |  |  |  | 58.583 | 277.947 | 6.28 | 1589 |  |  |  | 58.581 | 539.59 | 0.149 | 80 | 4.64
935.06 | 279.183 | 6.17 | 1567 |  |  |  | 58.581 | 279.21 | 6.28 | 1570 |  |  |  | 58.579 | 278.947 | 6.19 | 1574 |  |  |  | 58.58 | 539.81 | 0.147 | 79 | 4.64
935.56 | 279.183 | 6.17 | 1567 |  |  |  | 58.581 | 279.21 | 6.28 | 1570 |  |  |  | 58.579 | 278.947 | 6.19 | 1574 |  |  |  | 58.58 | 539.81 | 0.147 | 79 | 4.64
936.06 | 278.283 | 6.12 | 1613 |  |  |  | 58.58 | 278.28 | 6.24 | 1623 |  |  |  | 58.58 | 278.163 | 6.16 | 1626 |  |  |  | 58.581 | 534.21 | 0.151 | 81 | 4.64
936.56 | 278.283 | 6.12 | 1613 |  |  |  | 58.58 | 278.28 | 6.24 | 1623 |  |  |  | 58.58 | 278.163 | 6.16 | 1626 |  |  |  | 58.581 | 534.21 | 0.151 | 81 | 4.64
937.06 | 277.911 | 5.97 | 1617 |  |  |  | 58.58 | 277.997 | 6.08 | 1622 |  |  |  | 58.58 | 277.808 | 5.99 | 1622 |  |  |  | 58.579 | 533.37 | 0.151 | 80 | 4.64
937.56 | 277.911 | 5.97 | 1617 |  |  |  | 58.58 | 277.997 | 6.08 | 1622 |  |  |  | 58.58 | 277.808 | 5.99 | 1622 |  |  |  | 58.579 | 533.37 | 0.151 | 80 | 4.64
938.06 | 277.559 | 5.89 | 1614 |  |  |  | 58.58 | 277.539 | 6.01 | 1620 |  |  |  | 58.58 | 277.53 | 5.92 | 1623 |  |  |  | 58.58 | 533.4 | 0.153 | 82 | 4.64
938.56 | 277.559 | 5.89 | 1614 |  |  |  | 58.58 | 277.539 | 6.01 | 1620 |  |  |  | 58.58 | 277.53 | 5.92 | 1623 |  |  |  | 58.58 | 533.4 | 0.153 | 82 | 4.64
939.06 | 277.545 | 5.86 | 1614 |  |  |  | 58.58 | 277.629 | 5.98 | 1621 |  |  |  | 58.58 | 277.384 | 5.89 | 1624 |  |  |  | 58.581 | 533.39 | 0.149 | 80 | 4.64
939.56 | 277.545 | 5.86 | 1614 |  |  |  | 58.58 | 277.629 | 5.98 | 1621 |  |  |  | 58.58 | 277.384 | 5.89 | 1624 |  |  |  | 58.581 | 533.39 | 0.149 | 80 | 4.64
940.06 | 277.492 | 5.83 | 1611 |  |  |  | 58.579 | 277.414 | 5.96 | 1620 |  |  |  | 58.58 | 277.326 | 5.87 | 1622 |  |  |  | 58.579 | 529.63 | 0.151 | 80 | 4.64
940.56 | 277.492 | 5.83 | 1611 |  |  |  | 58.579 | 277.414 | 5.96 | 1620 |  |  |  | 58.58 | 277.326 | 5.87 | 1622 |  |  |  | 58.579 | 529.63 | 0.151 | 80 | 4.64
941.06 | 277.473 | 5.8 | 1602 |  |  |  | 58.581 | 277.541 | 5.92 | 1610 |  |  |  | 58.582 | 277.381 | 5.82 | 1610 |  |  |  | 58.58 | 526.96 | 0.147 | 77 | 4.64
941.56 | 277.473 | 5.8 | 1602 |  |  |  | 58.581 | 277.541 | 5.92 | 1610 |  |  |  | 58.582 | 277.381 | 5.82 | 1610 |  |  |  | 58.58 | 526.96 | 0.147 | 77 | 4.64
942.06 | 277.502 | 5.81 | 1607 |  |  |  | 58.58 | 277.476 | 5.92 | 1613 |  |  |  | 58.58 | 277.347 | 5.82 | 1612 |  |  |  | 58.58 | 530.25 | 0.149 | 79 | 4.64
942.56 | 277.502 | 5.81 | 1607 |  |  |  | 58.58 | 277.476 | 5.92 | 1613 |  |  |  | 58.58 | 277.347 | 5.82 | 1612 |  |  |  | 58.58 | 530.25 | 0.149 | 79 | 4.64
943.06 | 277.447 | 5.83 | 1613 |  |  |  | 58.58 | 277.308 | 5.94 | 1617 |  |  |  | 58.579 | 277.316 | 5.86 | 1621 |  |  |  | 58.581 | 533.42 | 0.152 | 81 | 4.64

## frt_rms_20.csv
TIME | AC_VRMS_1 | AC_IRMS_1 | AC_P_1 | AC_S_1 | AC_Q_1 | AC_PF_1 | AC_FREQ_1 | AC_VRMS_2 | AC_IRMS_2 | AC_P_2 | AC_S_2 | AC_Q_2 | AC_PF_2 | AC_FREQ_2 | AC_VRMS_3 | AC_IRMS_3 | AC_P_3 | AC_S_3 | AC_Q_3 | AC_PF_3 | AC_FREQ_3 | DC_V | DC_I | DC_P | AC_IRMS_MIN
0 | 277.49 | 5.83 | 1613 |  |  |  | 58.579 | 277.498 | 5.94 | 1620 |  |  |  | 58.579 | 277.281 | 5.86 | 1622 |  |  |  | 58.58 | 533.4 | 0.152 | 81
0.6 | 277.282 | 0 | 300 |  |  |  | 58.581 | 277.199 | 0 | 301 |  |  |  | 58.579 | 277.203 | 0 | 313 |  |  |  | 58.58 | 533.36 | 0.155 | 83
1.1 | 277.282 | 0 | 300 |  |  |  | 58.581 | 277.199 | 0 | 301 |  |  |  | 58.579 | 277.203 | 0 | 313 |  |  |  | 58.58 | 533.36 | 0.155 | 83
1.57 | 277.385 | 0 | 299 |  |  |  | 58.581 | 277.457 | 0 | 301 |  |  |  | 58.583 | 277.247 | 0 | 308 |  |  |  | 58.58 | 535.07 | 0.152 | 81
2.07 | 277.385 | 0 | 299 |  |  |  | 58.581 | 277.457 | 0 | 301 |  |  |  | 58.583 | 277.247 | 0 | 308 |  |  |  | 58.58 | 535.07 | 0.152 | 81
2.56 | 277.306 | 0 | 287 |  |  |  | 58.581 | 277.334 | 0 | 295 |  |  |  | 58.579 | 277.205 | 0 | 309 |  |  |  | 58.58 | 539.82 | 0.15 | 81
3.06 | 277.306 | 0 | 287 |  |  |  | 58.581 | 277.334 | 0 | 295 |  |  |  | 58.579 | 277.205 | 0 | 309 |  |  |  | 58.58 | 539.82 | 0.15 | 81
3.56 | 277.36 | 0 | 301 |  |  |  | 58.58 | 277.45 | 0 | 305 |  |  |  | 58.579 | 277.216 | 0 | 310 |  |  |  | 58.58 | 538.55 | 0.144 | 78
4.06 | 277.36 | 0 | 301 |  |  |  | 58.58 | 277.45 | 0 | 305 |  |  |  | 58.579 | 277.216 | 0 | 310 |  |  |  | 58.58 | 538.55 | 0.144 | 78
4.56 | 277.296 | 0 | 301 |  |  |  | 58.578 | 277.434 | 0 | 305 |  |  |  | 58.579 | 277.198 | 0 | 313 |  |  |  | 58.579 | 533.37 | 0.149 | 80
4.65 | 277.296 | 0 | 301 |  |  |  | 58.578 | 277.434 | 0 | 305 |  |  |  | 58.579 | 277.198 | 0 | 313 |  |  |  | 58.579 | 533.37 | 0.149 | 80 | 0
5.07 | 277.296 | 0 | 301 |  |  |  | 58.578 | 277.434 | 0 | 305 |  |  |  | 58.579 | 277.198 | 0 | 313 |  |  |  | 58.579 | 533.37 | 0.149 | 80 | 0
5.56 | 277.475 | 0 | 298 |  |  |  | 58.58 | 277.41 | 0 | 303 |  |  |  | 58.58 | 277.427 | 0 | 309 |  |  |  | 58.58 | 533.4 | 0.152 | 81 | 0
6.06 | 277.475 | 0 | 298 |  |  |  | 58.58 | 277.41 | 0 | 303 |  |  |  | 58.58 | 277.427 | 0 | 309 |  |  |  | 58.58 | 533.4 | 0.152 | 81 | 0
6.56 | 277.362 | 0 | 298 |  |  |  | 58.581 | 277.476 | 0 | 301 |  |  |  | 58.58 | 277.378 | 0 | 312 |  |  |  | 58.58 | 533.24 | 0.151 | 81 | 0
7.06 | 277.362 | 0 | 298 |  |  |  | 58.581 | 277.476 | 0 | 301 |  |  |  | 58.58 | 277.378 | 0 | 312 |  |  |  | 58.58 | 533.24 | 0.151 | 81 | 0
7.56 | 277.309 | 0 | 298 |  |  |  | 58.58 | 277.349 | 0 | 305 |  |  |  | 58.579 | 277.345 | 0 | 312 |  |  |  | 58.58 | 533.34 | 0.154 | 82 | 0
8.06 | 277.309 | 0 | 298 |  |  |  | 58.58 | 277.349 | 0 | 305 |  |  |  | 58.579 | 277.345 | 0 | 312 |  |  |  | 58.58 | 533.34 | 0.154 | 82 | 0
8.56 | 277.376 | 0 | 300 |  |  |  | 58.58 | 277.537 | 0 | 301 |  |  |  | 58.583 | 277.341 | 0 | 312 |  |  |  | 58.579 | 527 | 0.145 | 76 | 0
9.06 | 277.376 | 0 | 300 |  |  |  | 58.58 | 277.537 | 0 | 301 |  |  |  | 58.583 | 277.341 | 0 | 312 |  |  |  | 58.579 | 527 | 0.145 | 76 | 0
9.56 | 277.312 | 0 | 294 |  |  |  | 58.579 | 277.387 | 0 | 300 |  |  |  | 58.58 | 277.284 | 0 | 306 |  |  |  | 58.581 | 526.88 | 0.149 | 79 | 0
10.06 | 277.312 | 0 | 294 |  |  |  | 58.579 | 277.387 | 0 | 300 |  |  |  | 58.58 | 277.284 | 0 | 306 |  |  |  | 58.581 | 526.88 | 0.149 | 79 | 0
10.56 | 277.379 | 0 | 297 |  |  |  | 58.581 | 277.28 | 0 | 304 |  |  |  | 58.579 | 277.265 | 0 | 309 |  |  |  | 58.58 | 532.65 | 0.15 | 80 | 0
11.06 | 277.379 | 0 | 297 |  |  |  | 58.581 | 277.28 | 0 | 304 |  |  |  | 58.579 | 277.265 | 0 | 309 |  |  |  | 58.58 | 532.65 | 0.15 | 80 | 0
11.56 | 277.318 | 0 | 300 |  |  |  | 58.58 | 277.487 | 0 | 303 |  |  |  | 58.58 | 277.217 | 0 | 314 |  |  |  | 58.58 | 533.43 | 0.15 | 80 | 0
12.06 | 277.318 | 0 | 300 |  |  |  | 58.58 | 277.487 | 0 | 303 |  |  |  | 58.58 | 277.217 | 0 | 314 |  |  |  | 58.58 | 533.43 | 0.15 | 80 | 0
12.56 | 277.357 | 0 | 301 |  |  |  | 58.58 | 277.363 | 0 | 303 |  |  |  | 58.58 | 277.23 | 0 | 311 |  |  |  | 58.58 | 533.45 | 0.156 | 83 | 0
13.06 | 277.357 | 0 | 301 |  |  |  | 58.58 | 277.363 | 0 | 303 |  |  |  | 58.58 | 277.23 | 0 | 311 |  |  |  | 58.58 | 533.45 | 0.156 | 83 | 0
13.56 | 277.313 | 0 | 299 |  |  |  | 58.578 | 277.5 | 0 | 302 |  |  |  | 58.582 | 277.3 | 0 | 312 |  |  |  | 58.584 | 533.38 | 0.148 | 79 | 0
14.06 | 277.313 | 0 | 299 |  |  |  | 58.578 | 277.5 | 0 | 302 |  |  |  | 58.582 | 277.3 | 0 | 312 |  |  |  | 58.584 | 533.38 | 0.148 | 79 | 0
14.56 | 277.361 | 0 | 293 |  |  |  | 58.581 | 277.379 | 0 | 302 |  |  |  | 58.579 | 277.31 | 0 | 310 |  |  |  | 58.581 | 537.24 | 0.154 | 83 | 0
15.07 | 277.361 | 0 | 293 |  |  |  | 58.581 | 277.379 | 0 | 302 |  |  |  | 58.579 | 277.31 | 0 | 310 |  |  |  | 58.581 | 537.24 | 0.154 | 83 | 0
15.56 | 275.794 | 0 | 288 |  |  |  | 61.921 | 275.791 | 0 | 299 |  |  |  | 61.921 | 275.736 | 0 | 304 |  |  |  | 61.921 | 540 | 0.148 | 80 | 0
16.06 | 275.794 | 0 | 288 |  |  |  | 61.921 | 275.791 | 0 | 299 |  |  |  | 61.921 | 275.736 | 0 | 304 |  |  |  | 61.921 | 540 | 0.148 | 80 | 0
16.56 | 276.357 | 0 | 304 |  |  |  | 61.921 | 276.351 | 0 | 310 |  |  |  | 61.92 | 276.293 | 0 | 311 |  |  |  | 61.92 | 536.06 | 0.149 | 80 | 0
17.06 | 276.357 | 0 | 304 |  |  |  | 61.921 | 276.351 | 0 | 310 |  |  |  | 61.92 | 276.293 | 0 | 311 |  |  |  | 61.92 | 536.06 | 0.149 | 80 | 0
17.56 | 276.85 | 0 | 298 |  |  |  | 61.921 | 276.742 | 0 | 304 |  |  |  | 61.919 | 276.746 | 0 | 307 |  |  |  | 61.92 | 533.37 | 0.154 | 82 | 0
18.06 | 276.85 | 0 | 298 |  |  |  | 61.921 | 276.742 | 0 | 304 |  |  |  | 61.919 | 276.746 | 0 | 307 |  |  |  | 61.92 | 533.37 | 0.154 | 82 | 0
18.56 | 277.016 | 0 | 295 |  |  |  | 61.921 | 277.179 | 0 | 303 |  |  |  | 61.92 | 277.05 | 0 | 307 |  |  |  | 61.92 | 533.37 | 0.148 | 79 | 0
19.06 | 277.016 | 0 | 295 |  |  |  | 61.921 | 277.179 | 0 | 303 |  |  |  | 61.92 | 277.05 | 0 | 307 |  |  |  | 61.92 | 533.37 | 0.148 | 79 | 0
19.56 | 277.213 | 0 | 300 |  |  |  | 61.921 | 277.211 | 0 | 302 |  |  |  | 61.919 | 277.131 | 0 | 311 |  |  |  | 61.921 | 533.47 | 0.145 | 77 | 0
20.06 | 277.213 | 0 | 300 |  |  |  | 61.921 | 277.211 | 0 | 302 |  |  |  | 61.919 | 277.131 | 0 | 311 |  |  |  | 61.921 | 533.47 | 0.145 | 77 | 0
20.56 | 277.199 | 0 | 299 |  |  |  | 61.92 | 277.449 | 0 | 301 |  |  |  | 61.921 | 277.167 | 0 | 312 |  |  |  | 61.92 | 529.75 | 0.149 | 79 | 0
21.06 | 277.199 | 0 | 299 |  |  |  | 61.92 | 277.449 | 0 | 301 |  |  |  | 61.921 | 277.167 | 0 | 312 |  |  |  | 61.92 | 529.75 | 0.149 | 79 | 0
21.56 | 277.276 | 0 | 296 |  |  |  | 61.921 | 277.381 | 0 | 304 |  |  |  | 61.921 | 277.184 | 0 | 308 |  |  |  | 61.921 | 527 | 0.147 | 78 | 0
22.06 | 277.276 | 0 | 296 |  |  |  | 61.921 | 277.381 | 0 | 304 |  |  |  | 61.921 | 277.184 | 0 | 308 |  |  |  | 61.921 | 527 | 0.147 | 78 | 0
22.56 | 277.234 | 0 | 298 |  |  |  | 61.919 | 277.284 | 0 | 300 |  |  |  | 61.919 | 277.273 | 0 | 309 |  |  |  | 61.919 | 530.6 | 0.148 | 78 | 0
23.06 | 277.234 | 0 | 298 |  |  |  | 61.919 | 277.284 | 0 | 300 |  |  |  | 61.919 | 277.273 | 0 | 309 |  |  |  | 61.919 | 530.6 | 0.148 | 78 | 0
23.56 | 277.294 | 0 | 300 |  |  |  | 61.921 | 277.441 | 0 | 306 |  |  |  | 61.92 | 277.267 | 0 | 313 |  |  |  | 61.92 | 533.38 | 0.149 | 79 | 0
24.06 | 277.294 | 0 | 300 |  |  |  | 61.921 | 277.441 | 0 | 306 |  |  |  | 61.92 | 277.267 | 0 | 313 |  |  |  | 61.92 | 533.38 | 0.149 | 79 | 0
24.56 | 277.338 | 0 | 299 |  |  |  | 61.92 | 277.375 | 0 | 305 |  |  |  | 61.92 | 277.226 | 0 | 312 |  |  |  | 61.92 | 533.35 | 0.153 | 82 | 0
25.06 | 277.338 | 0 | 299 |  |  |  | 61.92 | 277.375 | 0 | 305 |  |  |  | 61.92 | 277.226 | 0 | 312 |  |  |  | 61.92 | 533.35 | 0.153 | 82 | 0
25.56 | 277.308 | 0 | 300 |  |  |  | 61.919 | 277.543 | 0 | 302 |  |  |  | 61.922 | 277.192 | 0 | 310 |  |  |  | 61.92 | 533.27 | 0.151 | 81 | 0
26.06 | 277.308 | 0 | 300 |  |  |  | 61.919 | 277.543 | 0 | 302 |  |  |  | 61.922 | 277.192 | 0 | 310 |  |  |  | 61.92 | 533.27 | 0.151 | 81 | 0
26.56 | 277.385 | 0 | 295 |  |  |  | 61.92 | 277.371 | 0 | 306 |  |  |  | 61.92 | 277.276 | 0 | 309 |  |  |  | 61.92 | 536.85 | 0.154 | 83 | 0
27.06 | 277.385 | 0 | 295 |  |  |  | 61.92 | 277.371 | 0 | 306 |  |  |  | 61.92 | 277.276 | 0 | 309 |  |  |  | 61.92 | 536.85 | 0.154 | 83 | 0
27.56 | 277.308 | 0 | 291 |  |  |  | 61.921 | 277.446 | 0 | 293 |  |  |  | 61.92 | 277.271 | 0 | 303 |  |  |  | 61.92 | 539.71 | 0.152 | 82 | 0
28.1 | 277.308 | 0 | 291 |  |  |  | 61.921 | 277.446 | 0 | 293 |  |  |  | 61.92 | 277.271 | 0 | 303 |  |  |  | 61.92 | 539.71 | 0.152 | 82 | 0
28.6 | 277.371 | 0 | 295 |  |  |  | 61.921 | 277.423 | 0 | 302 |  |  |  | 61.92 | 277.254 | 0 | 315 |  |  |  | 61.919 | 535.89 | 0.154 | 83 | 0
29.08 | 277.371 | 0 | 295 |  |  |  | 61.921 | 277.423 | 0 | 302 |  |  |  | 61.92 | 277.254 | 0 | 315 |  |  |  | 61.919 | 535.89 | 0.154 | 83 | 0
29.58 | 277.313 | 0 | 298 |  |  |  | 61.92 | 277.274 | 0 | 301 |  |  |  | 61.921 | 277.192 | 0 | 311 |  |  |  | 61.921 | 533.34 | 0.154 | 82 | 0
30.06 | 277.313 | 0 | 298 |  |  |  | 61.92 | 277.274 | 0 | 301 |  |  |  | 61.921 | 277.192 | 0 | 311 |  |  |  | 61.921 | 533.34 | 0.154 | 82 | 0
30.56 | 277.35 | 0 | 296 |  |  |  | 61.921 | 277.502 | 0 | 302 |  |  |  | 61.92 | 277.167 | 0 | 310 |  |  |  | 61.92 | 533.37 | 0.151 | 80 | 0
31.1 | 277.35 | 0 | 296 |  |  |  | 61.921 | 277.502 | 0 | 302 |  |  |  | 61.92 | 277.167 | 0 | 310 |  |  |  | 61.92 | 533.37 | 0.151 | 80 | 0
31.6 | 277.278 | 0 | 301 |  |  |  | 61.917 | 277.379 | 0 | 305 |  |  |  | 61.92 | 277.259 | 0 | 307 |  |  |  | 61.921 | 533.43 | 0.152 | 81 | 0
32.09 | 277.35 | 0 | 297 |  |  |  | 61.921 | 277.516 | 0 | 305 |  |  |  | 61.923 | 277.257 | 0 | 314 |  |  |  | 61.92 | 529.93 | 0.152 | 81 | 0
32.59 | 277.35 | 0 | 297 |  |  |  | 61.921 | 277.516 | 0 | 305 |  |  |  | 61.923 | 277.257 | 0 | 314 |  |  |  | 61.92 | 529.93 | 0.152 | 81 | 0
33.07 | 277.408 | 0 | 296 |  |  |  | 61.92 | 277.416 | 0 | 304 |  |  |  | 61.919 | 277.216 | 0 | 306 |  |  |  | 61.921 | 526.91 | 0.153 | 81 | 0
33.57 | 277.408 | 0 | 296 |  |  |  | 61.92 | 277.416 | 0 | 304 |  |  |  | 61.919 | 277.216 | 0 | 306 |  |  |  | 61.921 | 526.91 | 0.153 | 81 | 0
34.06 | 277.354 | 0 | 292 |  |  |  | 61.92 | 277.292 | 0 | 302 |  |  |  | 61.92 | 277.152 | 0 | 308 |  |  |  | 61.92 | 530.57 | 0.152 | 80 | 0
34.56 | 277.354 | 0 | 292 |  |  |  | 61.92 | 277.292 | 0 | 302 |  |  |  | 61.92 | 277.152 | 0 | 308 |  |  |  | 61.92 | 530.57 | 0.152 | 80 | 0
35.06 | 277.423 | 0 | 299 |  |  |  | 61.921 | 277.401 | 0 | 301 |  |  |  | 61.92 | 277.254 | 0 | 312 |  |  |  | 61.921 | 533.34 | 0.151 | 81 | 0
35.56 | 277.423 | 0 | 299 |  |  |  | 61.921 | 277.401 | 0 | 301 |  |  |  | 61.92 | 277.254 | 0 | 312 |  |  |  | 61.921 | 533.34 | 0.151 | 81 | 0
36.06 | 277.343 | 0 | 300 |  |  |  | 61.92 | 277.284 | 0 | 302 |  |  |  | 61.92 | 277.243 | 0 | 310 |  |  |  | 61.921 | 533.39 | 0.151 | 80 | 0
36.56 | 277.343 | 0 | 300 |  |  |  | 61.92 | 277.284 | 0 | 302 |  |  |  | 61.92 | 277.243 | 0 | 310 |  |  |  | 61.921 | 533.39 | 0.151 | 80 | 0
37.06 | 277.392 | 0 | 296 |  |  |  | 61.922 | 277.478 | 0 | 301 |  |  |  | 61.923 | 277.245 | 0 | 316 |  |  |  | 61.921 | 533.25 | 0.149 | 79 | 0
37.56 | 277.392 | 0 | 296 |  |  |  | 61.922 | 277.478 | 0 | 301 |  |  |  | 61.923 | 277.245 | 0 | 316 |  |  |  | 61.921 | 533.25 | 0.149 | 79 | 0
38.06 | 277.331 | 0 | 293 |  |  |  | 61.919 | 277.326 | 0 | 303 |  |  |  | 61.918 | 277.185 | 0 | 311 |  |  |  | 61.921 | 536.73 | 0.148 | 79 | 0
38.56 | 277.331 | 0 | 293 |  |  |  | 61.919 | 277.326 | 0 | 303 |  |  |  | 61.918 | 277.185 | 0 | 311 |  |  |  | 61.921 | 536.73 | 0.148 | 79 | 0
39.06 | 277.393 | 0 | 292 |  |  |  | 61.921 | 277.431 | 0 | 298 |  |  |  | 61.92 | 277.284 | 0 | 303 |  |  |  | 61.921 | 539.83 | 0.152 | 82 | 0
39.56 | 277.393 | 0 | 292 |  |  |  | 61.921 | 277.431 | 0 | 298 |  |  |  | 61.92 | 277.284 | 0 | 303 |  |  |  | 61.921 | 539.83 | 0.152 | 82 | 0
40.06 | 277.293 | 0 | 301 |  |  |  | 61.917 | 277.387 | 0 | 307 |  |  |  | 61.92 | 277.246 | 0 | 314 |  |  |  | 61.921 | 536.29 | 0.148 | 80 | 0
40.56 | 277.293 | 0 | 301 |  |  |  | 61.917 | 277.387 | 0 | 307 |  |  |  | 61.92 | 277.246 | 0 | 314 |  |  |  | 61.921 | 536.29 | 0.148 | 80 | 0
41.06 | 277.377 | 0 | 300 |  |  |  | 61.921 | 277.245 | 0 | 306 |  |  |  | 61.919 | 277.238 | 0 | 307 |  |  |  | 61.92 | 533.35 | 0.149 | 79 | 0
41.56 | 277.377 | 0 | 300 |  |  |  | 61.921 | 277.245 | 0 | 306 |  |  |  | 61.919 | 277.238 | 0 | 307 |  |  |  | 61.92 | 533.35 | 0.149 | 79 | 0
42.06 | 277.442 | 0 | 300 |  |  |  | 61.921 | 277.461 | 0 | 304 |  |  |  | 61.92 | 277.219 | 0 | 313 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 0
42.56 | 277.442 | 0 | 300 |  |  |  | 61.921 | 277.461 | 0 | 304 |  |  |  | 61.92 | 277.219 | 0 | 313 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 0
43.06 | 277.346 | 0 | 300 |  |  |  | 61.921 | 277.313 | 0 | 304 |  |  |  | 61.921 | 277.308 | 0 | 309 |  |  |  | 61.921 | 533.29 | 0.151 | 81 | 0
43.56 | 277.346 | 0 | 300 |  |  |  | 61.921 | 277.313 | 0 | 304 |  |  |  | 61.921 | 277.308 | 0 | 309 |  |  |  | 61.921 | 533.29 | 0.151 | 81 | 0
44.06 | 277.408 | 0 | 301 |  |  |  | 61.921 | 277.443 | 0 | 301 |  |  |  | 61.923 | 277.291 | 0 | 311 |  |  |  | 61.921 | 529.93 | 0.154 | 82 | 0
44.56 | 277.408 | 0 | 301 |  |  |  | 61.921 | 277.443 | 0 | 301 |  |  |  | 61.923 | 277.291 | 0 | 311 |  |  |  | 61.921 | 529.93 | 0.154 | 82 | 0
45.06 | 277.338 | 0 | 295 |  |  |  | 61.92 | 277.331 | 0 | 300 |  |  |  | 61.92 | 277.264 | 0 | 308 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 0
45.56 | 277.338 | 0 | 295 |  |  |  | 61.92 | 277.331 | 0 | 300 |  |  |  | 61.92 | 277.264 | 0 | 308 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 0
46.06 | 277.384 | 0 | 293 |  |  |  | 61.921 | 277.254 | 0 | 297 |  |  |  | 61.919 | 277.259 | 0 | 304 |  |  |  | 61.92 | 530.38 | 0.157 | 83 | 0
46.56 | 277.384 | 0 | 293 |  |  |  | 61.921 | 277.254 | 0 | 297 |  |  |  | 61.919 | 277.259 | 0 | 304 |  |  |  | 61.92 | 530.38 | 0.157 | 83 | 0
47.06 | 277.332 | 0 | 297 |  |  |  | 61.92 | 277.378 | 0 | 302 |  |  |  | 61.92 | 277.232 | 0 | 307 |  |  |  | 61.92 | 533.25 | 0.151 | 80 | 0
47.56 | 277.332 | 0 | 297 |  |  |  | 61.92 | 277.378 | 0 | 302 |  |  |  | 61.92 | 277.232 | 0 | 307 |  |  |  | 61.92 | 533.25 | 0.151 | 80 | 0
48.06 | 277.389 | 0 | 299 |  |  |  | 61.92 | 277.292 | 0 | 303 |  |  |  | 61.92 | 277.321 | 0 | 311 |  |  |  | 61.92 | 533.28 | 0.153 | 82 | 0
48.56 | 277.389 | 0 | 299 |  |  |  | 61.92 | 277.292 | 0 | 303 |  |  |  | 61.92 | 277.321 | 0 | 311 |  |  |  | 61.92 | 533.28 | 0.153 | 82 | 0
49.06 | 277.298 | 0 | 300 |  |  |  | 61.916 | 277.456 | 0 | 305 |  |  |  | 61.922 | 277.274 | 0 | 311 |  |  |  | 61.92 | 533.46 | 0.151 | 81 | 0
49.56 | 277.298 | 0 | 300 |  |  |  | 61.916 | 277.456 | 0 | 305 |  |  |  | 61.922 | 277.274 | 0 | 311 |  |  |  | 61.92 | 533.46 | 0.151 | 81 | 0
50.06 | 277.364 | 0 | 299 |  |  |  | 61.92 | 277.321 | 0 | 300 |  |  |  | 61.919 | 277.245 | 0 | 313 |  |  |  | 61.921 | 536.54 | 0.15 | 81 | 0
50.56 | 277.364 | 0 | 299 |  |  |  | 61.92 | 277.321 | 0 | 300 |  |  |  | 61.919 | 277.245 | 0 | 313 |  |  |  | 61.921 | 536.54 | 0.15 | 81 | 0
51.06 | 277.434 | 0 | 287 |  |  |  | 61.921 | 277.435 | 0 | 296 |  |  |  | 61.921 | 277.23 | 0 | 305 |  |  |  | 61.92 | 539.64 | 0.155 | 84 | 0
51.56 | 277.434 | 0 | 287 |  |  |  | 61.921 | 277.435 | 0 | 296 |  |  |  | 61.921 | 277.23 | 0 | 305 |  |  |  | 61.92 | 539.64 | 0.155 | 84 | 0
52.06 | 277.335 | 0 | 298 |  |  |  | 61.921 | 277.404 | 0 | 303 |  |  |  | 61.919 | 277.325 | 0 | 311 |  |  |  | 61.92 | 536.24 | 0.154 | 82 | 0
52.56 | 277.335 | 0 | 298 |  |  |  | 61.921 | 277.404 | 0 | 303 |  |  |  | 61.919 | 277.325 | 0 | 311 |  |  |  | 61.92 | 536.24 | 0.154 | 82 | 0
53.06 | 277.388 | 0 | 300 |  |  |  | 61.921 | 277.277 | 0 | 302 |  |  |  | 61.921 | 277.285 | 0 | 312 |  |  |  | 61.92 | 533.41 | 0.155 | 83 | 0
53.56 | 277.388 | 0 | 300 |  |  |  | 61.921 | 277.277 | 0 | 302 |  |  |  | 61.921 | 277.285 | 0 | 312 |  |  |  | 61.92 | 533.41 | 0.155 | 83 | 0
54.06 | 277.347 | 0 | 298 |  |  |  | 61.919 | 277.44 | 0 | 302 |  |  |  | 61.919 | 277.243 | 0 | 309 |  |  |  | 61.92 | 533.38 | 0.156 | 83 | 0
54.56 | 277.347 | 0 | 298 |  |  |  | 61.919 | 277.44 | 0 | 302 |  |  |  | 61.919 | 277.243 | 0 | 309 |  |  |  | 61.92 | 533.38 | 0.156 | 83 | 0
55.06 | 277.404 | 0 | 300 |  |  |  | 61.921 | 277.355 | 0 | 302 |  |  |  | 61.92 | 277.232 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.149 | 79 | 0
55.56 | 277.404 | 0 | 300 |  |  |  | 61.921 | 277.355 | 0 | 302 |  |  |  | 61.92 | 277.232 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.149 | 79 | 0
56.06 | 277.332 | 0 | 297 |  |  |  | 61.921 | 277.499 | 0 | 303 |  |  |  | 61.922 | 277.317 | 0 | 313 |  |  |  | 61.924 | 530.1 | 0.154 | 81 | 0
56.56 | 277.332 | 0 | 297 |  |  |  | 61.921 | 277.499 | 0 | 303 |  |  |  | 61.922 | 277.317 | 0 | 313 |  |  |  | 61.924 | 530.1 | 0.154 | 81 | 0
57.06 | 277.41 | 0 | 294 |  |  |  | 61.92 | 277.387 | 0 | 300 |  |  |  | 61.92 | 277.308 | 0 | 309 |  |  |  | 61.92 | 526.86 | 0.146 | 77 | 0
57.56 | 277.41 | 0 | 294 |  |  |  | 61.92 | 277.387 | 0 | 300 |  |  |  | 61.92 | 277.308 | 0 | 309 |  |  |  | 61.92 | 526.86 | 0.146 | 77 | 0
58.06 | 277.28 | 0 | 297 |  |  |  | 61.916 | 277.264 | 0 | 299 |  |  |  | 61.919 | 277.255 | 0 | 309 |  |  |  | 61.919 | 530.43 | 0.155 | 82 | 0
58.6 | 277.28 | 0 | 297 |  |  |  | 61.916 | 277.264 | 0 | 299 |  |  |  | 61.919 | 277.255 | 0 | 309 |  |  |  | 61.919 | 530.43 | 0.155 | 82 | 0
59.1 | 277.341 | 0 | 292 |  |  |  | 61.92 | 277.458 | 0 | 299 |  |  |  | 61.921 | 277.226 | 0 | 311 |  |  |  | 61.92 | 533.4 | 0.156 | 83 | 0
59.58 | 277.341 | 0 | 292 |  |  |  | 61.92 | 277.458 | 0 | 299 |  |  |  | 61.921 | 277.226 | 0 | 311 |  |  |  | 61.92 | 533.4 | 0.156 | 83 | 0
60.08 | 277.408 | 0 | 302 |  |  |  | 61.921 | 277.292 | 0 | 299 |  |  |  | 61.92 | 277.209 | 0 | 311 |  |  |  | 61.919 | 533.44 | 0.155 | 83 | 0
60.56 | 277.408 | 0 | 302 |  |  |  | 61.921 | 277.292 | 0 | 299 |  |  |  | 61.92 | 277.209 | 0 | 311 |  |  |  | 61.919 | 533.44 | 0.155 | 83 | 0
61.06 | 277.311 | 0 | 295 |  |  |  | 61.921 | 277.527 | 0 | 305 |  |  |  | 61.921 | 277.312 | 0 | 311 |  |  |  | 61.92 | 533.37 | 0.152 | 81 | 0
61.6 | 277.375 | 0 | 297 |  |  |  | 61.92 | 277.399 | 0 | 302 |  |  |  | 61.921 | 277.288 | 0 | 307 |  |  |  | 61.92 | 536.5 | 0.154 | 82 | 0
62.1 | 277.375 | 0 | 297 |  |  |  | 61.92 | 277.399 | 0 | 302 |  |  |  | 61.921 | 277.288 | 0 | 307 |  |  |  | 61.92 | 536.5 | 0.154 | 82 | 0
62.59 | 277.326 | 0 | 291 |  |  |  | 61.921 | 277.512 | 0 | 294 |  |  |  | 61.922 | 277.244 | 0 | 304 |  |  |  | 61.921 | 539.75 | 0.153 | 83 | 0
63.09 | 277.326 | 0 | 291 |  |  |  | 61.921 | 277.512 | 0 | 294 |  |  |  | 61.922 | 277.244 | 0 | 304 |  |  |  | 61.921 | 539.75 | 0.153 | 83 | 0
63.57 | 277.372 | 0 | 300 |  |  |  | 61.92 | 277.439 | 0 | 304 |  |  |  | 61.92 | 277.228 | 0 | 312 |  |  |  | 61.92 | 536.41 | 0.15 | 80 | 0
64.07 | 277.372 | 0 | 300 |  |  |  | 61.92 | 277.439 | 0 | 304 |  |  |  | 61.92 | 277.228 | 0 | 312 |  |  |  | 61.92 | 536.41 | 0.15 | 80 | 0
64.56 | 277.294 | 0 | 299 |  |  |  | 61.921 | 277.32 | 0 | 302 |  |  |  | 61.92 | 277.314 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 0
65.06 | 277.294 | 0 | 299 |  |  |  | 61.921 | 277.32 | 0 | 302 |  |  |  | 61.92 | 277.314 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 0
65.56 | 277.369 | 0 | 297 |  |  |  | 61.92 | 277.486 | 0 | 301 |  |  |  | 61.92 | 277.302 | 0 | 312 |  |  |  | 61.92 | 533.34 | 0.152 | 81 | 0
66.06 | 277.369 | 0 | 297 |  |  |  | 61.92 | 277.486 | 0 | 301 |  |  |  | 61.92 | 277.302 | 0 | 312 |  |  |  | 61.92 | 533.34 | 0.152 | 81 | 0
66.56 | 277.281 | 0 | 298 |  |  |  | 61.918 | 277.323 | 0 | 308 |  |  |  | 61.919 | 277.26 | 0 | 313 |  |  |  | 61.92 | 533.39 | 0.152 | 81 | 0
67.06 | 277.281 | 0 | 298 |  |  |  | 61.918 | 277.323 | 0 | 308 |  |  |  | 61.919 | 277.26 | 0 | 313 |  |  |  | 61.92 | 533.39 | 0.152 | 81 | 0
67.56 | 277.326 | 0 | 298 |  |  |  | 61.921 | 277.522 | 0 | 305 |  |  |  | 61.923 | 277.226 | 0 | 312 |  |  |  | 61.921 | 530.25 | 0.15 | 79 | 0
68.06 | 277.326 | 0 | 298 |  |  |  | 61.921 | 277.522 | 0 | 305 |  |  |  | 61.923 | 277.226 | 0 | 312 |  |  |  | 61.921 | 530.25 | 0.15 | 79 | 0
68.56 | 277.394 | 0 | 294 |  |  |  | 61.921 | 277.397 | 0 | 303 |  |  |  | 61.919 | 277.304 | 0 | 306 |  |  |  | 61.919 | 526.91 | 0.152 | 80 | 0
69.06 | 277.394 | 0 | 294 |  |  |  | 61.921 | 277.397 | 0 | 303 |  |  |  | 61.919 | 277.304 | 0 | 306 |  |  |  | 61.919 | 526.91 | 0.152 | 80 | 0
69.56 | 277.32 | 0 | 291 |  |  |  | 61.921 | 277.297 | 0 | 300 |  |  |  | 61.921 | 277.302 | 0 | 308 |  |  |  | 61.921 | 530.35 | 0.149 | 79 | 0
70.06 | 277.32 | 0 | 291 |  |  |  | 61.921 | 277.297 | 0 | 300 |  |  |  | 61.921 | 277.302 | 0 | 308 |  |  |  | 61.921 | 530.35 | 0.149 | 79 | 0
70.56 | 277.37 | 0 | 295 |  |  |  | 61.92 | 277.449 | 0 | 299 |  |  |  | 61.92 | 277.272 | 0 | 313 |  |  |  | 61.92 | 533.32 | 0.155 | 83 | 0
71.06 | 277.37 | 0 | 295 |  |  |  | 61.92 | 277.449 | 0 | 299 |  |  |  | 61.92 | 277.272 | 0 | 313 |  |  |  | 61.92 | 533.32 | 0.155 | 83 | 0
71.56 | 277.329 | 0 | 298 |  |  |  | 61.92 | 277.325 | 0 | 301 |  |  |  | 61.919 | 277.226 | 0 | 310 |  |  |  | 61.921 | 533.3 | 0.152 | 81 | 0
72.06 | 277.329 | 0 | 298 |  |  |  | 61.92 | 277.325 | 0 | 301 |  |  |  | 61.919 | 277.226 | 0 | 310 |  |  |  | 61.921 | 533.3 | 0.152 | 81 | 0
72.56 | 277.372 | 0 | 298 |  |  |  | 61.921 | 277.484 | 0 | 305 |  |  |  | 61.921 | 277.208 | 0 | 309 |  |  |  | 61.92 | 533.49 | 0.154 | 82 | 0
73.06 | 277.372 | 0 | 298 |  |  |  | 61.921 | 277.484 | 0 | 305 |  |  |  | 61.921 | 277.208 | 0 | 309 |  |  |  | 61.92 | 533.49 | 0.154 | 82 | 0
73.56 | 277.313 | 0 | 299 |  |  |  | 61.921 | 277.345 | 0 | 300 |  |  |  | 61.92 | 277.299 | 0 | 305 |  |  |  | 61.921 | 536.32 | 0.151 | 81 | 0
74.06 | 277.313 | 0 | 299 |  |  |  | 61.921 | 277.345 | 0 | 300 |  |  |  | 61.92 | 277.299 | 0 | 305 |  |  |  | 61.921 | 536.32 | 0.151 | 81 | 0
74.56 | 277.392 | 0 | 290 |  |  |  | 61.92 | 277.464 | 0 | 299 |  |  |  | 61.921 | 277.29 | 0 | 300 |  |  |  | 61.919 | 539.72 | 0.155 | 84 | 0
75.06 | 277.392 | 0 | 290 |  |  |  | 61.92 | 277.464 | 0 | 299 |  |  |  | 61.921 | 277.29 | 0 | 300 |  |  |  | 61.919 | 539.72 | 0.155 | 84 | 0
75.56 | 277.305 | 0 | 298 |  |  |  | 61.918 | 277.394 | 0 | 309 |  |  |  | 61.919 | 277.235 | 0 | 313 |  |  |  | 61.92 | 536.48 | 0.157 | 84 | 0
76.06 | 277.305 | 0 | 298 |  |  |  | 61.918 | 277.394 | 0 | 309 |  |  |  | 61.919 | 277.235 | 0 | 313 |  |  |  | 61.92 | 536.48 | 0.157 | 84 | 0
76.56 | 277.358 | 0 | 296 |  |  |  | 61.921 | 277.3 | 0 | 303 |  |  |  | 61.92 | 277.197 | 0 | 306 |  |  |  | 61.92 | 533.37 | 0.153 | 82 | 0
77.06 | 277.358 | 0 | 296 |  |  |  | 61.921 | 277.3 | 0 | 303 |  |  |  | 61.92 | 277.197 | 0 | 306 |  |  |  | 61.92 | 533.37 | 0.153 | 82 | 0
77.56 | 277.426 | 0 | 301 |  |  |  | 61.92 | 277.446 | 0 | 303 |  |  |  | 61.919 | 277.293 | 0 | 312 |  |  |  | 61.92 | 533.3 | 0.151 | 81 | 0
78.06 | 277.426 | 0 | 301 |  |  |  | 61.92 | 277.446 | 0 | 303 |  |  |  | 61.919 | 277.293 | 0 | 312 |  |  |  | 61.92 | 533.3 | 0.151 | 81 | 0
78.56 | 277.369 | 0 | 293 |  |  |  | 61.92 | 277.32 | 0 | 300 |  |  |  | 61.919 | 277.288 | 0 | 309 |  |  |  | 61.92 | 533.24 | 0.158 | 84 | 0
79.06 | 277.369 | 0 | 293 |  |  |  | 61.92 | 277.32 | 0 | 300 |  |  |  | 61.919 | 277.288 | 0 | 309 |  |  |  | 61.92 | 533.24 | 0.158 | 84 | 0
79.56 | 277.406 | 0 | 298 |  |  |  | 61.919 | 277.498 | 0 | 301 |  |  |  | 61.923 | 277.267 | 0 | 313 |  |  |  | 61.92 | 530.27 | 0.154 | 81 | 0
80.06 | 277.406 | 0 | 298 |  |  |  | 61.919 | 277.498 | 0 | 301 |  |  |  | 61.923 | 277.267 | 0 | 313 |  |  |  | 61.92 | 530.27 | 0.154 | 81 | 0
80.56 | 277.353 | 0 | 296 |  |  |  | 61.921 | 277.359 | 0 | 300 |  |  |  | 61.919 | 277.212 | 0 | 306 |  |  |  | 61.921 | 526.87 | 0.154 | 81 | 0
81.06 | 277.353 | 0 | 296 |  |  |  | 61.921 | 277.359 | 0 | 300 |  |  |  | 61.919 | 277.212 | 0 | 306 |  |  |  | 61.921 | 526.87 | 0.154 | 81 | 0
81.56 | 277.403 | 0 | 293 |  |  |  | 61.921 | 277.248 | 0 | 297 |  |  |  | 61.919 | 277.312 | 0 | 308 |  |  |  | 61.92 | 530.3 | 0.156 | 83 | 0
82.06 | 277.403 | 0 | 293 |  |  |  | 61.921 | 277.248 | 0 | 297 |  |  |  | 61.919 | 277.312 | 0 | 308 |  |  |  | 61.92 | 530.3 | 0.156 | 83 | 0
82.56 | 277.308 | 0 | 298 |  |  |  | 61.921 | 277.385 | 0 | 300 |  |  |  | 61.921 | 277.285 | 0 | 308 |  |  |  | 61.921 | 533.28 | 0.153 | 81 | 0
83.06 | 277.308 | 0 | 298 |  |  |  | 61.921 | 277.385 | 0 | 300 |  |  |  | 61.921 | 277.285 | 0 | 308 |  |  |  | 61.921 | 533.28 | 0.153 | 81 | 0
83.56 | 277.383 | 0 | 299 |  |  |  | 61.921 | 277.268 | 0 | 305 |  |  |  | 61.92 | 277.279 | 0 | 310 |  |  |  | 61.921 | 533.3 | 0.151 | 80 | 0
84.06 | 277.383 | 0 | 299 |  |  |  | 61.921 | 277.268 | 0 | 305 |  |  |  | 61.92 | 277.279 | 0 | 310 |  |  |  | 61.921 | 533.3 | 0.151 | 80 | 0
84.56 | 277.313 | 0 | 295 |  |  |  | 61.917 | 277.431 | 0 | 300 |  |  |  | 61.92 | 277.24 | 0 | 313 |  |  |  | 61.922 | 533.3 | 0.147 | 79 | 0
85.06 | 277.313 | 0 | 295 |  |  |  | 61.917 | 277.431 | 0 | 300 |  |  |  | 61.92 | 277.24 | 0 | 313 |  |  |  | 61.922 | 533.3 | 0.147 | 79 | 0
85.56 | 277.368 | 0 | 299 |  |  |  | 61.92 | 277.342 | 0 | 304 |  |  |  | 61.918 | 277.184 | 0 | 307 |  |  |  | 61.92 | 536.3 | 0.146 | 78 | 0
86.06 | 277.368 | 0 | 299 |  |  |  | 61.92 | 277.342 | 0 | 304 |  |  |  | 61.918 | 277.184 | 0 | 307 |  |  |  | 61.92 | 536.3 | 0.146 | 78 | 0
86.56 | 277.422 | 0 | 287 |  |  |  | 61.921 | 277.438 | 0 | 298 |  |  |  | 61.921 | 277.282 | 0 | 302 |  |  |  | 61.921 | 539.78 | 0.147 | 79 | 0
87.06 | 277.422 | 0 | 287 |  |  |  | 61.921 | 277.438 | 0 | 298 |  |  |  | 61.921 | 277.282 | 0 | 302 |  |  |  | 61.921 | 539.78 | 0.147 | 79 | 0
87.56 | 277.376 | 0 | 300 |  |  |  | 61.921 | 277.367 | 0 | 307 |  |  |  | 61.919 | 277.278 | 0 | 312 |  |  |  | 61.92 | 536.46 | 0.148 | 80 | 0
88.06 | 277.376 | 0 | 300 |  |  |  | 61.921 | 277.367 | 0 | 307 |  |  |  | 61.919 | 277.278 | 0 | 312 |  |  |  | 61.92 | 536.46 | 0.148 | 80 | 0
88.56 | 277.419 | 0 | 300 |  |  |  | 61.92 | 277.225 | 0 | 302 |  |  |  | 61.92 | 277.266 | 0 | 310 |  |  |  | 61.921 | 533.31 | 0.148 | 79 | 0
89.06 | 277.419 | 0 | 300 |  |  |  | 61.92 | 277.225 | 0 | 302 |  |  |  | 61.92 | 277.266 | 0 | 310 |  |  |  | 61.921 | 533.31 | 0.148 | 79 | 0
89.56 | 277.342 | 0 | 295 |  |  |  | 61.92 | 277.429 | 0 | 302 |  |  |  | 61.92 | 277.22 | 0 | 310 |  |  |  | 61.919 | 533.29 | 0.147 | 78 | 0
90.06 | 277.342 | 0 | 295 |  |  |  | 61.92 | 277.429 | 0 | 302 |  |  |  | 61.92 | 277.22 | 0 | 310 |  |  |  | 61.919 | 533.29 | 0.147 | 78 | 0
90.56 | 277.42 | 0 | 295 |  |  |  | 61.921 | 277.304 | 0 | 301 |  |  |  | 61.92 | 277.311 | 0 | 309 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 0
91.1 | 277.42 | 0 | 295 |  |  |  | 61.921 | 277.304 | 0 | 301 |  |  |  | 61.92 | 277.311 | 0 | 309 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 0
91.6 | 277.305 | 0 | 298 |  |  |  | 61.921 | 277.479 | 0 | 303 |  |  |  | 61.924 | 277.273 | 0 | 309 |  |  |  | 61.921 | 530.29 | 0.149 | 79 | 0
92.08 | 277.305 | 0 | 298 |  |  |  | 61.921 | 277.479 | 0 | 303 |  |  |  | 61.924 | 277.273 | 0 | 309 |  |  |  | 61.921 | 530.29 | 0.149 | 79 | 0
92.58 | 277.384 | 0 | 292 |  |  |  | 61.92 | 277.336 | 0 | 299 |  |  |  | 61.918 | 277.268 | 0 | 308 |  |  |  | 61.92 | 526.92 | 0.148 | 78 | 0
93.07 | 277.384 | 0 | 292 |  |  |  | 61.92 | 277.336 | 0 | 299 |  |  |  | 61.918 | 277.268 | 0 | 308 |  |  |  | 61.92 | 526.92 | 0.148 | 78 | 0
93.57 | 277.312 | 0 | 295 |  |  |  | 61.917 | 277.318 | 0 | 298 |  |  |  | 61.92 | 277.235 | 0 | 304 |  |  |  | 61.921 | 530.25 | 0.151 | 80 | 0
94.1 | 277.312 | 0 | 295 |  |  |  | 61.917 | 277.318 | 0 | 298 |  |  |  | 61.92 | 277.235 | 0 | 304 |  |  |  | 61.921 | 530.25 | 0.151 | 80 | 0
94.6 | 277.365 | 0 | 297 |  |  |  | 61.921 | 277.43 | 0 | 300 |  |  |  | 61.921 | 277.33 | 0 | 312 |  |  |  | 61.921 | 533.34 | 0.148 | 79 | 0
95.09 | 277.423 | 0 | 301 |  |  |  | 61.92 | 277.311 | 0 | 307 |  |  |  | 61.92 | 277.28 | 0 | 313 |  |  |  | 61.921 | 533.44 | 0.147 | 79 | 0
95.59 | 277.423 | 0 | 301 |  |  |  | 61.92 | 277.311 | 0 | 307 |  |  |  | 61.92 | 277.28 | 0 | 313 |  |  |  | 61.921 | 533.44 | 0.147 | 79 | 0
96.07 | 277.378 | 0 | 295 |  |  |  | 61.92 | 277.494 | 0 | 299 |  |  |  | 61.919 | 277.255 | 0 | 308 |  |  |  | 61.92 | 533.3 | 0.146 | 78 | 0
96.57 | 277.378 | 0 | 295 |  |  |  | 61.92 | 277.494 | 0 | 299 |  |  |  | 61.919 | 277.255 | 0 | 308 |  |  |  | 61.92 | 533.3 | 0.146 | 78 | 0
97.07 | 277.42 | 0 | 296 |  |  |  | 61.92 | 277.329 | 0 | 302 |  |  |  | 61.92 | 277.246 | 0 | 312 |  |  |  | 61.92 | 536.49 | 0.15 | 80 | 0
97.57 | 277.42 | 0 | 296 |  |  |  | 61.92 | 277.329 | 0 | 302 |  |  |  | 61.92 | 277.246 | 0 | 312 |  |  |  | 61.92 | 536.49 | 0.15 | 80 | 0
98.06 | 277.318 | 0 | 290 |  |  |  | 61.921 | 277.512 | 0 | 294 |  |  |  | 61.923 | 277.242 | 0 | 305 |  |  |  | 61.921 | 539.84 | 0.152 | 82 | 0
98.56 | 277.318 | 0 | 290 |  |  |  | 61.921 | 277.512 | 0 | 294 |  |  |  | 61.923 | 277.242 | 0 | 305 |  |  |  | 61.921 | 539.84 | 0.152 | 82 | 0
99.06 | 277.387 | 0 | 299 |  |  |  | 61.921 | 277.399 | 0 | 302 |  |  |  | 61.921 | 277.314 | 0 | 310 |  |  |  | 61.92 | 536.52 | 0.146 | 78 | 0
99.56 | 277.387 | 0 | 299 |  |  |  | 61.921 | 277.399 | 0 | 302 |  |  |  | 61.921 | 277.314 | 0 | 310 |  |  |  | 61.92 | 536.52 | 0.146 | 78 | 0
100.06 | 277.275 | 0 | 297 |  |  |  | 61.92 | 277.303 | 0 | 301 |  |  |  | 61.919 | 277.26 | 0 | 313 |  |  |  | 61.92 | 533.36 | 0.149 | 79 | 0
100.56 | 277.275 | 0 | 297 |  |  |  | 61.92 | 277.303 | 0 | 301 |  |  |  | 61.919 | 277.26 | 0 | 313 |  |  |  | 61.92 | 533.36 | 0.149 | 79 | 0
101.06 | 277.345 | 0 | 296 |  |  |  | 61.92 | 277.443 | 0 | 304 |  |  |  | 61.92 | 277.241 | 0 | 309 |  |  |  | 61.921 | 533.36 | 0.149 | 79 | 0
101.56 | 277.345 | 0 | 296 |  |  |  | 61.92 | 277.443 | 0 | 304 |  |  |  | 61.92 | 277.241 | 0 | 309 |  |  |  | 61.921 | 533.36 | 0.149 | 79 | 0
102.06 | 277.303 | 0 | 298 |  |  |  | 61.917 | 277.319 | 0 | 304 |  |  |  | 61.92 | 277.227 | 0 | 312 |  |  |  | 61.919 | 533.42 | 0.15 | 80 | 0
102.56 | 277.303 | 0 | 298 |  |  |  | 61.917 | 277.319 | 0 | 304 |  |  |  | 61.92 | 277.227 | 0 | 312 |  |  |  | 61.919 | 533.42 | 0.15 | 80 | 0
103.06 | 277.344 | 0 | 298 |  |  |  | 61.92 | 277.516 | 0 | 306 |  |  |  | 61.923 | 277.322 | 0 | 311 |  |  |  | 61.921 | 530.39 | 0.148 | 78 | 0
103.56 | 277.344 | 0 | 298 |  |  |  | 61.92 | 277.516 | 0 | 306 |  |  |  | 61.923 | 277.322 | 0 | 311 |  |  |  | 61.921 | 530.39 | 0.148 | 78 | 0
104.06 | 277.374 | 0 | 297 |  |  |  | 61.921 | 277.361 | 0 | 303 |  |  |  | 61.921 | 277.276 | 0 | 309 |  |  |  | 61.92 | 527.03 | 0.152 | 80 | 0
104.56 | 277.374 | 0 | 297 |  |  |  | 61.921 | 277.361 | 0 | 303 |  |  |  | 61.921 | 277.276 | 0 | 309 |  |  |  | 61.92 | 527.03 | 0.152 | 80 | 0
105.06 | 277.357 | 0 | 297 |  |  |  | 61.92 | 277.397 | 0 | 298 |  |  |  | 61.919 | 277.241 | 0 | 309 |  |  |  | 61.921 | 530.16 | 0.152 | 81 | 0
105.56 | 277.357 | 0 | 297 |  |  |  | 61.92 | 277.397 | 0 | 298 |  |  |  | 61.919 | 277.241 | 0 | 309 |  |  |  | 61.921 | 530.16 | 0.152 | 81 | 0
106.06 | 277.395 | 0 | 297 |  |  |  | 61.921 | 277.413 | 0 | 303 |  |  |  | 61.92 | 277.231 | 0 | 311 |  |  |  | 61.919 | 533.31 | 0.149 | 80 | 0
106.56 | 277.395 | 0 | 297 |  |  |  | 61.921 | 277.413 | 0 | 303 |  |  |  | 61.92 | 277.231 | 0 | 311 |  |  |  | 61.919 | 533.31 | 0.149 | 80 | 0
107.06 | 277.322 | 0 | 295 |  |  |  | 61.921 | 277.303 | 0 | 305 |  |  |  | 61.921 | 277.327 | 0 | 311 |  |  |  | 61.921 | 533.42 | 0.149 | 79 | 0
107.56 | 277.322 | 0 | 295 |  |  |  | 61.921 | 277.303 | 0 | 305 |  |  |  | 61.921 | 277.327 | 0 | 311 |  |  |  | 61.921 | 533.42 | 0.149 | 79 | 0
108.06 | 277.399 | 0 | 300 |  |  |  | 61.92 | 277.511 | 0 | 305 |  |  |  | 61.919 | 277.3 | 0 | 316 |  |  |  | 61.92 | 533.37 | 0.153 | 82 | 0
108.56 | 277.399 | 0 | 300 |  |  |  | 61.92 | 277.511 | 0 | 305 |  |  |  | 61.919 | 277.3 | 0 | 316 |  |  |  | 61.92 | 533.37 | 0.153 | 82 | 0
109.06 | 277.299 | 0 | 301 |  |  |  | 61.921 | 277.413 | 0 | 299 |  |  |  | 61.92 | 277.253 | 0 | 310 |  |  |  | 61.921 | 536.31 | 0.151 | 81 | 0
109.56 | 277.299 | 0 | 301 |  |  |  | 61.921 | 277.413 | 0 | 299 |  |  |  | 61.92 | 277.253 | 0 | 310 |  |  |  | 61.921 | 536.31 | 0.151 | 81 | 0
110.06 | 277.344 | 0 | 293 |  |  |  | 61.921 | 277.497 | 0 | 291 |  |  |  | 61.923 | 277.225 | 0 | 303 |  |  |  | 61.921 | 539.82 | 0.152 | 82 | 0
110.56 | 277.344 | 0 | 293 |  |  |  | 61.921 | 277.497 | 0 | 291 |  |  |  | 61.923 | 277.225 | 0 | 303 |  |  |  | 61.921 | 539.82 | 0.152 | 82 | 0
111.06 | 277.308 | 0 | 301 |  |  |  | 61.918 | 277.38 | 0 | 302 |  |  |  | 61.92 | 277.3 | 0 | 312 |  |  |  | 61.923 | 536.58 | 0.153 | 82 | 0
111.56 | 277.308 | 0 | 301 |  |  |  | 61.918 | 277.38 | 0 | 302 |  |  |  | 61.92 | 277.3 | 0 | 312 |  |  |  | 61.923 | 536.58 | 0.153 | 82 | 0
112.06 | 277.364 | 0 | 299 |  |  |  | 61.92 | 277.262 | 0 | 303 |  |  |  | 61.919 | 277.303 | 0 | 311 |  |  |  | 61.92 | 533.39 | 0.154 | 82 | 0
112.56 | 277.364 | 0 | 299 |  |  |  | 61.92 | 277.262 | 0 | 303 |  |  |  | 61.919 | 277.303 | 0 | 311 |  |  |  | 61.92 | 533.39 | 0.154 | 82 | 0
113.06 | 277.392 | 0 | 297 |  |  |  | 61.921 | 277.415 | 0 | 305 |  |  |  | 61.919 | 277.264 | 0 | 313 |  |  |  | 61.921 | 533.43 | 0.155 | 83 | 0
113.56 | 277.392 | 0 | 297 |  |  |  | 61.921 | 277.415 | 0 | 305 |  |  |  | 61.919 | 277.264 | 0 | 313 |  |  |  | 61.921 | 533.43 | 0.155 | 83 | 0
114.06 | 277.36 | 0 | 294 |  |  |  | 61.921 | 277.318 | 0 | 302 |  |  |  | 61.919 | 277.233 | 0 | 315 |  |  |  | 61.921 | 533.29 | 0.152 | 81 | 0
114.56 | 277.36 | 0 | 294 |  |  |  | 61.921 | 277.318 | 0 | 302 |  |  |  | 61.919 | 277.233 | 0 | 315 |  |  |  | 61.921 | 533.29 | 0.152 | 81 | 0
115.06 | 277.408 | 0 | 298 |  |  |  | 61.92 | 277.476 | 0 | 304 |  |  |  | 61.922 | 277.212 | 0 | 312 |  |  |  | 61.92 | 530.5 | 0.156 | 83 | 0
115.56 | 277.408 | 0 | 298 |  |  |  | 61.92 | 277.476 | 0 | 304 |  |  |  | 61.922 | 277.212 | 0 | 312 |  |  |  | 61.92 | 530.5 | 0.156 | 83 | 0
116.06 | 277.298 | 0 | 294 |  |  |  | 61.921 | 277.337 | 0 | 300 |  |  |  | 61.918 | 277.301 | 0 | 311 |  |  |  | 61.921 | 526.87 | 0.155 | 82 | 0
116.56 | 277.298 | 0 | 294 |  |  |  | 61.921 | 277.337 | 0 | 300 |  |  |  | 61.918 | 277.301 | 0 | 311 |  |  |  | 61.921 | 526.87 | 0.155 | 82 | 0
117.06 | 277.384 | 0 | 294 |  |  |  | 61.92 | 277.436 | 0 | 304 |  |  |  | 61.921 | 277.29 | 0 | 310 |  |  |  | 61.919 | 530.11 | 0.156 | 83 | 0
117.56 | 277.384 | 0 | 294 |  |  |  | 61.92 | 277.436 | 0 | 304 |  |  |  | 61.921 | 277.29 | 0 | 310 |  |  |  | 61.919 | 530.11 | 0.156 | 83 | 0
118.06 | 277.286 | 0 | 297 |  |  |  | 61.921 | 277.42 | 0 | 308 |  |  |  | 61.921 | 277.241 | 0 | 314 |  |  |  | 61.921 | 533.36 | 0.157 | 84 | 0
118.56 | 277.286 | 0 | 297 |  |  |  | 61.921 | 277.42 | 0 | 308 |  |  |  | 61.921 | 277.241 | 0 | 314 |  |  |  | 61.921 | 533.36 | 0.157 | 84 | 0
119.06 | 277.343 | 0 | 298 |  |  |  | 61.92 | 277.279 | 0 | 301 |  |  |  | 61.919 | 277.205 | 0 | 310 |  |  |  | 61.919 | 533.24 | 0.154 | 82 | 0
119.56 | 277.343 | 0 | 298 |  |  |  | 61.92 | 277.279 | 0 | 301 |  |  |  | 61.919 | 277.205 | 0 | 310 |  |  |  | 61.919 | 533.24 | 0.154 | 82 | 0
120.06 | 277.318 | 0 | 300 |  |  |  | 61.918 | 277.418 | 0 | 301 |  |  |  | 61.92 | 277.3 | 0 | 312 |  |  |  | 61.921 | 533.36 | 0.155 | 82 | 0
120.56 | 277.318 | 0 | 300 |  |  |  | 61.918 | 277.418 | 0 | 301 |  |  |  | 61.92 | 277.3 | 0 | 312 |  |  |  | 61.921 | 533.36 | 0.155 | 82 | 0
121.06 | 277.36 | 0 | 298 |  |  |  | 61.92 | 277.294 | 0 | 302 |  |  |  | 61.92 | 277.29 | 0 | 310 |  |  |  | 61.919 | 536.35 | 0.151 | 81 | 0
121.56 | 277.36 | 0 | 298 |  |  |  | 61.92 | 277.294 | 0 | 302 |  |  |  | 61.92 | 277.29 | 0 | 310 |  |  |  | 61.919 | 536.35 | 0.151 | 81 | 0
122.06 | 277.392 | 0 | 294 |  |  |  | 61.92 | 277.475 | 0 | 296 |  |  |  | 61.923 | 277.257 | 0 | 302 |  |  |  | 61.92 | 539.77 | 0.156 | 84 | 0
122.56 | 277.392 | 0 | 294 |  |  |  | 61.92 | 277.475 | 0 | 296 |  |  |  | 61.923 | 277.257 | 0 | 302 |  |  |  | 61.92 | 539.77 | 0.156 | 84 | 0
123.06 | 277.352 | 0 | 299 |  |  |  | 61.921 | 277.353 | 0 | 304 |  |  |  | 61.919 | 277.214 | 0 | 316 |  |  |  | 61.919 | 536.63 | 0.154 | 83 | 0
123.59 | 277.352 | 0 | 299 |  |  |  | 61.921 | 277.353 | 0 | 304 |  |  |  | 61.919 | 277.214 | 0 | 316 |  |  |  | 61.919 | 536.63 | 0.154 | 83 | 0
124.09 | 277.418 | 0 | 296 |  |  |  | 61.919 | 277.209 | 0 | 300 |  |  |  | 61.92 | 277.342 | 0 | 312 |  |  |  | 61.919 | 533.3 | 0.152 | 81 | 0
124.57 | 277.418 | 0 | 296 |  |  |  | 61.919 | 277.209 | 0 | 300 |  |  |  | 61.92 | 277.342 | 0 | 312 |  |  |  | 61.919 | 533.3 | 0.152 | 81 | 0
125.07 | 277.319 | 0 | 297 |  |  |  | 61.921 | 277.352 | 0 | 299 |  |  |  | 61.92 | 277.32 | 0 | 311 |  |  |  | 61.92 | 533.28 | 0.148 | 79 | 0
125.56 | 277.319 | 0 | 297 |  |  |  | 61.921 | 277.352 | 0 | 299 |  |  |  | 61.92 | 277.32 | 0 | 311 |  |  |  | 61.92 | 533.28 | 0.148 | 79 | 0
126.06 | 277.4 | 0 | 296 |  |  |  | 61.92 | 277.209 | 0 | 299 |  |  |  | 61.919 | 277.309 | 0 | 309 |  |  |  | 61.921 | 533.35 | 0.158 | 84 | 0
126.6 | 277.338 | 0 | 300 |  |  |  | 61.92 | 277.45 | 0 | 307 |  |  |  | 61.919 | 277.258 | 0 | 312 |  |  |  | 61.921 | 530.43 | 0.155 | 82 | 0
127.1 | 277.338 | 0 | 300 |  |  |  | 61.92 | 277.45 | 0 | 307 |  |  |  | 61.919 | 277.258 | 0 | 312 |  |  |  | 61.921 | 530.43 | 0.155 | 82 | 0
127.57 | 277.369 | 0 | 295 |  |  |  | 61.92 | 277.307 | 0 | 305 |  |  |  | 61.919 | 277.226 | 0 | 309 |  |  |  | 61.919 | 526.9 | 0.157 | 82 | 0
128.07 | 277.369 | 0 | 295 |  |  |  | 61.92 | 277.307 | 0 | 305 |  |  |  | 61.919 | 277.226 | 0 | 309 |  |  |  | 61.919 | 526.9 | 0.157 | 82 | 0
128.56 | 277.34 | 0 | 295 |  |  |  | 61.918 | 277.41 | 0 | 301 |  |  |  | 61.921 | 277.312 | 0 | 311 |  |  |  | 61.921 | 530.05 | 0.154 | 82 | 0
129.06 | 277.34 | 0 | 295 |  |  |  | 61.918 | 277.41 | 0 | 301 |  |  |  | 61.921 | 277.312 | 0 | 311 |  |  |  | 61.921 | 530.05 | 0.154 | 82 | 0
129.56 | 277.386 | 0 | 299 |  |  |  | 61.921 | 277.378 | 0 | 302 |  |  |  | 61.92 | 277.302 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
130.06 | 277.386 | 0 | 299 |  |  |  | 61.921 | 277.378 | 0 | 302 |  |  |  | 61.92 | 277.302 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
130.56 | 277.417 | 0 | 295 |  |  |  | 61.92 | 277.269 | 0 | 302 |  |  |  | 61.92 | 277.271 | 0 | 311 |  |  |  | 61.92 | 533.31 | 0.152 | 81 | 0
131.06 | 277.417 | 0 | 295 |  |  |  | 61.92 | 277.269 | 0 | 302 |  |  |  | 61.92 | 277.271 | 0 | 311 |  |  |  | 61.92 | 533.31 | 0.152 | 81 | 0
131.56 | 277.372 | 0 | 298 |  |  |  | 61.921 | 277.439 | 0 | 305 |  |  |  | 61.92 | 277.224 | 0 | 311 |  |  |  | 61.919 | 533.38 | 0.154 | 82 | 0
132.06 | 277.372 | 0 | 298 |  |  |  | 61.921 | 277.439 | 0 | 305 |  |  |  | 61.92 | 277.224 | 0 | 311 |  |  |  | 61.919 | 533.38 | 0.154 | 82 | 0
132.56 | 277.431 | 0 | 296 |  |  |  | 61.921 | 277.314 | 0 | 299 |  |  |  | 61.92 | 277.332 | 0 | 309 |  |  |  | 61.921 | 536.14 | 0.151 | 81 | 0
133.06 | 277.431 | 0 | 296 |  |  |  | 61.921 | 277.314 | 0 | 299 |  |  |  | 61.92 | 277.332 | 0 | 309 |  |  |  | 61.921 | 536.14 | 0.151 | 81 | 0
133.56 | 277.284 | 0 | 293 |  |  |  | 61.921 | 277.48 | 0 | 293 |  |  |  | 61.923 | 277.308 | 0 | 303 |  |  |  | 61.919 | 539.83 | 0.155 | 84 | 0
134.06 | 277.284 | 0 | 293 |  |  |  | 61.921 | 277.48 | 0 | 293 |  |  |  | 61.923 | 277.308 | 0 | 303 |  |  |  | 61.919 | 539.83 | 0.155 | 84 | 0
134.56 | 277.369 | 0 | 297 |  |  |  | 61.92 | 277.345 | 0 | 307 |  |  |  | 61.92 | 277.292 | 0 | 317 |  |  |  | 61.92 | 536.83 | 0.155 | 83 | 0
135.06 | 277.369 | 0 | 297 |  |  |  | 61.92 | 277.345 | 0 | 307 |  |  |  | 61.92 | 277.292 | 0 | 317 |  |  |  | 61.92 | 536.83 | 0.155 | 83 | 0
135.56 | 277.305 | 0 | 298 |  |  |  | 61.921 | 277.287 | 0 | 303 |  |  |  | 61.919 | 277.255 | 0 | 312 |  |  |  | 61.919 | 533.34 | 0.152 | 81 | 0
136.06 | 277.305 | 0 | 298 |  |  |  | 61.921 | 277.287 | 0 | 303 |  |  |  | 61.919 | 277.255 | 0 | 312 |  |  |  | 61.919 | 533.34 | 0.152 | 81 | 0
136.56 | 277.353 | 0 | 300 |  |  |  | 61.921 | 277.435 | 0 | 300 |  |  |  | 61.919 | 277.343 | 0 | 307 |  |  |  | 61.921 | 533.44 | 0.154 | 82 | 0
137.06 | 277.353 | 0 | 300 |  |  |  | 61.921 | 277.435 | 0 | 300 |  |  |  | 61.919 | 277.343 | 0 | 307 |  |  |  | 61.921 | 533.44 | 0.154 | 82 | 0
137.56 | 277.308 | 0 | 297 |  |  |  | 61.917 | 277.299 | 0 | 308 |  |  |  | 61.92 | 277.302 | 0 | 313 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 0
138.06 | 277.308 | 0 | 297 |  |  |  | 61.917 | 277.299 | 0 | 308 |  |  |  | 61.92 | 277.302 | 0 | 313 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 0
138.56 | 277.367 | 0 | 297 |  |  |  | 61.92 | 277.492 | 0 | 306 |  |  |  | 61.921 | 277.29 | 0 | 314 |  |  |  | 61.921 | 530.58 | 0.155 | 82 | 0
139.06 | 277.367 | 0 | 297 |  |  |  | 61.92 | 277.492 | 0 | 306 |  |  |  | 61.921 | 277.29 | 0 | 314 |  |  |  | 61.921 | 530.58 | 0.155 | 82 | 0
139.56 | 277.417 | 0 | 297 |  |  |  | 61.919 | 277.364 | 0 | 297 |  |  |  | 61.919 | 277.271 | 0 | 309 |  |  |  | 61.92 | 526.9 | 0.154 | 81 | 0
140.06 | 277.417 | 0 | 297 |  |  |  | 61.919 | 277.364 | 0 | 297 |  |  |  | 61.919 | 277.271 | 0 | 309 |  |  |  | 61.92 | 526.9 | 0.154 | 81 | 0
140.56 | 277.329 | 0 | 293 |  |  |  | 61.921 | 277.506 | 0 | 297 |  |  |  | 61.923 | 277.357 | 0 | 309 |  |  |  | 61.92 | 530.02 | 0.149 | 79 | 0
141.06 | 277.329 | 0 | 293 |  |  |  | 61.921 | 277.506 | 0 | 297 |  |  |  | 61.923 | 277.357 | 0 | 309 |  |  |  | 61.92 | 530.02 | 0.149 | 79 | 0
141.56 | 277.407 | 0 | 298 |  |  |  | 61.921 | 277.414 | 0 | 303 |  |  |  | 61.919 | 277.33 | 0 | 312 |  |  |  | 61.92 | 533.48 | 0.154 | 82 | 0
142.06 | 277.407 | 0 | 298 |  |  |  | 61.921 | 277.414 | 0 | 303 |  |  |  | 61.919 | 277.33 | 0 | 312 |  |  |  | 61.92 | 533.48 | 0.154 | 82 | 0
142.56 | 277.291 | 0 | 300 |  |  |  | 61.92 | 277.345 | 0 | 302 |  |  |  | 61.92 | 277.295 | 0 | 317 |  |  |  | 61.919 | 533.42 | 0.149 | 80 | 0
143.06 | 277.291 | 0 | 300 |  |  |  | 61.92 | 277.345 | 0 | 302 |  |  |  | 61.92 | 277.295 | 0 | 317 |  |  |  | 61.919 | 533.42 | 0.149 | 80 | 0
143.56 | 277.352 | 0 | 300 |  |  |  | 61.921 | 277.462 | 0 | 301 |  |  |  | 61.919 | 277.283 | 0 | 309 |  |  |  | 61.921 | 533.39 | 0.157 | 84 | 0
144.06 | 277.352 | 0 | 300 |  |  |  | 61.921 | 277.462 | 0 | 301 |  |  |  | 61.919 | 277.283 | 0 | 309 |  |  |  | 61.921 | 533.39 | 0.157 | 84 | 0
144.56 | 277.313 | 0 | 295 |  |  |  | 61.92 | 277.357 | 0 | 298 |  |  |  | 61.919 | 277.243 | 0 | 312 |  |  |  | 61.92 | 536.12 | 0.15 | 80 | 0
145.06 | 277.313 | 0 | 295 |  |  |  | 61.92 | 277.357 | 0 | 298 |  |  |  | 61.919 | 277.243 | 0 | 312 |  |  |  | 61.92 | 536.12 | 0.15 | 80 | 0
145.56 | 277.341 | 0 | 292 |  |  |  | 61.921 | 277.555 | 0 | 298 |  |  |  | 61.923 | 277.338 | 0 | 306 |  |  |  | 61.921 | 539.85 | 0.154 | 83 | 0
146.06 | 277.341 | 0 | 292 |  |  |  | 61.921 | 277.555 | 0 | 298 |  |  |  | 61.923 | 277.338 | 0 | 306 |  |  |  | 61.921 | 539.85 | 0.154 | 83 | 0
146.56 | 277.308 | 0 | 305 |  |  |  | 61.918 | 277.432 | 0 | 303 |  |  |  | 61.92 | 277.29 | 0 | 316 |  |  |  | 61.92 | 536.94 | 0.15 | 80 | 0
147.06 | 277.308 | 0 | 305 |  |  |  | 61.918 | 277.432 | 0 | 303 |  |  |  | 61.92 | 277.29 | 0 | 316 |  |  |  | 61.92 | 536.94 | 0.15 | 80 | 0
147.56 | 277.374 | 0 | 297 |  |  |  | 61.921 | 277.352 | 0 | 306 |  |  |  | 61.92 | 277.266 | 0 | 306 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 0
148.06 | 277.374 | 0 | 297 |  |  |  | 61.921 | 277.352 | 0 | 306 |  |  |  | 61.92 | 277.266 | 0 | 306 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 0
148.56 | 277.412 | 0 | 300 |  |  |  | 61.92 | 277.454 | 0 | 303 |  |  |  | 61.92 | 277.251 | 0 | 314 |  |  |  | 61.92 | 533.46 | 0.153 | 81 | 0
149.06 | 277.412 | 0 | 300 |  |  |  | 61.92 | 277.454 | 0 | 303 |  |  |  | 61.92 | 277.251 | 0 | 314 |  |  |  | 61.92 | 533.46 | 0.153 | 81 | 0
149.56 | 277.327 | 0 | 299 |  |  |  | 61.921 | 277.29 | 0 | 307 |  |  |  | 61.92 | 277.334 | 0 | 309 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 0
150.06 | 277.327 | 0 | 299 |  |  |  | 61.921 | 277.29 | 0 | 307 |  |  |  | 61.92 | 277.334 | 0 | 309 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 0
150.56 | 277.389 | 0 | 297 |  |  |  | 61.921 | 277.475 | 0 | 303 |  |  |  | 61.919 | 277.284 | 0 | 314 |  |  |  | 61.92 | 530.73 | 0.148 | 78 | 0
151.06 | 277.389 | 0 | 297 |  |  |  | 61.921 | 277.475 | 0 | 303 |  |  |  | 61.919 | 277.284 | 0 | 314 |  |  |  | 61.92 | 530.73 | 0.148 | 78 | 0
151.56 | 277.3 | 0 | 295 |  |  |  | 61.921 | 277.389 | 0 | 301 |  |  |  | 61.92 | 277.244 | 0 | 310 |  |  |  | 61.921 | 526.98 | 0.153 | 81 | 0
152.06 | 277.3 | 0 | 295 |  |  |  | 61.921 | 277.389 | 0 | 301 |  |  |  | 61.92 | 277.244 | 0 | 310 |  |  |  | 61.921 | 526.98 | 0.153 | 81 | 0
152.56 | 277.339 | 0 | 296 |  |  |  | 61.921 | 277.518 | 0 | 302 |  |  |  | 61.922 | 277.224 | 0 | 311 |  |  |  | 61.92 | 529.85 | 0.148 | 79 | 0
153.1 | 277.339 | 0 | 296 |  |  |  | 61.921 | 277.518 | 0 | 302 |  |  |  | 61.922 | 277.224 | 0 | 311 |  |  |  | 61.92 | 529.85 | 0.148 | 79 | 0
153.6 | 277.324 | 0 | 302 |  |  |  | 61.92 | 277.375 | 0 | 304 |  |  |  | 61.92 | 277.309 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.149 | 79 | 0
154.08 | 277.324 | 0 | 302 |  |  |  | 61.92 | 277.375 | 0 | 304 |  |  |  | 61.92 | 277.309 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.149 | 79 | 0
154.58 | 277.36 | 0 | 300 |  |  |  | 61.92 | 277.26 | 0 | 302 |  |  |  | 61.92 | 277.299 | 0 | 311 |  |  |  | 61.92 | 533.47 | 0.151 | 80 | 0
155.07 | 277.36 | 0 | 300 |  |  |  | 61.92 | 277.26 | 0 | 302 |  |  |  | 61.92 | 277.299 | 0 | 311 |  |  |  | 61.92 | 533.47 | 0.151 | 80 | 0
155.57 | 277.294 | 0 | 298 |  |  |  | 61.918 | 277.467 | 0 | 302 |  |  |  | 61.92 | 277.238 | 0 | 312 |  |  |  | 61.921 | 533.48 | 0.15 | 80 | 0
156.06 | 277.294 | 0 | 298 |  |  |  | 61.918 | 277.467 | 0 | 302 |  |  |  | 61.92 | 277.238 | 0 | 312 |  |  |  | 61.921 | 533.48 | 0.15 | 80 | 0
156.56 | 277.388 | 0 | 297 |  |  |  | 61.92 | 277.313 | 0 | 301 |  |  |  | 61.92 | 277.21 | 0 | 313 |  |  |  | 61.919 | 536.05 | 0.149 | 80 | 0
157.09 | 277.431 | 0 | 291 |  |  |  | 61.919 | 277.512 | 0 | 301 |  |  |  | 61.921 | 277.304 | 0 | 299 |  |  |  | 61.921 | 539.8 | 0.149 | 80 | 0
157.59 | 277.431 | 0 | 291 |  |  |  | 61.919 | 277.512 | 0 | 301 |  |  |  | 61.921 | 277.304 | 0 | 299 |  |  |  | 61.921 | 539.8 | 0.149 | 80 | 0
158.07 | 277.322 | 0 | 302 |  |  |  | 61.921 | 277.359 | 0 | 307 |  |  |  | 61.92 | 277.308 | 0 | 315 |  |  |  | 61.921 | 537.02 | 0.148 | 79 | 0
158.57 | 277.322 | 0 | 302 |  |  |  | 61.921 | 277.359 | 0 | 307 |  |  |  | 61.92 | 277.308 | 0 | 315 |  |  |  | 61.921 | 537.02 | 0.148 | 79 | 0
159.06 | 277.399 | 0 | 295 |  |  |  | 61.921 | 277.368 | 0 | 306 |  |  |  | 61.92 | 277.286 | 0 | 312 |  |  |  | 61.92 | 533.26 | 0.148 | 79 | 0
159.56 | 277.399 | 0 | 295 |  |  |  | 61.921 | 277.368 | 0 | 306 |  |  |  | 61.92 | 277.286 | 0 | 312 |  |  |  | 61.92 | 533.26 | 0.148 | 79 | 0
160.06 | 277.307 | 0 | 302 |  |  |  | 61.92 | 277.424 | 0 | 301 |  |  |  | 61.919 | 277.233 | 0 | 310 |  |  |  | 61.921 | 533.38 | 0.151 | 80 | 0
160.56 | 277.307 | 0 | 302 |  |  |  | 61.92 | 277.424 | 0 | 301 |  |  |  | 61.919 | 277.233 | 0 | 310 |  |  |  | 61.921 | 533.38 | 0.151 | 80 | 0
161.06 | 277.349 | 0 | 297 |  |  |  | 61.921 | 277.289 | 0 | 303 |  |  |  | 61.92 | 277.212 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.152 | 81 | 0
161.56 | 277.349 | 0 | 297 |  |  |  | 61.921 | 277.289 | 0 | 303 |  |  |  | 61.92 | 277.212 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.152 | 81 | 0
162.06 | 277.301 | 0 | 302 |  |  |  | 61.92 | 277.415 | 0 | 302 |  |  |  | 61.919 | 277.289 | 0 | 310 |  |  |  | 61.921 | 530.79 | 0.155 | 82 | 0
162.56 | 277.301 | 0 | 302 |  |  |  | 61.92 | 277.415 | 0 | 302 |  |  |  | 61.919 | 277.289 | 0 | 310 |  |  |  | 61.921 | 530.79 | 0.155 | 82 | 0
163.06 | 277.364 | 0 | 294 |  |  |  | 61.921 | 277.292 | 0 | 298 |  |  |  | 61.92 | 277.281 | 0 | 309 |  |  |  | 61.921 | 527.01 | 0.152 | 80 | 0
163.56 | 277.364 | 0 | 294 |  |  |  | 61.921 | 277.292 | 0 | 298 |  |  |  | 61.92 | 277.281 | 0 | 309 |  |  |  | 61.921 | 527.01 | 0.152 | 80 | 0
164.06 | 277.269 | 0 | 298 |  |  |  | 61.917 | 277.508 | 0 | 302 |  |  |  | 61.921 | 277.236 | 0 | 308 |  |  |  | 61.92 | 529.77 | 0.151 | 80 | 0
164.56 | 277.269 | 0 | 298 |  |  |  | 61.917 | 277.508 | 0 | 302 |  |  |  | 61.921 | 277.236 | 0 | 308 |  |  |  | 61.92 | 529.77 | 0.151 | 80 | 0
165.06 | 277.357 | 0 | 297 |  |  |  | 61.921 | 277.364 | 0 | 307 |  |  |  | 61.921 | 277.206 | 0 | 310 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 0
165.56 | 277.357 | 0 | 297 |  |  |  | 61.921 | 277.364 | 0 | 307 |  |  |  | 61.921 | 277.206 | 0 | 310 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 0
166.06 | 277.426 | 0 | 297 |  |  |  | 61.92 | 277.239 | 0 | 305 |  |  |  | 61.919 | 277.294 | 0 | 314 |  |  |  | 61.92 | 533.31 | 0.155 | 83 | 0
166.56 | 277.426 | 0 | 297 |  |  |  | 61.92 | 277.239 | 0 | 305 |  |  |  | 61.919 | 277.294 | 0 | 314 |  |  |  | 61.92 | 533.31 | 0.155 | 83 | 0
167.06 | 277.304 | 0 | 301 |  |  |  | 61.92 | 277.422 | 0 | 304 |  |  |  | 61.92 | 277.287 | 0 | 315 |  |  |  | 61.92 | 533.44 | 0.155 | 83 | 0
167.56 | 277.304 | 0 | 301 |  |  |  | 61.92 | 277.422 | 0 | 304 |  |  |  | 61.92 | 277.287 | 0 | 315 |  |  |  | 61.92 | 533.44 | 0.155 | 83 | 0
168.06 | 277.381 | 0 | 295 |  |  |  | 61.921 | 277.297 | 0 | 301 |  |  |  | 61.92 | 277.267 | 0 | 307 |  |  |  | 61.919 | 535.79 | 0.152 | 81 | 0
168.56 | 277.381 | 0 | 295 |  |  |  | 61.921 | 277.297 | 0 | 301 |  |  |  | 61.92 | 277.267 | 0 | 307 |  |  |  | 61.919 | 535.79 | 0.152 | 81 | 0
169.06 | 277.308 | 0 | 291 |  |  |  | 61.92 | 277.478 | 0 | 294 |  |  |  | 61.923 | 277.217 | 0 | 305 |  |  |  | 61.921 | 539.88 | 0.153 | 83 | 0
169.56 | 277.308 | 0 | 291 |  |  |  | 61.92 | 277.478 | 0 | 294 |  |  |  | 61.923 | 277.217 | 0 | 305 |  |  |  | 61.921 | 539.88 | 0.153 | 83 | 0
170.06 | 277.357 | 0 | 300 |  |  |  | 61.921 | 277.341 | 0 | 303 |  |  |  | 61.92 | 277.301 | 0 | 313 |  |  |  | 61.921 | 537.03 | 0.151 | 81 | 0
170.56 | 277.357 | 0 | 300 |  |  |  | 61.921 | 277.341 | 0 | 303 |  |  |  | 61.92 | 277.301 | 0 | 313 |  |  |  | 61.921 | 537.03 | 0.151 | 81 | 0
171.06 | 277.313 | 0 | 297 |  |  |  | 61.921 | 277.424 | 0 | 301 |  |  |  | 61.922 | 277.28 | 0 | 309 |  |  |  | 61.919 | 533.35 | 0.15 | 80 | 0
171.56 | 277.313 | 0 | 297 |  |  |  | 61.921 | 277.424 | 0 | 301 |  |  |  | 61.922 | 277.28 | 0 | 309 |  |  |  | 61.919 | 533.35 | 0.15 | 80 | 0
172.06 | 277.371 | 0 | 298 |  |  |  | 61.921 | 277.365 | 0 | 301 |  |  |  | 61.918 | 277.274 | 0 | 312 |  |  |  | 61.92 | 533.34 | 0.15 | 80 | 0
172.56 | 277.371 | 0 | 298 |  |  |  | 61.921 | 277.365 | 0 | 301 |  |  |  | 61.918 | 277.274 | 0 | 312 |  |  |  | 61.92 | 533.34 | 0.15 | 80 | 0
173.06 | 277.278 | 0 | 298 |  |  |  | 61.918 | 277.287 | 0 | 300 |  |  |  | 61.92 | 277.232 | 0 | 310 |  |  |  | 61.92 | 533.4 | 0.151 | 80 | 0
173.56 | 277.278 | 0 | 298 |  |  |  | 61.918 | 277.287 | 0 | 300 |  |  |  | 61.92 | 277.232 | 0 | 310 |  |  |  | 61.92 | 533.4 | 0.151 | 80 | 0
174.06 | 277.355 | 0 | 300 |  |  |  | 61.921 | 277.429 | 0 | 304 |  |  |  | 61.921 | 277.352 | 0 | 313 |  |  |  | 61.923 | 530.91 | 0.153 | 81 | 0
174.56 | 277.355 | 0 | 300 |  |  |  | 61.921 | 277.429 | 0 | 304 |  |  |  | 61.921 | 277.352 | 0 | 313 |  |  |  | 61.923 | 530.91 | 0.153 | 81 | 0
175.06 | 277.424 | 0 | 295 |  |  |  | 61.919 | 277.328 | 0 | 297 |  |  |  | 61.919 | 277.314 | 0 | 308 |  |  |  | 61.921 | 526.94 | 0.153 | 80 | 0
175.56 | 277.424 | 0 | 295 |  |  |  | 61.919 | 277.328 | 0 | 297 |  |  |  | 61.919 | 277.314 | 0 | 308 |  |  |  | 61.921 | 526.94 | 0.153 | 80 | 0
176.06 | 277.303 | 0 | 294 |  |  |  | 61.921 | 277.527 | 0 | 304 |  |  |  | 61.923 | 277.307 | 0 | 314 |  |  |  | 61.92 | 529.64 | 0.148 | 78 | 0
176.56 | 277.303 | 0 | 294 |  |  |  | 61.921 | 277.527 | 0 | 304 |  |  |  | 61.923 | 277.307 | 0 | 314 |  |  |  | 61.92 | 529.64 | 0.148 | 78 | 0
177.06 | 277.363 | 0 | 300 |  |  |  | 61.92 | 277.39 | 0 | 301 |  |  |  | 61.919 | 277.292 | 0 | 312 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 0
177.56 | 277.363 | 0 | 300 |  |  |  | 61.92 | 277.39 | 0 | 301 |  |  |  | 61.919 | 277.292 | 0 | 312 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 0
178.06 | 277.314 | 0 | 298 |  |  |  | 61.921 | 277.277 | 0 | 304 |  |  |  | 61.92 | 277.238 | 0 | 309 |  |  |  | 61.92 | 533.42 | 0.149 | 79 | 0
178.56 | 277.314 | 0 | 298 |  |  |  | 61.921 | 277.277 | 0 | 304 |  |  |  | 61.92 | 277.238 | 0 | 309 |  |  |  | 61.92 | 533.42 | 0.149 | 79 | 0
179.06 | 277.353 | 0 | 299 |  |  |  | 61.92 | 277.463 | 0 | 303 |  |  |  | 61.921 | 277.325 | 0 | 311 |  |  |  | 61.92 | 533.35 | 0.151 | 80 | 0
179.56 | 277.353 | 0 | 299 |  |  |  | 61.92 | 277.463 | 0 | 303 |  |  |  | 61.921 | 277.325 | 0 | 311 |  |  |  | 61.92 | 533.35 | 0.151 | 80 | 0
180.06 | 277.312 | 0 | 295 |  |  |  | 61.919 | 277.348 | 0 | 301 |  |  |  | 61.919 | 277.294 | 0 | 308 |  |  |  | 61.92 | 535.81 | 0.152 | 81 | 0
180.56 | 277.312 | 0 | 295 |  |  |  | 61.919 | 277.348 | 0 | 301 |  |  |  | 61.919 | 277.294 | 0 | 308 |  |  |  | 61.92 | 535.81 | 0.152 | 81 | 0
181.06 | 277.38 | 0 | 294 |  |  |  | 61.921 | 277.495 | 0 | 296 |  |  |  | 61.922 | 277.284 | 0 | 304 |  |  |  | 61.92 | 539.86 | 0.154 | 83 | 0
181.56 | 277.38 | 0 | 294 |  |  |  | 61.921 | 277.495 | 0 | 296 |  |  |  | 61.922 | 277.284 | 0 | 304 |  |  |  | 61.92 | 539.86 | 0.154 | 83 | 0
182.06 | 277.282 | 0 | 299 |  |  |  | 61.917 | 277.389 | 0 | 304 |  |  |  | 61.919 | 277.247 | 0 | 314 |  |  |  | 61.921 | 537.03 | 0.143 | 77 | 0
182.56 | 277.282 | 0 | 299 |  |  |  | 61.917 | 277.389 | 0 | 304 |  |  |  | 61.919 | 277.247 | 0 | 314 |  |  |  | 61.921 | 537.03 | 0.143 | 77 | 0
183.06 | 277.353 | 0 | 301 |  |  |  | 61.921 | 277.476 | 0 | 304 |  |  |  | 61.92 | 277.356 | 0 | 311 |  |  |  | 61.92 | 533.35 | 0.148 | 79 | 0
183.56 | 277.353 | 0 | 301 |  |  |  | 61.921 | 277.476 | 0 | 304 |  |  |  | 61.92 | 277.356 | 0 | 311 |  |  |  | 61.92 | 533.35 | 0.148 | 79 | 0
184.06 | 277.42 | 0 | 300 |  |  |  | 61.92 | 277.426 | 0 | 303 |  |  |  | 61.92 | 277.303 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 0
184.6 | 277.42 | 0 | 300 |  |  |  | 61.92 | 277.426 | 0 | 303 |  |  |  | 61.92 | 277.303 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.148 | 79 | 0
185.11 | 277.303 | 0 | 298 |  |  |  | 61.92 | 277.318 | 0 | 304 |  |  |  | 61.92 | 277.284 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.149 | 80 | 0
185.58 | 277.303 | 0 | 298 |  |  |  | 61.92 | 277.318 | 0 | 304 |  |  |  | 61.92 | 277.284 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.149 | 80 | 0
186.08 | 277.359 | 0 | 296 |  |  |  | 61.921 | 277.488 | 0 | 306 |  |  |  | 61.92 | 277.266 | 0 | 313 |  |  |  | 61.921 | 530.93 | 0.152 | 81 | 0
186.57 | 277.359 | 0 | 296 |  |  |  | 61.921 | 277.488 | 0 | 306 |  |  |  | 61.92 | 277.266 | 0 | 313 |  |  |  | 61.921 | 530.93 | 0.152 | 81 | 0
187.07 | 277.316 | 0 | 297 |  |  |  | 61.92 | 277.325 | 0 | 299 |  |  |  | 61.92 | 277.355 | 0 | 306 |  |  |  | 61.92 | 526.97 | 0.149 | 79 | 0
187.56 | 277.316 | 0 | 297 |  |  |  | 61.92 | 277.325 | 0 | 299 |  |  |  | 61.92 | 277.355 | 0 | 306 |  |  |  | 61.92 | 526.97 | 0.149 | 79 | 0
188.06 | 277.361 | 0 | 296 |  |  |  | 61.92 | 277.552 | 0 | 297 |  |  |  | 61.922 | 277.282 | 0 | 310 |  |  |  | 61.921 | 529.61 | 0.155 | 82 | 0
188.6 | 277.316 | 0 | 295 |  |  |  | 61.921 | 277.43 | 0 | 303 |  |  |  | 61.92 | 277.244 | 0 | 310 |  |  |  | 61.921 | 533.45 | 0.152 | 81 | 0
189.1 | 277.316 | 0 | 295 |  |  |  | 61.921 | 277.43 | 0 | 303 |  |  |  | 61.92 | 277.244 | 0 | 310 |  |  |  | 61.921 | 533.45 | 0.152 | 81 | 0
189.58 | 277.391 | 0 | 298 |  |  |  | 61.92 | 277.307 | 0 | 305 |  |  |  | 61.92 | 277.231 | 0 | 309 |  |  |  | 61.92 | 533.3 | 0.15 | 80 | 0
190.08 | 277.391 | 0 | 298 |  |  |  | 61.92 | 277.307 | 0 | 305 |  |  |  | 61.92 | 277.231 | 0 | 309 |  |  |  | 61.92 | 533.3 | 0.15 | 80 | 0
190.56 | 277.271 | 0 | 300 |  |  |  | 61.917 | 277.475 | 0 | 301 |  |  |  | 61.919 | 277.313 | 0 | 309 |  |  |  | 61.922 | 533.48 | 0.151 | 81 | 0
191.06 | 277.271 | 0 | 300 |  |  |  | 61.917 | 277.475 | 0 | 301 |  |  |  | 61.919 | 277.313 | 0 | 309 |  |  |  | 61.922 | 533.48 | 0.151 | 81 | 0
191.56 | 277.334 | 0 | 293 |  |  |  | 61.92 | 277.325 | 0 | 298 |  |  |  | 61.921 | 277.307 | 0 | 308 |  |  |  | 61.919 | 535.68 | 0.149 | 80 | 0
192.06 | 277.334 | 0 | 293 |  |  |  | 61.92 | 277.325 | 0 | 298 |  |  |  | 61.921 | 277.307 | 0 | 308 |  |  |  | 61.919 | 535.68 | 0.149 | 80 | 0
192.56 | 277.41 | 0 | 290 |  |  |  | 61.92 | 277.526 | 0 | 294 |  |  |  | 61.923 | 277.264 | 0 | 305 |  |  |  | 61.921 | 539.89 | 0.153 | 83 | 0
193.06 | 277.41 | 0 | 290 |  |  |  | 61.92 | 277.526 | 0 | 294 |  |  |  | 61.923 | 277.264 | 0 | 305 |  |  |  | 61.921 | 539.89 | 0.153 | 83 | 0
193.56 | 277.312 | 0 | 302 |  |  |  | 61.921 | 277.365 | 0 | 303 |  |  |  | 61.919 | 277.238 | 0 | 314 |  |  |  | 61.92 | 537.15 | 0.154 | 83 | 0
194.06 | 277.312 | 0 | 302 |  |  |  | 61.921 | 277.365 | 0 | 303 |  |  |  | 61.919 | 277.238 | 0 | 314 |  |  |  | 61.92 | 537.15 | 0.154 | 83 | 0
194.56 | 277.364 | 0 | 299 |  |  |  | 61.921 | 277.453 | 0 | 302 |  |  |  | 61.92 | 277.227 | 0 | 310 |  |  |  | 61.921 | 533.37 | 0.153 | 82 | 0
195.06 | 277.364 | 0 | 299 |  |  |  | 61.921 | 277.453 | 0 | 302 |  |  |  | 61.92 | 277.227 | 0 | 310 |  |  |  | 61.921 | 533.37 | 0.153 | 82 | 0
195.56 | 277.32 | 0 | 297 |  |  |  | 61.921 | 277.391 | 0 | 304 |  |  |  | 61.919 | 277.316 | 0 | 309 |  |  |  | 61.919 | 533.3 | 0.147 | 78 | 0
196.06 | 277.32 | 0 | 297 |  |  |  | 61.921 | 277.391 | 0 | 304 |  |  |  | 61.919 | 277.316 | 0 | 309 |  |  |  | 61.919 | 533.3 | 0.147 | 78 | 0
196.56 | 277.377 | 0 | 297 |  |  |  | 61.92 | 277.289 | 0 | 302 |  |  |  | 61.92 | 277.291 | 0 | 315 |  |  |  | 61.92 | 533.43 | 0.145 | 78 | 0
197.06 | 277.377 | 0 | 297 |  |  |  | 61.92 | 277.289 | 0 | 302 |  |  |  | 61.92 | 277.291 | 0 | 315 |  |  |  | 61.92 | 533.43 | 0.145 | 78 | 0
197.56 | 277.327 | 0 | 297 |  |  |  | 61.921 | 277.48 | 0 | 305 |  |  |  | 61.92 | 277.237 | 0 | 313 |  |  |  | 61.921 | 530.98 | 0.155 | 82 | 0
198.06 | 277.327 | 0 | 297 |  |  |  | 61.921 | 277.48 | 0 | 305 |  |  |  | 61.92 | 277.237 | 0 | 313 |  |  |  | 61.921 | 530.98 | 0.155 | 82 | 0
198.56 | 277.403 | 0 | 295 |  |  |  | 61.921 | 277.331 | 0 | 301 |  |  |  | 61.919 | 277.208 | 0 | 307 |  |  |  | 61.92 | 526.93 | 0.151 | 80 | 0
199.06 | 277.403 | 0 | 295 |  |  |  | 61.921 | 277.331 | 0 | 301 |  |  |  | 61.919 | 277.208 | 0 | 307 |  |  |  | 61.92 | 526.93 | 0.151 | 80 | 0
199.56 | 277.3 | 0 | 295 |  |  |  | 61.917 | 277.465 | 0 | 300 |  |  |  | 61.923 | 277.314 | 0 | 305 |  |  |  | 61.92 | 529.55 | 0.149 | 79 | 0
200.06 | 277.3 | 0 | 295 |  |  |  | 61.917 | 277.465 | 0 | 300 |  |  |  | 61.923 | 277.314 | 0 | 305 |  |  |  | 61.92 | 529.55 | 0.149 | 79 | 0
200.56 | 277.348 | 0 | 297 |  |  |  | 61.92 | 277.351 | 0 | 303 |  |  |  | 61.92 | 277.308 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 0
201.06 | 277.348 | 0 | 297 |  |  |  | 61.92 | 277.351 | 0 | 303 |  |  |  | 61.92 | 277.308 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 0
201.56 | 277.429 | 0 | 299 |  |  |  | 61.92 | 277.276 | 0 | 301 |  |  |  | 61.919 | 277.262 | 0 | 307 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 0
202.06 | 277.429 | 0 | 299 |  |  |  | 61.92 | 277.276 | 0 | 301 |  |  |  | 61.919 | 277.262 | 0 | 307 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 0
202.56 | 277.346 | 0 | 299 |  |  |  | 61.92 | 277.4 | 0 | 301 |  |  |  | 61.92 | 277.217 | 0 | 308 |  |  |  | 61.92 | 533.33 | 0.149 | 80 | 0
203.06 | 277.346 | 0 | 299 |  |  |  | 61.92 | 277.4 | 0 | 301 |  |  |  | 61.92 | 277.217 | 0 | 308 |  |  |  | 61.92 | 533.33 | 0.149 | 80 | 0
203.56 | 277.377 | 0 | 296 |  |  |  | 61.921 | 277.271 | 0 | 303 |  |  |  | 61.92 | 277.3 | 0 | 313 |  |  |  | 61.921 | 535.64 | 0.152 | 81 | 0
204.06 | 277.377 | 0 | 296 |  |  |  | 61.921 | 277.271 | 0 | 303 |  |  |  | 61.92 | 277.3 | 0 | 313 |  |  |  | 61.921 | 535.64 | 0.152 | 81 | 0
204.56 | 277.358 | 0 | 290 |  |  |  | 61.921 | 277.451 | 0 | 292 |  |  |  | 61.921 | 277.294 | 0 | 306 |  |  |  | 61.919 | 539.8 | 0.148 | 80 | 0
205.06 | 277.358 | 0 | 290 |  |  |  | 61.921 | 277.451 | 0 | 292 |  |  |  | 61.921 | 277.294 | 0 | 306 |  |  |  | 61.919 | 539.8 | 0.148 | 80 | 0
205.56 | 277.4 | 0 | 302 |  |  |  | 61.921 | 277.327 | 0 | 303 |  |  |  | 61.92 | 277.271 | 0 | 312 |  |  |  | 61.92 | 537.16 | 0.152 | 81 | 0
206.06 | 277.4 | 0 | 302 |  |  |  | 61.921 | 277.327 | 0 | 303 |  |  |  | 61.92 | 277.271 | 0 | 312 |  |  |  | 61.92 | 537.16 | 0.152 | 81 | 0
206.56 | 277.316 | 0 | 297 |  |  |  | 61.92 | 277.4 | 0 | 299 |  |  |  | 61.919 | 277.217 | 0 | 309 |  |  |  | 61.92 | 533.25 | 0.15 | 80 | 0
207.06 | 277.316 | 0 | 297 |  |  |  | 61.92 | 277.4 | 0 | 299 |  |  |  | 61.919 | 277.217 | 0 | 309 |  |  |  | 61.92 | 533.25 | 0.15 | 80 | 0
207.56 | 277.401 | 0 | 297 |  |  |  | 61.921 | 277.361 | 0 | 301 |  |  |  | 61.92 | 277.237 | 0 | 309 |  |  |  | 61.92 | 533.35 | 0.149 | 80 | 0
208.06 | 277.401 | 0 | 297 |  |  |  | 61.921 | 277.361 | 0 | 301 |  |  |  | 61.92 | 277.237 | 0 | 309 |  |  |  | 61.92 | 533.35 | 0.149 | 80 | 0
208.56 | 277.307 | 0 | 294 |  |  |  | 61.917 | 277.258 | 0 | 302 |  |  |  | 61.919 | 277.283 | 0 | 309 |  |  |  | 61.921 | 533.33 | 0.153 | 81 | 0
209.06 | 277.307 | 0 | 294 |  |  |  | 61.917 | 277.258 | 0 | 302 |  |  |  | 61.919 | 277.283 | 0 | 309 |  |  |  | 61.921 | 533.33 | 0.153 | 81 | 0
209.56 | 277.364 | 0 | 294 |  |  |  | 61.92 | 277.415 | 0 | 307 |  |  |  | 61.92 | 277.286 | 0 | 310 |  |  |  | 61.921 | 531.06 | 0.154 | 82 | 0
210.06 | 277.364 | 0 | 294 |  |  |  | 61.92 | 277.415 | 0 | 307 |  |  |  | 61.92 | 277.286 | 0 | 310 |  |  |  | 61.921 | 531.06 | 0.154 | 82 | 0
210.56 | 277.416 | 0 | 299 |  |  |  | 61.92 | 277.316 | 0 | 296 |  |  |  | 61.92 | 277.255 | 0 | 309 |  |  |  | 61.919 | 526.93 | 0.152 | 80 | 0
211.06 | 277.416 | 0 | 299 |  |  |  | 61.92 | 277.316 | 0 | 296 |  |  |  | 61.92 | 277.255 | 0 | 309 |  |  |  | 61.919 | 526.93 | 0.152 | 80 | 0
211.56 | 277.349 | 0 | 298 |  |  |  | 61.92 | 277.493 | 0 | 302 |  |  |  | 61.922 | 277.199 | 0 | 307 |  |  |  | 61.92 | 529.38 | 0.149 | 79 | 0
212.06 | 277.349 | 0 | 298 |  |  |  | 61.92 | 277.493 | 0 | 302 |  |  |  | 61.922 | 277.199 | 0 | 307 |  |  |  | 61.92 | 529.38 | 0.149 | 79 | 0
212.56 | 277.395 | 0 | 297 |  |  |  | 61.921 | 277.353 | 0 | 306 |  |  |  | 61.919 | 277.282 | 0 | 313 |  |  |  | 61.92 | 533.37 | 0.146 | 78 | 0
213.06 | 277.395 | 0 | 297 |  |  |  | 61.921 | 277.353 | 0 | 306 |  |  |  | 61.919 | 277.282 | 0 | 313 |  |  |  | 61.92 | 533.37 | 0.146 | 78 | 0
213.56 | 277.345 | 0 | 297 |  |  |  | 61.921 | 277.226 | 0 | 301 |  |  |  | 61.919 | 277.268 | 0 | 310 |  |  |  | 61.92 | 533.32 | 0.149 | 80 | 0
214.06 | 277.345 | 0 | 297 |  |  |  | 61.921 | 277.226 | 0 | 301 |  |  |  | 61.919 | 277.268 | 0 | 310 |  |  |  | 61.92 | 533.32 | 0.149 | 80 | 0
214.56 | 277.42 | 0 | 297 |  |  |  | 61.921 | 277.422 | 0 | 303 |  |  |  | 61.919 | 277.252 | 0 | 312 |  |  |  | 61.92 | 533.49 | 0.149 | 79 | 0
215.06 | 277.42 | 0 | 297 |  |  |  | 61.921 | 277.422 | 0 | 303 |  |  |  | 61.919 | 277.252 | 0 | 312 |  |  |  | 61.92 | 533.49 | 0.149 | 79 | 0
215.56 | 277.285 | 0 | 296 |  |  |  | 61.921 | 277.275 | 0 | 303 |  |  |  | 61.92 | 277.207 | 0 | 312 |  |  |  | 61.921 | 535.61 | 0.15 | 80 | 0
216.1 | 277.285 | 0 | 296 |  |  |  | 61.921 | 277.275 | 0 | 303 |  |  |  | 61.92 | 277.207 | 0 | 312 |  |  |  | 61.921 | 535.61 | 0.15 | 80 | 0
216.6 | 277.364 | 0 | 293 |  |  |  | 61.92 | 277.461 | 0 | 296 |  |  |  | 61.923 | 277.305 | 0 | 307 |  |  |  | 61.921 | 539.87 | 0.149 | 81 | 0
217.08 | 277.364 | 0 | 293 |  |  |  | 61.92 | 277.461 | 0 | 296 |  |  |  | 61.923 | 277.305 | 0 | 307 |  |  |  | 61.921 | 539.87 | 0.149 | 81 | 0
217.58 | 277.285 | 0 | 303 |  |  |  | 61.918 | 277.365 | 0 | 305 |  |  |  | 61.919 | 277.271 | 0 | 310 |  |  |  | 61.92 | 537.35 | 0.151 | 81 | 0
218.07 | 277.285 | 0 | 303 |  |  |  | 61.918 | 277.365 | 0 | 305 |  |  |  | 61.919 | 277.271 | 0 | 310 |  |  |  | 61.92 | 537.35 | 0.151 | 81 | 0
218.57 | 277.334 | 0 | 300 |  |  |  | 61.92 | 277.484 | 0 | 301 |  |  |  | 61.921 | 277.26 | 0 | 311 |  |  |  | 61.921 | 533.44 | 0.149 | 80 | 0
219.06 | 277.334 | 0 | 300 |  |  |  | 61.92 | 277.484 | 0 | 301 |  |  |  | 61.921 | 277.26 | 0 | 311 |  |  |  | 61.921 | 533.44 | 0.149 | 80 | 0
219.56 | 277.4 | 0 | 300 |  |  |  | 61.921 | 277.391 | 0 | 308 |  |  |  | 61.919 | 277.233 | 0 | 315 |  |  |  | 61.92 | 533.38 | 0.147 | 79 | 0
220.1 | 277.337 | 0 | 294 |  |  |  | 61.92 | 277.277 | 0 | 302 |  |  |  | 61.921 | 277.329 | 0 | 311 |  |  |  | 61.92 | 533.32 | 0.148 | 79 | 0
220.6 | 277.337 | 0 | 294 |  |  |  | 61.92 | 277.277 | 0 | 302 |  |  |  | 61.921 | 277.329 | 0 | 311 |  |  |  | 61.92 | 533.32 | 0.148 | 79 | 0
221.08 | 277.375 | 0 | 301 |  |  |  | 61.92 | 277.508 | 0 | 305 |  |  |  | 61.92 | 277.291 | 0 | 316 |  |  |  | 61.92 | 531.02 | 0.15 | 80 | 0
221.58 | 277.375 | 0 | 301 |  |  |  | 61.92 | 277.508 | 0 | 305 |  |  |  | 61.92 | 277.291 | 0 | 316 |  |  |  | 61.92 | 531.02 | 0.15 | 80 | 0
222.07 | 277.327 | 0 | 294 |  |  |  | 61.92 | 277.335 | 0 | 303 |  |  |  | 61.919 | 277.26 | 0 | 304 |  |  |  | 61.921 | 526.96 | 0.149 | 78 | 0
222.57 | 277.327 | 0 | 294 |  |  |  | 61.92 | 277.335 | 0 | 303 |  |  |  | 61.919 | 277.26 | 0 | 304 |  |  |  | 61.921 | 526.96 | 0.149 | 78 | 0
223.06 | 277.394 | 0 | 294 |  |  |  | 61.92 | 277.525 | 0 | 296 |  |  |  | 61.922 | 277.247 | 0 | 306 |  |  |  | 61.92 | 529.3 | 0.15 | 79 | 0
223.56 | 277.394 | 0 | 294 |  |  |  | 61.92 | 277.525 | 0 | 296 |  |  |  | 61.922 | 277.247 | 0 | 306 |  |  |  | 61.92 | 529.3 | 0.15 | 79 | 0
224.06 | 277.283 | 0 | 296 |  |  |  | 61.921 | 277.391 | 0 | 300 |  |  |  | 61.92 | 277.213 | 0 | 315 |  |  |  | 61.921 | 533.41 | 0.147 | 78 | 0
224.56 | 277.283 | 0 | 296 |  |  |  | 61.921 | 277.391 | 0 | 300 |  |  |  | 61.92 | 277.213 | 0 | 315 |  |  |  | 61.921 | 533.41 | 0.147 | 78 | 0
225.06 | 277.358 | 0 | 298 |  |  |  | 61.921 | 277.295 | 0 | 302 |  |  |  | 61.919 | 277.3 | 0 | 309 |  |  |  | 61.92 | 533.2 | 0.152 | 81 | 0
225.56 | 277.358 | 0 | 298 |  |  |  | 61.921 | 277.295 | 0 | 302 |  |  |  | 61.919 | 277.3 | 0 | 309 |  |  |  | 61.92 | 533.2 | 0.152 | 81 | 0
226.06 | 277.294 | 0 | 296 |  |  |  | 61.917 | 277.467 | 0 | 300 |  |  |  | 61.92 | 277.259 | 0 | 313 |  |  |  | 61.919 | 533.46 | 0.157 | 84 | 0
226.56 | 277.294 | 0 | 296 |  |  |  | 61.917 | 277.467 | 0 | 300 |  |  |  | 61.92 | 277.259 | 0 | 313 |  |  |  | 61.919 | 533.46 | 0.157 | 84 | 0
227.06 | 277.333 | 0 | 296 |  |  |  | 61.921 | 277.348 | 0 | 300 |  |  |  | 61.92 | 277.251 | 0 | 312 |  |  |  | 61.919 | 535.53 | 0.151 | 81 | 0
227.56 | 277.333 | 0 | 296 |  |  |  | 61.921 | 277.348 | 0 | 300 |  |  |  | 61.92 | 277.251 | 0 | 312 |  |  |  | 61.919 | 535.53 | 0.151 | 81 | 0
228.06 | 277.379 | 0 | 292 |  |  |  | 61.921 | 277.465 | 0 | 297 |  |  |  | 61.92 | 277.22 | 0 | 303 |  |  |  | 61.921 | 539.71 | 0.15 | 81 | 0
228.56 | 277.379 | 0 | 292 |  |  |  | 61.921 | 277.465 | 0 | 297 |  |  |  | 61.92 | 277.22 | 0 | 303 |  |  |  | 61.921 | 539.71 | 0.15 | 81 | 0
229.06 | 277.336 | 0 | 300 |  |  |  | 61.92 | 277.343 | 0 | 305 |  |  |  | 61.92 | 277.323 | 0 | 314 |  |  |  | 61.921 | 537.25 | 0.153 | 82 | 0
229.56 | 277.336 | 0 | 300 |  |  |  | 61.92 | 277.343 | 0 | 305 |  |  |  | 61.92 | 277.323 | 0 | 314 |  |  |  | 61.921 | 537.25 | 0.153 | 82 | 0
230.06 | 277.38 | 0 | 296 |  |  |  | 61.919 | 277.532 | 0 | 303 |  |  |  | 61.922 | 277.277 | 0 | 312 |  |  |  | 61.92 | 533.27 | 0.153 | 81 | 0
230.56 | 277.38 | 0 | 296 |  |  |  | 61.919 | 277.532 | 0 | 303 |  |  |  | 61.922 | 277.277 | 0 | 312 |  |  |  | 61.92 | 533.27 | 0.153 | 81 | 0
231.06 | 277.31 | 0 | 303 |  |  |  | 61.921 | 277.404 | 0 | 303 |  |  |  | 61.92 | 277.235 | 0 | 310 |  |  |  | 61.92 | 533.28 | 0.15 | 80 | 0
231.56 | 277.31 | 0 | 303 |  |  |  | 61.921 | 277.404 | 0 | 303 |  |  |  | 61.92 | 277.235 | 0 | 310 |  |  |  | 61.92 | 533.28 | 0.15 | 80 | 0
232.06 | 277.4 | 0 | 299 |  |  |  | 61.92 | 277.274 | 0 | 301 |  |  |  | 61.92 | 277.238 | 0 | 309 |  |  |  | 61.921 | 533.4 | 0.151 | 80 | 0
232.56 | 277.4 | 0 | 299 |  |  |  | 61.92 | 277.274 | 0 | 301 |  |  |  | 61.92 | 277.238 | 0 | 309 |  |  |  | 61.921 | 533.4 | 0.151 | 80 | 0
233.06 | 277.292 | 0 | 302 |  |  |  | 61.92 | 277.502 | 0 | 304 |  |  |  | 61.921 | 277.323 | 0 | 316 |  |  |  | 61.92 | 531.24 | 0.152 | 81 | 0
233.56 | 277.292 | 0 | 302 |  |  |  | 61.92 | 277.502 | 0 | 304 |  |  |  | 61.921 | 277.323 | 0 | 316 |  |  |  | 61.92 | 531.24 | 0.152 | 81 | 0
234.06 | 277.352 | 0 | 294 |  |  |  | 61.921 | 277.374 | 0 | 301 |  |  |  | 61.918 | 277.307 | 0 | 308 |  |  |  | 61.919 | 526.9 | 0.152 | 80 | 0
234.56 | 277.352 | 0 | 294 |  |  |  | 61.921 | 277.374 | 0 | 301 |  |  |  | 61.918 | 277.307 | 0 | 308 |  |  |  | 61.919 | 526.9 | 0.152 | 80 | 0
235.06 | 277.3 | 0 | 294 |  |  |  | 61.918 | 277.539 | 0 | 297 |  |  |  | 61.923 | 277.247 | 0 | 308 |  |  |  | 61.92 | 529.33 | 0.151 | 80 | 0
235.56 | 277.3 | 0 | 294 |  |  |  | 61.918 | 277.539 | 0 | 297 |  |  |  | 61.923 | 277.247 | 0 | 308 |  |  |  | 61.92 | 529.33 | 0.151 | 80 | 0
236.06 | 277.342 | 0 | 299 |  |  |  | 61.92 | 277.384 | 0 | 302 |  |  |  | 61.919 | 277.225 | 0 | 309 |  |  |  | 61.921 | 533.38 | 0.152 | 81 | 0
236.56 | 277.342 | 0 | 299 |  |  |  | 61.92 | 277.384 | 0 | 302 |  |  |  | 61.919 | 277.225 | 0 | 309 |  |  |  | 61.921 | 533.38 | 0.152 | 81 | 0
237.06 | 277.388 | 0 | 296 |  |  |  | 61.921 | 277.249 | 0 | 304 |  |  |  | 61.92 | 277.322 | 0 | 312 |  |  |  | 61.92 | 533.38 | 0.15 | 80 | 0
237.56 | 277.388 | 0 | 296 |  |  |  | 61.921 | 277.249 | 0 | 304 |  |  |  | 61.92 | 277.322 | 0 | 312 |  |  |  | 61.92 | 533.38 | 0.15 | 80 | 0
238.06 | 277.33 | 0 | 297 |  |  |  | 61.92 | 277.393 | 0 | 303 |  |  |  | 61.92 | 277.318 | 0 | 309 |  |  |  | 61.921 | 533.4 | 0.153 | 82 | 0
238.56 | 277.33 | 0 | 297 |  |  |  | 61.92 | 277.393 | 0 | 303 |  |  |  | 61.92 | 277.318 | 0 | 309 |  |  |  | 61.921 | 533.4 | 0.153 | 82 | 0
239.06 | 277.393 | 0 | 298 |  |  |  | 61.921 | 277.327 | 0 | 298 |  |  |  | 61.92 | 277.269 | 0 | 311 |  |  |  | 61.921 | 535.48 | 0.153 | 82 | 0
239.56 | 277.393 | 0 | 298 |  |  |  | 61.921 | 277.327 | 0 | 298 |  |  |  | 61.92 | 277.269 | 0 | 311 |  |  |  | 61.921 | 535.48 | 0.153 | 82 | 0
240.06 | 277.302 | 0 | 294 |  |  |  | 61.921 | 277.449 | 0 | 299 |  |  |  | 61.921 | 277.219 | 0 | 303 |  |  |  | 61.92 | 539.8 | 0.153 | 83 | 0
240.56 | 277.302 | 0 | 294 |  |  |  | 61.921 | 277.449 | 0 | 299 |  |  |  | 61.921 | 277.219 | 0 | 303 |  |  |  | 61.92 | 539.8 | 0.153 | 83 | 0
241.06 | 277.387 | 0 | 302 |  |  |  | 61.921 | 277.311 | 0 | 302 |  |  |  | 61.92 | 277.207 | 0 | 306 |  |  |  | 61.921 | 537.46 | 0.153 | 82 | 0
241.56 | 277.387 | 0 | 302 |  |  |  | 61.921 | 277.311 | 0 | 302 |  |  |  | 61.92 | 277.207 | 0 | 306 |  |  |  | 61.921 | 537.46 | 0.153 | 82 | 0
242.06 | 277.29 | 0 | 299 |  |  |  | 61.921 | 277.457 | 0 | 304 |  |  |  | 61.923 | 277.296 | 0 | 311 |  |  |  | 61.919 | 533.33 | 0.152 | 81 | 0
242.56 | 277.29 | 0 | 299 |  |  |  | 61.921 | 277.457 | 0 | 304 |  |  |  | 61.923 | 277.296 | 0 | 311 |  |  |  | 61.919 | 533.33 | 0.152 | 81 | 0
243.06 | 277.345 | 0 | 300 |  |  |  | 61.92 | 277.405 | 0 | 307 |  |  |  | 61.92 | 277.28 | 0 | 310 |  |  |  | 61.921 | 533.38 | 0.151 | 80 | 0
243.56 | 277.345 | 0 | 300 |  |  |  | 61.92 | 277.405 | 0 | 307 |  |  |  | 61.92 | 277.28 | 0 | 310 |  |  |  | 61.921 | 533.38 | 0.151 | 80 | 0
244.06 | 277.305 | 0 | 299 |  |  |  | 61.917 | 277.247 | 0 | 300 |  |  |  | 61.92 | 277.236 | 0 | 312 |  |  |  | 61.92 | 533.49 | 0.152 | 81 | 0
244.56 | 277.305 | 0 | 299 |  |  |  | 61.917 | 277.247 | 0 | 300 |  |  |  | 61.92 | 277.236 | 0 | 312 |  |  |  | 61.92 | 533.49 | 0.152 | 81 | 0
245.06 | 277.348 | 0 | 297 |  |  |  | 61.92 | 277.434 | 0 | 301 |  |  |  | 61.92 | 277.195 | 0 | 308 |  |  |  | 61.921 | 531.18 | 0.148 | 79 | 0
245.56 | 277.348 | 0 | 297 |  |  |  | 61.92 | 277.434 | 0 | 301 |  |  |  | 61.92 | 277.195 | 0 | 308 |  |  |  | 61.921 | 531.18 | 0.148 | 79 | 0
246.06 | 277.369 | 0 | 294 |  |  |  | 61.921 | 277.327 | 0 | 301 |  |  |  | 61.919 | 277.292 | 0 | 307 |  |  |  | 61.92 | 527 | 0.15 | 79 | 0
246.56 | 277.369 | 0 | 294 |  |  |  | 61.921 | 277.327 | 0 | 301 |  |  |  | 61.919 | 277.292 | 0 | 307 |  |  |  | 61.92 | 527 | 0.15 | 79 | 0
247.06 | 277.339 | 0 | 294 |  |  |  | 61.92 | 277.475 | 0 | 299 |  |  |  | 61.922 | 277.292 | 0 | 310 |  |  |  | 61.92 | 529.21 | 0.156 | 82 | 0
247.56 | 277.339 | 0 | 294 |  |  |  | 61.92 | 277.475 | 0 | 299 |  |  |  | 61.922 | 277.292 | 0 | 310 |  |  |  | 61.92 | 529.21 | 0.156 | 82 | 0
248.06 | 277.402 | 0 | 299 |  |  |  | 61.921 | 277.366 | 0 | 300 |  |  |  | 61.92 | 277.255 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.15 | 80 | 0
248.58 | 277.402 | 0 | 299 |  |  |  | 61.921 | 277.366 | 0 | 300 |  |  |  | 61.92 | 277.255 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.15 | 80 | 0
249.09 | 277.3 | 0 | 296 |  |  |  | 61.92 | 277.272 | 0 | 301 |  |  |  | 61.92 | 277.198 | 0 | 311 |  |  |  | 61.92 | 533.34 | 0.151 | 80 | 0
249.57 | 277.3 | 0 | 296 |  |  |  | 61.92 | 277.272 | 0 | 301 |  |  |  | 61.92 | 277.198 | 0 | 311 |  |  |  | 61.92 | 533.34 | 0.151 | 80 | 0
250.07 | 277.378 | 0 | 301 |  |  |  | 61.921 | 277.388 | 0 | 298 |  |  |  | 61.919 | 277.3 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.154 | 82 | 0
250.56 | 277.378 | 0 | 301 |  |  |  | 61.921 | 277.388 | 0 | 298 |  |  |  | 61.919 | 277.3 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.154 | 82 | 0
251.06 | 277.29 | 0 | 298 |  |  |  | 61.92 | 277.258 | 0 | 305 |  |  |  | 61.919 | 277.278 | 0 | 310 |  |  |  | 61.919 | 535.43 | 0.153 | 82 | 0
251.6 | 277.29 | 0 | 298 |  |  |  | 61.92 | 277.258 | 0 | 305 |  |  |  | 61.919 | 277.278 | 0 | 310 |  |  |  | 61.919 | 535.43 | 0.153 | 82 | 0
252.1 | 277.347 | 0 | 290 |  |  |  | 61.921 | 277.47 | 0 | 297 |  |  |  | 61.92 | 277.277 | 0 | 305 |  |  |  | 61.919 | 539.82 | 0.147 | 80 | 0
252.6 | 277.347 | 0 | 290 |  |  |  | 61.921 | 277.47 | 0 | 297 |  |  |  | 61.92 | 277.277 | 0 | 305 |  |  |  | 61.919 | 539.82 | 0.147 | 80 | 0
253.1 | 277.301 | 0 | 301 |  |  |  | 61.918 | 277.293 | 0 | 305 |  |  |  | 61.92 | 277.228 | 0 | 315 |  |  |  | 61.921 | 537.31 | 0.151 | 81 | 0
253.6 | 277.352 | 0 | 300 |  |  |  | 61.921 | 277.506 | 0 | 303 |  |  |  | 61.922 | 277.321 | 0 | 312 |  |  |  | 61.921 | 533.41 | 0.147 | 78 | 0
254.1 | 277.352 | 0 | 300 |  |  |  | 61.921 | 277.506 | 0 | 303 |  |  |  | 61.922 | 277.321 | 0 | 312 |  |  |  | 61.921 | 533.41 | 0.147 | 78 | 0
254.57 | 277.401 | 0 | 298 |  |  |  | 61.92 | 277.424 | 0 | 302 |  |  |  | 61.92 | 277.284 | 0 | 313 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 0
255.07 | 277.401 | 0 | 298 |  |  |  | 61.92 | 277.424 | 0 | 302 |  |  |  | 61.92 | 277.284 | 0 | 313 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 0
255.56 | 277.336 | 0 | 302 |  |  |  | 61.919 | 277.289 | 0 | 305 |  |  |  | 61.921 | 277.272 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.149 | 80 | 0
256.06 | 277.336 | 0 | 302 |  |  |  | 61.919 | 277.289 | 0 | 305 |  |  |  | 61.921 | 277.272 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.149 | 80 | 0
256.56 | 277.39 | 0 | 301 |  |  |  | 61.921 | 277.456 | 0 | 306 |  |  |  | 61.919 | 277.246 | 0 | 311 |  |  |  | 61.92 | 531.12 | 0.152 | 80 | 0
257.06 | 277.39 | 0 | 301 |  |  |  | 61.921 | 277.456 | 0 | 306 |  |  |  | 61.919 | 277.246 | 0 | 311 |  |  |  | 61.92 | 531.12 | 0.152 | 80 | 0
257.56 | 277.287 | 0 | 298 |  |  |  | 61.921 | 277.33 | 0 | 300 |  |  |  | 61.92 | 277.321 | 0 | 308 |  |  |  | 61.922 | 526.92 | 0.155 | 81 | 0
258.06 | 277.287 | 0 | 298 |  |  |  | 61.921 | 277.33 | 0 | 300 |  |  |  | 61.92 | 277.321 | 0 | 308 |  |  |  | 61.922 | 526.92 | 0.155 | 81 | 0
258.56 | 277.36 | 0 | 296 |  |  |  | 61.921 | 277.483 | 0 | 298 |  |  |  | 61.922 | 277.284 | 0 | 305 |  |  |  | 61.921 | 529.5 | 0.154 | 82 | 0
259.06 | 277.36 | 0 | 296 |  |  |  | 61.921 | 277.483 | 0 | 298 |  |  |  | 61.922 | 277.284 | 0 | 305 |  |  |  | 61.921 | 529.5 | 0.154 | 82 | 0
259.56 | 277.307 | 0 | 296 |  |  |  | 61.919 | 277.341 | 0 | 306 |  |  |  | 61.919 | 277.258 | 0 | 311 |  |  |  | 61.921 | 533.34 | 0.15 | 80 | 0
260.06 | 277.307 | 0 | 296 |  |  |  | 61.919 | 277.341 | 0 | 306 |  |  |  | 61.919 | 277.258 | 0 | 311 |  |  |  | 61.921 | 533.34 | 0.15 | 80 | 0
260.56 | 277.355 | 0 | 300 |  |  |  | 61.92 | 277.474 | 0 | 303 |  |  |  | 61.92 | 277.243 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.155 | 83 | 0
261.06 | 277.355 | 0 | 300 |  |  |  | 61.92 | 277.474 | 0 | 303 |  |  |  | 61.92 | 277.243 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.155 | 83 | 0
261.56 | 277.314 | 0 | 299 |  |  |  | 61.918 | 277.393 | 0 | 301 |  |  |  | 61.918 | 277.19 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 0
262.06 | 277.314 | 0 | 299 |  |  |  | 61.918 | 277.393 | 0 | 301 |  |  |  | 61.918 | 277.19 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 0
262.56 | 277.362 | 0 | 297 |  |  |  | 61.921 | 277.295 | 0 | 305 |  |  |  | 61.921 | 277.306 | 0 | 312 |  |  |  | 61.921 | 535.62 | 0.151 | 81 | 0
263.06 | 277.362 | 0 | 297 |  |  |  | 61.921 | 277.295 | 0 | 305 |  |  |  | 61.921 | 277.306 | 0 | 312 |  |  |  | 61.921 | 535.62 | 0.151 | 81 | 0
263.56 | 277.39 | 0 | 290 |  |  |  | 61.921 | 277.49 | 0 | 299 |  |  |  | 61.92 | 277.258 | 0 | 304 |  |  |  | 61.92 | 539.78 | 0.148 | 80 | 0
264.06 | 277.39 | 0 | 290 |  |  |  | 61.921 | 277.49 | 0 | 299 |  |  |  | 61.92 | 277.258 | 0 | 304 |  |  |  | 61.92 | 539.78 | 0.148 | 80 | 0
264.56 | 277.328 | 0 | 299 |  |  |  | 61.919 | 277.348 | 0 | 302 |  |  |  | 61.919 | 277.24 | 0 | 313 |  |  |  | 61.92 | 537.35 | 0.151 | 81 | 0
265.06 | 277.328 | 0 | 299 |  |  |  | 61.919 | 277.348 | 0 | 302 |  |  |  | 61.919 | 277.24 | 0 | 313 |  |  |  | 61.92 | 537.35 | 0.151 | 81 | 0
265.56 | 277.402 | 0 | 297 |  |  |  | 61.921 | 277.53 | 0 | 303 |  |  |  | 61.923 | 277.218 | 0 | 310 |  |  |  | 61.92 | 533.35 | 0.147 | 79 | 0
266.06 | 277.402 | 0 | 297 |  |  |  | 61.921 | 277.53 | 0 | 303 |  |  |  | 61.923 | 277.218 | 0 | 310 |  |  |  | 61.92 | 533.35 | 0.147 | 79 | 0
266.56 | 277.297 | 0 | 296 |  |  |  | 61.92 | 277.426 | 0 | 302 |  |  |  | 61.919 | 277.316 | 0 | 312 |  |  |  | 61.921 | 533.48 | 0.147 | 78 | 0
267.06 | 277.297 | 0 | 296 |  |  |  | 61.92 | 277.426 | 0 | 302 |  |  |  | 61.919 | 277.316 | 0 | 312 |  |  |  | 61.921 | 533.48 | 0.147 | 78 | 0
267.56 | 277.371 | 0 | 296 |  |  |  | 61.921 | 277.352 | 0 | 301 |  |  |  | 61.92 | 277.275 | 0 | 313 |  |  |  | 61.92 | 533.32 | 0.152 | 81 | 0
268.06 | 277.371 | 0 | 296 |  |  |  | 61.921 | 277.352 | 0 | 301 |  |  |  | 61.92 | 277.275 | 0 | 313 |  |  |  | 61.92 | 533.32 | 0.152 | 81 | 0
268.56 | 277.308 | 0 | 299 |  |  |  | 61.92 | 277.422 | 0 | 307 |  |  |  | 61.92 | 277.245 | 0 | 314 |  |  |  | 61.92 | 531.21 | 0.151 | 80 | 0
269.06 | 277.308 | 0 | 299 |  |  |  | 61.92 | 277.422 | 0 | 307 |  |  |  | 61.92 | 277.245 | 0 | 314 |  |  |  | 61.92 | 531.21 | 0.151 | 80 | 0
269.56 | 277.351 | 0 | 296 |  |  |  | 61.921 | 277.335 | 0 | 301 |  |  |  | 61.921 | 277.234 | 0 | 309 |  |  |  | 61.92 | 527.02 | 0.15 | 79 | 0
270.06 | 277.351 | 0 | 296 |  |  |  | 61.921 | 277.335 | 0 | 301 |  |  |  | 61.921 | 277.234 | 0 | 309 |  |  |  | 61.92 | 527.02 | 0.15 | 79 | 0
270.56 | 277.291 | 0 | 290 |  |  |  | 61.919 | 277.492 | 0 | 298 |  |  |  | 61.92 | 277.323 | 0 | 307 |  |  |  | 61.921 | 529.35 | 0.148 | 78 | 0
271.06 | 277.291 | 0 | 290 |  |  |  | 61.919 | 277.492 | 0 | 298 |  |  |  | 61.92 | 277.323 | 0 | 307 |  |  |  | 61.921 | 529.35 | 0.148 | 78 | 0
271.56 | 277.361 | 0 | 299 |  |  |  | 61.92 | 277.377 | 0 | 305 |  |  |  | 61.919 | 277.293 | 0 | 312 |  |  |  | 61.92 | 533.33 | 0.15 | 80 | 0
272.06 | 277.361 | 0 | 299 |  |  |  | 61.92 | 277.377 | 0 | 305 |  |  |  | 61.919 | 277.293 | 0 | 312 |  |  |  | 61.92 | 533.33 | 0.15 | 80 | 0
272.56 | 277.399 | 0 | 299 |  |  |  | 61.92 | 277.531 | 0 | 302 |  |  |  | 61.923 | 277.251 | 0 | 311 |  |  |  | 61.92 | 533.38 | 0.153 | 82 | 0
273.06 | 277.399 | 0 | 299 |  |  |  | 61.92 | 277.531 | 0 | 302 |  |  |  | 61.923 | 277.251 | 0 | 311 |  |  |  | 61.92 | 533.38 | 0.153 | 82 | 0
273.56 | 277.324 | 0 | 299 |  |  |  | 61.921 | 277.415 | 0 | 300 |  |  |  | 61.92 | 277.24 | 0 | 315 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 0
274.06 | 277.324 | 0 | 299 |  |  |  | 61.921 | 277.415 | 0 | 300 |  |  |  | 61.92 | 277.24 | 0 | 315 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 0
274.56 | 277.399 | 0 | 294 |  |  |  | 61.921 | 277.274 | 0 | 299 |  |  |  | 61.92 | 277.313 | 0 | 307 |  |  |  | 61.92 | 535.52 | 0.151 | 81 | 0
275.06 | 277.399 | 0 | 294 |  |  |  | 61.921 | 277.274 | 0 | 299 |  |  |  | 61.92 | 277.313 | 0 | 307 |  |  |  | 61.92 | 535.52 | 0.151 | 81 | 0
275.56 | 277.305 | 0 | 289 |  |  |  | 61.921 | 277.462 | 0 | 297 |  |  |  | 61.92 | 277.305 | 0 | 303 |  |  |  | 61.92 | 539.82 | 0.148 | 80 | 0
276.06 | 277.305 | 0 | 289 |  |  |  | 61.921 | 277.462 | 0 | 297 |  |  |  | 61.92 | 277.305 | 0 | 303 |  |  |  | 61.92 | 539.82 | 0.148 | 80 | 0
276.56 | 277.366 | 0 | 300 |  |  |  | 61.92 | 277.354 | 0 | 307 |  |  |  | 61.92 | 277.258 | 0 | 313 |  |  |  | 61.921 | 537.54 | 0.154 | 83 | 0
277.06 | 277.366 | 0 | 300 |  |  |  | 61.92 | 277.354 | 0 | 307 |  |  |  | 61.92 | 277.258 | 0 | 313 |  |  |  | 61.921 | 537.54 | 0.154 | 83 | 0
277.56 | 277.316 | 0 | 300 |  |  |  | 61.92 | 277.519 | 0 | 304 |  |  |  | 61.922 | 277.226 | 0 | 310 |  |  |  | 61.92 | 533.31 | 0.151 | 80 | 0
278.06 | 277.316 | 0 | 300 |  |  |  | 61.92 | 277.519 | 0 | 304 |  |  |  | 61.922 | 277.226 | 0 | 310 |  |  |  | 61.92 | 533.31 | 0.151 | 80 | 0
278.56 | 277.362 | 0 | 297 |  |  |  | 61.921 | 277.362 | 0 | 301 |  |  |  | 61.919 | 277.312 | 0 | 312 |  |  |  | 61.923 | 533.46 | 0.152 | 81 | 0
279.06 | 277.362 | 0 | 297 |  |  |  | 61.921 | 277.362 | 0 | 301 |  |  |  | 61.919 | 277.312 | 0 | 312 |  |  |  | 61.923 | 533.46 | 0.152 | 81 | 0
279.56 | 277.28 | 0 | 301 |  |  |  | 61.918 | 277.325 | 0 | 303 |  |  |  | 61.921 | 277.316 | 0 | 308 |  |  |  | 61.92 | 533.46 | 0.155 | 83 | 0
280.06 | 277.28 | 0 | 301 |  |  |  | 61.918 | 277.325 | 0 | 303 |  |  |  | 61.921 | 277.316 | 0 | 308 |  |  |  | 61.92 | 533.46 | 0.155 | 83 | 0
280.56 | 277.377 | 0 | 297 |  |  |  | 61.921 | 277.411 | 0 | 300 |  |  |  | 61.92 | 277.293 | 0 | 312 |  |  |  | 61.919 | 531.22 | 0.151 | 80 | 0
281.1 | 277.377 | 0 | 297 |  |  |  | 61.921 | 277.411 | 0 | 300 |  |  |  | 61.92 | 277.293 | 0 | 312 |  |  |  | 61.919 | 531.22 | 0.151 | 80 | 0
281.6 | 277.426 | 0 | 296 |  |  |  | 61.92 | 277.27 | 0 | 300 |  |  |  | 61.919 | 277.236 | 0 | 313 |  |  |  | 61.921 | 526.98 | 0.153 | 80 | 0
282.09 | 277.426 | 0 | 296 |  |  |  | 61.92 | 277.27 | 0 | 300 |  |  |  | 61.919 | 277.236 | 0 | 313 |  |  |  | 61.921 | 526.98 | 0.153 | 80 | 0
282.59 | 277.337 | 0 | 290 |  |  |  | 61.921 | 277.446 | 0 | 299 |  |  |  | 61.922 | 277.208 | 0 | 304 |  |  |  | 61.92 | 529.35 | 0.148 | 78 | 0
283.07 | 277.337 | 0 | 290 |  |  |  | 61.921 | 277.446 | 0 | 299 |  |  |  | 61.922 | 277.208 | 0 | 304 |  |  |  | 61.92 | 529.35 | 0.148 | 78 | 0
283.57 | 277.418 | 0 | 300 |  |  |  | 61.921 | 277.308 | 0 | 303 |  |  |  | 61.92 | 277.302 | 0 | 311 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 0
284.06 | 277.418 | 0 | 300 |  |  |  | 61.921 | 277.308 | 0 | 303 |  |  |  | 61.92 | 277.302 | 0 | 311 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 0
284.56 | 277.349 | 0 | 298 |  |  |  | 61.921 | 277.485 | 0 | 301 |  |  |  | 61.923 | 277.29 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.148 | 79 | 0
285.09 | 277.408 | 0 | 299 |  |  |  | 61.921 | 277.381 | 0 | 301 |  |  |  | 61.92 | 277.244 | 0 | 310 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 0
285.59 | 277.408 | 0 | 299 |  |  |  | 61.921 | 277.381 | 0 | 301 |  |  |  | 61.92 | 277.244 | 0 | 310 |  |  |  | 61.92 | 533.42 | 0.148 | 79 | 0
286.08 | 277.354 | 0 | 298 |  |  |  | 61.92 | 277.25 | 0 | 302 |  |  |  | 61.92 | 277.198 | 0 | 309 |  |  |  | 61.921 | 535.48 | 0.151 | 81 | 0
286.58 | 277.354 | 0 | 298 |  |  |  | 61.92 | 277.25 | 0 | 302 |  |  |  | 61.92 | 277.198 | 0 | 309 |  |  |  | 61.921 | 535.48 | 0.151 | 81 | 0
287.06 | 277.404 | 0 | 291 |  |  |  | 61.92 | 277.395 | 0 | 297 |  |  |  | 61.92 | 277.298 | 0 | 300 |  |  |  | 61.92 | 539.83 | 0.148 | 80 | 0
287.56 | 277.404 | 0 | 291 |  |  |  | 61.92 | 277.395 | 0 | 297 |  |  |  | 61.92 | 277.298 | 0 | 300 |  |  |  | 61.92 | 539.83 | 0.148 | 80 | 0
288.06 | 277.304 | 0 | 299 |  |  |  | 61.918 | 277.275 | 0 | 305 |  |  |  | 61.919 | 277.292 | 0 | 310 |  |  |  | 61.919 | 537.58 | 0.152 | 82 | 0
288.56 | 277.304 | 0 | 299 |  |  |  | 61.918 | 277.275 | 0 | 305 |  |  |  | 61.919 | 277.292 | 0 | 310 |  |  |  | 61.919 | 537.58 | 0.152 | 82 | 0
289.06 | 277.382 | 0 | 297 |  |  |  | 61.92 | 277.472 | 0 | 303 |  |  |  | 61.923 | 277.272 | 0 | 311 |  |  |  | 61.921 | 533.37 | 0.155 | 82 | 0
289.56 | 277.382 | 0 | 297 |  |  |  | 61.92 | 277.472 | 0 | 303 |  |  |  | 61.923 | 277.272 | 0 | 311 |  |  |  | 61.921 | 533.37 | 0.155 | 82 | 0
290.06 | 277.444 | 0 | 295 |  |  |  | 61.922 | 277.334 | 0 | 302 |  |  |  | 61.921 | 277.211 | 0 | 313 |  |  |  | 61.92 | 533.38 | 0.151 | 81 | 0
290.56 | 277.444 | 0 | 295 |  |  |  | 61.922 | 277.334 | 0 | 302 |  |  |  | 61.921 | 277.211 | 0 | 313 |  |  |  | 61.92 | 533.38 | 0.151 | 81 | 0
291.06 | 277.336 | 0 | 298 |  |  |  | 61.92 | 277.301 | 0 | 303 |  |  |  | 61.918 | 277.303 | 0 | 313 |  |  |  | 61.921 | 533.37 | 0.154 | 82 | 0
291.56 | 277.336 | 0 | 298 |  |  |  | 61.92 | 277.301 | 0 | 303 |  |  |  | 61.918 | 277.303 | 0 | 313 |  |  |  | 61.921 | 533.37 | 0.154 | 82 | 0
292.06 | 277.415 | 0 | 300 |  |  |  | 61.921 | 277.389 | 0 | 304 |  |  |  | 61.92 | 277.272 | 0 | 311 |  |  |  | 61.919 | 531.32 | 0.151 | 80 | 0
292.56 | 277.415 | 0 | 300 |  |  |  | 61.921 | 277.389 | 0 | 304 |  |  |  | 61.92 | 277.272 | 0 | 311 |  |  |  | 61.919 | 531.32 | 0.151 | 80 | 0
293.06 | 277.351 | 0 | 298 |  |  |  | 61.92 | 277.263 | 0 | 300 |  |  |  | 61.92 | 277.259 | 0 | 310 |  |  |  | 61.921 | 526.98 | 0.152 | 80 | 0
293.56 | 277.351 | 0 | 298 |  |  |  | 61.92 | 277.263 | 0 | 300 |  |  |  | 61.92 | 277.259 | 0 | 310 |  |  |  | 61.921 | 526.98 | 0.152 | 80 | 0
294.06 | 277.396 | 0 | 297 |  |  |  | 61.92 | 277.456 | 0 | 303 |  |  |  | 61.92 | 277.219 | 0 | 309 |  |  |  | 61.919 | 529.17 | 0.152 | 80 | 0
294.56 | 277.396 | 0 | 297 |  |  |  | 61.92 | 277.456 | 0 | 303 |  |  |  | 61.92 | 277.219 | 0 | 309 |  |  |  | 61.919 | 529.17 | 0.152 | 80 | 0
295.06 | 277.349 | 0 | 295 |  |  |  | 61.92 | 277.326 | 0 | 303 |  |  |  | 61.919 | 277.336 | 0 | 307 |  |  |  | 61.92 | 533.35 | 0.149 | 79 | 0
295.56 | 277.349 | 0 | 295 |  |  |  | 61.92 | 277.326 | 0 | 303 |  |  |  | 61.919 | 277.336 | 0 | 307 |  |  |  | 61.92 | 533.35 | 0.149 | 79 | 0
296.06 | 277.405 | 0 | 294 |  |  |  | 61.921 | 277.468 | 0 | 301 |  |  |  | 61.922 | 277.29 | 0 | 313 |  |  |  | 61.921 | 533.53 | 0.151 | 81 | 0
296.56 | 277.405 | 0 | 294 |  |  |  | 61.921 | 277.468 | 0 | 301 |  |  |  | 61.922 | 277.29 | 0 | 313 |  |  |  | 61.921 | 533.53 | 0.151 | 81 | 0
297.06 | 277.297 | 0 | 300 |  |  |  | 61.92 | 277.376 | 0 | 305 |  |  |  | 61.921 | 277.272 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.149 | 79 | 0
297.56 | 277.297 | 0 | 300 |  |  |  | 61.92 | 277.376 | 0 | 305 |  |  |  | 61.921 | 277.272 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.149 | 79 | 0
298.06 | 277.378 | 0 | 299 |  |  |  | 61.922 | 277.274 | 0 | 300 |  |  |  | 61.919 | 277.254 | 0 | 312 |  |  |  | 61.92 | 535.35 | 0.151 | 81 | 0
298.56 | 277.378 | 0 | 299 |  |  |  | 61.922 | 277.274 | 0 | 300 |  |  |  | 61.919 | 277.254 | 0 | 312 |  |  |  | 61.92 | 535.35 | 0.151 | 81 | 0
299.06 | 277.435 | 0 | 294 |  |  |  | 61.92 | 277.444 | 0 | 295 |  |  |  | 61.919 | 277.207 | 0 | 305 |  |  |  | 61.92 | 539.84 | 0.147 | 79 | 0
299.56 | 277.435 | 0 | 294 |  |  |  | 61.92 | 277.444 | 0 | 295 |  |  |  | 61.919 | 277.207 | 0 | 305 |  |  |  | 61.92 | 539.84 | 0.147 | 79 | 0
300.06 | 277.346 | 0 | 301 |  |  |  | 61.92 | 277.344 | 0 | 301 |  |  |  | 61.919 | 277.296 | 0 | 314 |  |  |  | 61.921 | 537.63 | 0.158 | 85 | 0
300.56 | 277.346 | 0 | 301 |  |  |  | 61.92 | 277.344 | 0 | 301 |  |  |  | 61.919 | 277.296 | 0 | 314 |  |  |  | 61.921 | 537.63 | 0.158 | 85 | 0
301.06 | 277.404 | 0 | 298 |  |  |  | 61.92 | 277.525 | 0 | 306 |  |  |  | 61.923 | 277.256 | 0 | 309 |  |  |  | 61.92 | 533.54 | 0.157 | 84 | 0
301.56 | 277.404 | 0 | 298 |  |  |  | 61.92 | 277.525 | 0 | 306 |  |  |  | 61.923 | 277.256 | 0 | 309 |  |  |  | 61.92 | 533.54 | 0.157 | 84 | 0
302.06 | 277.358 | 0 | 297 |  |  |  | 61.92 | 277.406 | 0 | 302 |  |  |  | 61.919 | 277.245 | 0 | 314 |  |  |  | 61.919 | 533.33 | 0.153 | 82 | 0
302.56 | 277.358 | 0 | 297 |  |  |  | 61.92 | 277.406 | 0 | 302 |  |  |  | 61.919 | 277.245 | 0 | 314 |  |  |  | 61.919 | 533.33 | 0.153 | 82 | 0
303.06 | 277.406 | 0 | 293 |  |  |  | 61.92 | 277.317 | 0 | 305 |  |  |  | 61.92 | 277.215 | 0 | 310 |  |  |  | 61.92 | 533.35 | 0.151 | 81 | 0
303.56 | 277.406 | 0 | 293 |  |  |  | 61.92 | 277.317 | 0 | 305 |  |  |  | 61.92 | 277.215 | 0 | 310 |  |  |  | 61.92 | 533.35 | 0.151 | 81 | 0
304.06 | 277.353 | 0 | 298 |  |  |  | 61.92 | 277.448 | 0 | 302 |  |  |  | 61.92 | 277.318 | 0 | 312 |  |  |  | 61.92 | 531.3 | 0.147 | 78 | 0
304.56 | 277.353 | 0 | 298 |  |  |  | 61.92 | 277.448 | 0 | 302 |  |  |  | 61.92 | 277.318 | 0 | 312 |  |  |  | 61.92 | 531.3 | 0.147 | 78 | 0
305.06 | 277.402 | 0 | 295 |  |  |  | 61.92 | 277.361 | 0 | 300 |  |  |  | 61.92 | 277.272 | 0 | 308 |  |  |  | 61.92 | 526.92 | 0.149 | 79 | 0
305.56 | 277.402 | 0 | 295 |  |  |  | 61.92 | 277.361 | 0 | 300 |  |  |  | 61.92 | 277.272 | 0 | 308 |  |  |  | 61.92 | 526.92 | 0.149 | 79 | 0
306.06 | 277.305 | 0 | 296 |  |  |  | 61.92 | 277.515 | 0 | 298 |  |  |  | 61.919 | 277.243 | 0 | 310 |  |  |  | 61.921 | 529.15 | 0.147 | 78 | 0
306.56 | 277.305 | 0 | 296 |  |  |  | 61.92 | 277.515 | 0 | 298 |  |  |  | 61.919 | 277.243 | 0 | 310 |  |  |  | 61.921 | 529.15 | 0.147 | 78 | 0
307.06 | 277.369 | 0 | 298 |  |  |  | 61.92 | 277.354 | 0 | 306 |  |  |  | 61.92 | 277.24 | 0 | 314 |  |  |  | 61.92 | 533.46 | 0.154 | 82 | 0
307.56 | 277.369 | 0 | 298 |  |  |  | 61.92 | 277.354 | 0 | 306 |  |  |  | 61.92 | 277.24 | 0 | 314 |  |  |  | 61.92 | 533.46 | 0.154 | 82 | 0
308.06 | 277.374 | 0 | 298 |  |  |  | 61.921 | 277.479 | 0 | 302 |  |  |  | 61.921 | 277.305 | 0 | 310 |  |  |  | 61.921 | 533.45 | 0.152 | 81 | 0
308.56 | 277.374 | 0 | 298 |  |  |  | 61.921 | 277.479 | 0 | 302 |  |  |  | 61.921 | 277.305 | 0 | 310 |  |  |  | 61.921 | 533.45 | 0.152 | 81 | 0
309.06 | 277.366 | 0 | 297 |  |  |  | 61.92 | 277.475 | 0 | 304 |  |  |  | 61.919 | 277.279 | 0 | 314 |  |  |  | 61.919 | 533.45 | 0.152 | 81 | 0
309.56 | 277.366 | 0 | 297 |  |  |  | 61.92 | 277.475 | 0 | 304 |  |  |  | 61.919 | 277.279 | 0 | 314 |  |  |  | 61.919 | 533.45 | 0.152 | 81 | 0
310.06 | 277.415 | 0 | 296 |  |  |  | 61.92 | 277.307 | 0 | 299 |  |  |  | 61.92 | 277.232 | 0 | 310 |  |  |  | 61.92 | 535.36 | 0.15 | 80 | 0
310.56 | 277.415 | 0 | 296 |  |  |  | 61.92 | 277.307 | 0 | 299 |  |  |  | 61.92 | 277.232 | 0 | 310 |  |  |  | 61.92 | 535.36 | 0.15 | 80 | 0
311.06 | 277.385 | 0 | 290 |  |  |  | 61.921 | 277.478 | 0 | 295 |  |  |  | 61.921 | 277.224 | 0 | 304 |  |  |  | 61.92 | 539.83 | 0.153 | 83 | 0
311.56 | 277.385 | 0 | 290 |  |  |  | 61.921 | 277.478 | 0 | 295 |  |  |  | 61.921 | 277.224 | 0 | 304 |  |  |  | 61.92 | 539.83 | 0.153 | 83 | 0
312.06 | 277.422 | 0 | 301 |  |  |  | 61.92 | 277.328 | 0 | 306 |  |  |  | 61.919 | 277.326 | 0 | 311 |  |  |  | 61.92 | 537.61 | 0.151 | 81 | 0
312.56 | 277.422 | 0 | 301 |  |  |  | 61.92 | 277.328 | 0 | 306 |  |  |  | 61.919 | 277.326 | 0 | 311 |  |  |  | 61.92 | 537.61 | 0.151 | 81 | 0
313.06 | 277.334 | 0 | 295 |  |  |  | 61.921 | 277.511 | 0 | 302 |  |  |  | 61.925 | 277.316 | 0 | 308 |  |  |  | 61.92 | 533.34 | 0.15 | 80 | 0
313.58 | 277.334 | 0 | 295 |  |  |  | 61.921 | 277.511 | 0 | 302 |  |  |  | 61.925 | 277.316 | 0 | 308 |  |  |  | 61.92 | 533.34 | 0.15 | 80 | 0
314.4 | 277.406 | 0 | 300 |  |  |  | 61.919 | 277.415 | 0 | 304 |  |  |  | 61.92 | 277.267 | 0 | 307 |  |  |  | 61.92 | 533.5 | 0.15 | 80 | 0
314.57 | 277.406 | 0 | 300 |  |  |  | 61.919 | 277.415 | 0 | 304 |  |  |  | 61.92 | 277.267 | 0 | 307 |  |  |  | 61.92 | 533.5 | 0.15 | 80 | 0
315.06 | 277.475 | 0 | 299 |  |  |  | 60.135 | 277.488 | 0 | 304 |  |  |  | 59.975 | 277.412 | 0 | 313 |  |  |  | 59.819 | 533.12 | 0.147 | 78 | 0
315.56 | 277.475 | 0 | 299 |  |  |  | 60.135 | 277.488 | 0 | 304 |  |  |  | 59.975 | 277.412 | 0 | 313 |  |  |  | 59.819 | 533.12 | 0.147 | 78 | 0
316.06 | 277.529 | 0 | 300 |  |  |  | 58.581 | 279.168 | 0 | 303 |  |  |  | 58.58 | 277.439 | 0 | 313 |  |  |  | 58.581 | 531.92 | 0.148 | 79 | 0
316.6 | 278.554 | 0 | 294 |  |  |  | 58.577 | 278.263 | 0 | 304 |  |  |  | 58.579 | 278.462 | 0 | 307 |  |  |  | 58.581 | 526.95 | 0.148 | 78 | 0
317.1 | 278.554 | 0 | 294 |  |  |  | 58.577 | 278.263 | 0 | 304 |  |  |  | 58.579 | 278.462 | 0 | 307 |  |  |  | 58.581 | 526.95 | 0.148 | 78 | 0
317.58 | 278.058 | 0 | 293 |  |  |  | 58.58 | 278.058 | 0 | 301 |  |  |  | 58.583 | 277.919 | 0 | 308 |  |  |  | 58.579 | 527.91 | 0.15 | 79 | 0
318.08 | 278.058 | 0 | 293 |  |  |  | 58.58 | 278.058 | 0 | 301 |  |  |  | 58.583 | 277.919 | 0 | 308 |  |  |  | 58.579 | 527.91 | 0.15 | 79 | 0
318.56 | 277.789 | 0 | 299 |  |  |  | 58.581 | 277.637 | 0 | 302 |  |  |  | 58.579 | 277.612 | 0 | 314 |  |  |  | 58.58 | 533.44 | 0.152 | 81 | 0
319.06 | 277.789 | 0 | 299 |  |  |  | 58.581 | 277.637 | 0 | 302 |  |  |  | 58.579 | 277.612 | 0 | 314 |  |  |  | 58.58 | 533.44 | 0.152 | 81 | 0
319.56 | 277.605 | 0 | 298 |  |  |  | 58.581 | 277.58 | 0 | 306 |  |  |  | 58.58 | 277.465 | 0 | 311 |  |  |  | 58.58 | 533.41 | 0.151 | 81 | 0
320.06 | 277.605 | 0 | 298 |  |  |  | 58.581 | 277.58 | 0 | 306 |  |  |  | 58.58 | 277.465 | 0 | 311 |  |  |  | 58.58 | 533.41 | 0.151 | 81 | 0
320.56 | 277.537 | 0 | 298 |  |  |  | 58.581 | 277.51 | 0 | 304 |  |  |  | 58.579 | 277.482 | 0 | 315 |  |  |  | 58.58 | 533.4 | 0.15 | 80 | 0
321.06 | 277.537 | 0 | 298 |  |  |  | 58.581 | 277.51 | 0 | 304 |  |  |  | 58.579 | 277.482 | 0 | 315 |  |  |  | 58.58 | 533.4 | 0.15 | 80 | 0
321.56 | 277.41 | 0 | 301 |  |  |  | 58.58 | 277.365 | 0 | 303 |  |  |  | 58.58 | 277.384 | 0 | 312 |  |  |  | 58.58 | 533.39 | 0.152 | 81 | 0
322.06 | 277.41 | 0 | 301 |  |  |  | 58.58 | 277.365 | 0 | 303 |  |  |  | 58.58 | 277.384 | 0 | 312 |  |  |  | 58.58 | 533.39 | 0.152 | 81 | 0
322.56 | 277.481 | 0 | 295 |  |  |  | 58.581 | 277.489 | 0 | 303 |  |  |  | 58.58 | 277.351 | 0 | 308 |  |  |  | 58.581 | 539.38 | 0.15 | 81 | 0
323.06 | 277.481 | 0 | 295 |  |  |  | 58.581 | 277.489 | 0 | 303 |  |  |  | 58.58 | 277.351 | 0 | 308 |  |  |  | 58.581 | 539.38 | 0.15 | 81 | 0
323.56 | 277.376 | 0 | 296 |  |  |  | 58.581 | 277.383 | 0 | 298 |  |  |  | 58.58 | 277.301 | 0 | 304 |  |  |  | 58.58 | 539.83 | 0.151 | 81 | 0
324.06 | 277.376 | 0 | 296 |  |  |  | 58.581 | 277.383 | 0 | 298 |  |  |  | 58.58 | 277.301 | 0 | 304 |  |  |  | 58.58 | 539.83 | 0.151 | 81 | 0
324.58 | 277.436 | 0 | 298 |  |  |  | 58.58 | 277.528 | 0 | 303 |  |  |  | 58.583 | 277.375 | 0 | 315 |  |  |  | 58.58 | 534.22 | 0.152 | 81 | 0
325.06 | 277.436 | 0 | 298 |  |  |  | 58.58 | 277.528 | 0 | 303 |  |  |  | 58.583 | 277.375 | 0 | 315 |  |  |  | 58.58 | 534.22 | 0.152 | 81 | 0
325.56 | 276.048 | 0 | 299 |  |  |  | 61.917 | 276 | 0 | 302 |  |  |  | 61.921 | 276.117 | 0 | 308 |  |  |  | 61.921 | 533.43 | 0.153 | 82 | 0
326.06 | 276.048 | 0 | 299 |  |  |  | 61.917 | 276 | 0 | 302 |  |  |  | 61.921 | 276.117 | 0 | 308 |  |  |  | 61.921 | 533.43 | 0.153 | 82 | 0
326.56 | 276.672 | 0 | 298 |  |  |  | 61.921 | 276.498 | 0 | 302 |  |  |  | 61.92 | 276.624 | 0 | 311 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 0
327.06 | 276.672 | 0 | 298 |  |  |  | 61.921 | 276.498 | 0 | 302 |  |  |  | 61.92 | 276.624 | 0 | 311 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 0
327.56 | 277.014 | 0 | 298 |  |  |  | 61.921 | 276.99 | 0 | 304 |  |  |  | 61.919 | 276.898 | 0 | 311 |  |  |  | 61.921 | 533.33 | 0.15 | 80 | 0
328.06 | 277.014 | 0 | 298 |  |  |  | 61.921 | 276.99 | 0 | 304 |  |  |  | 61.919 | 276.898 | 0 | 311 |  |  |  | 61.921 | 533.33 | 0.15 | 80 | 0
328.56 | 277.169 | 0 | 299 |  |  |  | 61.921 | 277.074 | 0 | 304 |  |  |  | 61.92 | 277.165 | 0 | 312 |  |  |  | 61.92 | 528.2 | 0.149 | 79 | 0
329.06 | 277.169 | 0 | 299 |  |  |  | 61.921 | 277.074 | 0 | 304 |  |  |  | 61.92 | 277.165 | 0 | 312 |  |  |  | 61.92 | 528.2 | 0.149 | 79 | 0
329.56 | 277.269 | 0 | 295 |  |  |  | 61.921 | 277.37 | 0 | 302 |  |  |  | 61.922 | 277.18 | 0 | 309 |  |  |  | 61.919 | 526.99 | 0.155 | 81 | 0
330.06 | 277.269 | 0 | 295 |  |  |  | 61.921 | 277.37 | 0 | 302 |  |  |  | 61.922 | 277.18 | 0 | 309 |  |  |  | 61.919 | 526.99 | 0.155 | 81 | 0
330.56 | 277.214 | 0 | 292 |  |  |  | 61.92 | 277.281 | 0 | 302 |  |  |  | 61.92 | 277.195 | 0 | 306 |  |  |  | 61.92 | 532.28 | 0.153 | 81 | 0
331.06 | 277.214 | 0 | 292 |  |  |  | 61.92 | 277.281 | 0 | 302 |  |  |  | 61.92 | 277.195 | 0 | 306 |  |  |  | 61.92 | 532.28 | 0.153 | 81 | 0
331.56 | 277.302 | 0 | 297 |  |  |  | 61.919 | 277.308 | 0 | 302 |  |  |  | 61.919 | 277.2 | 0 | 313 |  |  |  | 61.92 | 533.46 | 0.153 | 82 | 0
332.06 | 277.302 | 0 | 297 |  |  |  | 61.919 | 277.308 | 0 | 302 |  |  |  | 61.919 | 277.2 | 0 | 313 |  |  |  | 61.92 | 533.46 | 0.153 | 82 | 0
332.56 | 277.25 | 0 | 298 |  |  |  | 61.92 | 277.4 | 0 | 303 |  |  |  | 61.919 | 277.187 | 0 | 313 |  |  |  | 61.921 | 533.36 | 0.151 | 80 | 0
333.06 | 277.25 | 0 | 298 |  |  |  | 61.92 | 277.4 | 0 | 303 |  |  |  | 61.919 | 277.187 | 0 | 313 |  |  |  | 61.921 | 533.36 | 0.151 | 80 | 0
333.56 | 277.29 | 0 | 301 |  |  |  | 61.921 | 277.339 | 0 | 305 |  |  |  | 61.919 | 277.258 | 0 | 310 |  |  |  | 61.92 | 533.27 | 0.152 | 81 | 0
334.06 | 277.29 | 0 | 301 |  |  |  | 61.921 | 277.339 | 0 | 305 |  |  |  | 61.919 | 277.258 | 0 | 310 |  |  |  | 61.92 | 533.27 | 0.152 | 81 | 0
334.56 | 277.27 | 0 | 297 |  |  |  | 61.92 | 277.45 | 0 | 300 |  |  |  | 61.921 | 277.249 | 0 | 312 |  |  |  | 61.921 | 538.56 | 0.148 | 80 | 0
335.06 | 277.27 | 0 | 297 |  |  |  | 61.92 | 277.45 | 0 | 300 |  |  |  | 61.921 | 277.249 | 0 | 312 |  |  |  | 61.921 | 538.56 | 0.148 | 80 | 0
335.56 | 277.324 | 0 | 292 |  |  |  | 61.921 | 277.358 | 0 | 296 |  |  |  | 61.92 | 277.238 | 0 | 306 |  |  |  | 61.921 | 539.83 | 0.149 | 81 | 0
336.06 | 277.324 | 0 | 292 |  |  |  | 61.921 | 277.358 | 0 | 296 |  |  |  | 61.92 | 277.238 | 0 | 306 |  |  |  | 61.921 | 539.83 | 0.149 | 81 | 0
336.56 | 277.349 | 0 | 303 |  |  |  | 61.92 | 277.53 | 0 | 306 |  |  |  | 61.922 | 277.19 | 0 | 317 |  |  |  | 61.92 | 534.41 | 0.15 | 80 | 0
337.06 | 277.349 | 0 | 303 |  |  |  | 61.92 | 277.53 | 0 | 306 |  |  |  | 61.922 | 277.19 | 0 | 317 |  |  |  | 61.92 | 534.41 | 0.15 | 80 | 0
337.56 | 277.311 | 0 | 298 |  |  |  | 61.92 | 277.428 | 0 | 302 |  |  |  | 61.919 | 277.305 | 0 | 310 |  |  |  | 61.92 | 533.38 | 0.148 | 79 | 0
338.06 | 277.311 | 0 | 298 |  |  |  | 61.92 | 277.428 | 0 | 302 |  |  |  | 61.919 | 277.305 | 0 | 310 |  |  |  | 61.92 | 533.38 | 0.148 | 79 | 0
338.56 | 277.375 | 0 | 295 |  |  |  | 61.92 | 277.29 | 0 | 305 |  |  |  | 61.92 | 277.261 | 0 | 310 |  |  |  | 61.921 | 533.43 | 0.149 | 80 | 0
339.06 | 277.375 | 0 | 295 |  |  |  | 61.92 | 277.29 | 0 | 305 |  |  |  | 61.92 | 277.261 | 0 | 310 |  |  |  | 61.921 | 533.43 | 0.149 | 80 | 0
339.56 | 277.291 | 0 | 296 |  |  |  | 61.921 | 277.465 | 0 | 301 |  |  |  | 61.92 | 277.254 | 0 | 316 |  |  |  | 61.919 | 533.36 | 0.147 | 79 | 0
340.06 | 277.291 | 0 | 296 |  |  |  | 61.921 | 277.465 | 0 | 301 |  |  |  | 61.92 | 277.254 | 0 | 316 |  |  |  | 61.919 | 533.36 | 0.147 | 79 | 0
340.56 | 277.371 | 0 | 297 |  |  |  | 61.92 | 277.318 | 0 | 302 |  |  |  | 61.921 | 277.231 | 0 | 310 |  |  |  | 61.92 | 528.31 | 0.147 | 78 | 0
341.06 | 277.371 | 0 | 297 |  |  |  | 61.92 | 277.318 | 0 | 302 |  |  |  | 61.921 | 277.231 | 0 | 310 |  |  |  | 61.92 | 528.31 | 0.147 | 78 | 0
341.56 | 277.294 | 0 | 298 |  |  |  | 61.919 | 277.513 | 0 | 299 |  |  |  | 61.922 | 277.306 | 0 | 305 |  |  |  | 61.92 | 526.92 | 0.148 | 78 | 0
342.06 | 277.294 | 0 | 298 |  |  |  | 61.919 | 277.513 | 0 | 299 |  |  |  | 61.922 | 277.306 | 0 | 305 |  |  |  | 61.92 | 526.92 | 0.148 | 78 | 0
342.56 | 277.338 | 0 | 297 |  |  |  | 61.921 | 277.419 | 0 | 300 |  |  |  | 61.919 | 277.263 | 0 | 313 |  |  |  | 61.921 | 532.31 | 0.147 | 78 | 0
343.06 | 277.338 | 0 | 297 |  |  |  | 61.921 | 277.419 | 0 | 300 |  |  |  | 61.919 | 277.263 | 0 | 313 |  |  |  | 61.921 | 532.31 | 0.147 | 78 | 0
343.56 | 277.301 | 0 | 298 |  |  |  | 61.921 | 277.361 | 0 | 301 |  |  |  | 61.919 | 277.231 | 0 | 311 |  |  |  | 61.92 | 533.42 | 0.155 | 83 | 0
344.06 | 277.301 | 0 | 298 |  |  |  | 61.921 | 277.361 | 0 | 301 |  |  |  | 61.919 | 277.231 | 0 | 311 |  |  |  | 61.92 | 533.42 | 0.155 | 83 | 0
344.56 | 277.371 | 0 | 302 |  |  |  | 61.92 | 277.443 | 0 | 305 |  |  |  | 61.92 | 277.222 | 0 | 312 |  |  |  | 61.92 | 533.5 | 0.151 | 81 | 0
345.09 | 277.371 | 0 | 302 |  |  |  | 61.92 | 277.443 | 0 | 305 |  |  |  | 61.92 | 277.222 | 0 | 312 |  |  |  | 61.92 | 533.5 | 0.151 | 81 | 0
345.59 | 277.394 | 0 | 295 |  |  |  | 61.92 | 277.3 | 0 | 306 |  |  |  | 61.919 | 277.32 | 0 | 310 |  |  |  | 61.92 | 533.36 | 0.151 | 80 | 0
346.07 | 277.394 | 0 | 295 |  |  |  | 61.92 | 277.3 | 0 | 306 |  |  |  | 61.919 | 277.32 | 0 | 310 |  |  |  | 61.92 | 533.36 | 0.151 | 80 | 0
346.57 | 277.361 | 0 | 296 |  |  |  | 61.921 | 277.511 | 0 | 300 |  |  |  | 61.92 | 277.29 | 0 | 310 |  |  |  | 61.92 | 538.36 | 0.151 | 81 | 0
347.06 | 277.361 | 0 | 296 |  |  |  | 61.921 | 277.511 | 0 | 300 |  |  |  | 61.92 | 277.29 | 0 | 310 |  |  |  | 61.92 | 538.36 | 0.151 | 81 | 0
347.56 | 277.429 | 0 | 293 |  |  |  | 61.921 | 277.359 | 0 | 296 |  |  |  | 61.919 | 277.247 | 0 | 301 |  |  |  | 61.92 | 539.86 | 0.146 | 79 | 0
348.09 | 277.309 | 0 | 300 |  |  |  | 61.919 | 277.494 | 0 | 306 |  |  |  | 61.922 | 277.236 | 0 | 310 |  |  |  | 61.92 | 534.63 | 0.15 | 80 | 0
348.59 | 277.309 | 0 | 300 |  |  |  | 61.919 | 277.494 | 0 | 306 |  |  |  | 61.922 | 277.236 | 0 | 310 |  |  |  | 61.92 | 534.63 | 0.15 | 80 | 0
349.08 | 277.38 | 0 | 298 |  |  |  | 61.921 | 277.41 | 0 | 305 |  |  |  | 61.919 | 277.216 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.149 | 79 | 0
349.58 | 277.38 | 0 | 298 |  |  |  | 61.921 | 277.41 | 0 | 305 |  |  |  | 61.919 | 277.216 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.149 | 79 | 0
350.06 | 277.322 | 0 | 299 |  |  |  | 61.921 | 277.292 | 0 | 299 |  |  |  | 61.92 | 277.308 | 0 | 312 |  |  |  | 61.921 | 533.51 | 0.153 | 82 | 0
350.56 | 277.322 | 0 | 299 |  |  |  | 61.921 | 277.292 | 0 | 299 |  |  |  | 61.92 | 277.308 | 0 | 312 |  |  |  | 61.921 | 533.51 | 0.153 | 82 | 0
351.06 | 277.37 | 0 | 300 |  |  |  | 61.921 | 277.457 | 0 | 302 |  |  |  | 61.92 | 277.251 | 0 | 307 |  |  |  | 61.919 | 533.47 | 0.155 | 83 | 0
351.56 | 277.37 | 0 | 300 |  |  |  | 61.921 | 277.457 | 0 | 302 |  |  |  | 61.92 | 277.251 | 0 | 307 |  |  |  | 61.919 | 533.47 | 0.155 | 83 | 0
352.06 | 277.317 | 0 | 298 |  |  |  | 61.92 | 277.328 | 0 | 298 |  |  |  | 61.919 | 277.212 | 0 | 313 |  |  |  | 61.92 | 528.44 | 0.151 | 80 | 0
352.56 | 277.317 | 0 | 298 |  |  |  | 61.92 | 277.328 | 0 | 298 |  |  |  | 61.919 | 277.212 | 0 | 313 |  |  |  | 61.92 | 528.44 | 0.151 | 80 | 0
353.06 | 277.391 | 0 | 297 |  |  |  | 61.921 | 277.487 | 0 | 300 |  |  |  | 61.923 | 277.209 | 0 | 309 |  |  |  | 61.919 | 526.97 | 0.156 | 82 | 0
353.56 | 277.391 | 0 | 297 |  |  |  | 61.921 | 277.487 | 0 | 300 |  |  |  | 61.923 | 277.209 | 0 | 309 |  |  |  | 61.919 | 526.97 | 0.156 | 82 | 0
354.06 | 277.421 | 0 | 295 |  |  |  | 61.92 | 277.33 | 0 | 302 |  |  |  | 61.921 | 277.311 | 0 | 314 |  |  |  | 61.921 | 532.11 | 0.15 | 80 | 0
354.56 | 277.421 | 0 | 295 |  |  |  | 61.92 | 277.33 | 0 | 302 |  |  |  | 61.921 | 277.311 | 0 | 314 |  |  |  | 61.921 | 532.11 | 0.15 | 80 | 0
355.06 | 277.337 | 0 | 295 |  |  |  | 61.921 | 277.282 | 0 | 306 |  |  |  | 61.92 | 277.291 | 0 | 314 |  |  |  | 61.921 | 533.38 | 0.151 | 81 | 0
355.56 | 277.337 | 0 | 295 |  |  |  | 61.921 | 277.282 | 0 | 306 |  |  |  | 61.92 | 277.291 | 0 | 314 |  |  |  | 61.921 | 533.38 | 0.151 | 81 | 0
356.06 | 277.43 | 0 | 297 |  |  |  | 61.921 | 277.419 | 0 | 301 |  |  |  | 61.919 | 277.24 | 0 | 310 |  |  |  | 61.92 | 533.34 | 0.152 | 81 | 0
356.56 | 277.43 | 0 | 297 |  |  |  | 61.921 | 277.419 | 0 | 301 |  |  |  | 61.919 | 277.24 | 0 | 310 |  |  |  | 61.92 | 533.34 | 0.152 | 81 | 0
357.06 | 277.317 | 0 | 296 |  |  |  | 61.919 | 277.3 | 0 | 304 |  |  |  | 61.92 | 277.205 | 0 | 312 |  |  |  | 61.921 | 533.42 | 0.153 | 82 | 0
357.56 | 277.317 | 0 | 296 |  |  |  | 61.919 | 277.3 | 0 | 304 |  |  |  | 61.92 | 277.205 | 0 | 312 |  |  |  | 61.921 | 533.42 | 0.153 | 82 | 0
358.06 | 277.358 | 0 | 298 |  |  |  | 61.921 | 277.446 | 0 | 303 |  |  |  | 61.92 | 277.289 | 0 | 307 |  |  |  | 61.92 | 538.35 | 0.157 | 84 | 0
358.56 | 277.358 | 0 | 298 |  |  |  | 61.921 | 277.446 | 0 | 303 |  |  |  | 61.92 | 277.289 | 0 | 307 |  |  |  | 61.92 | 538.35 | 0.157 | 84 | 0
359.06 | 277.335 | 0 | 288 |  |  |  | 61.921 | 277.324 | 0 | 298 |  |  |  | 61.919 | 277.284 | 0 | 306 |  |  |  | 61.92 | 539.83 | 0.15 | 81 | 0
359.56 | 277.335 | 0 | 288 |  |  |  | 61.921 | 277.324 | 0 | 298 |  |  |  | 61.919 | 277.284 | 0 | 306 |  |  |  | 61.92 | 539.83 | 0.15 | 81 | 0
360.06 | 277.368 | 0 | 298 |  |  |  | 61.92 | 277.49 | 0 | 302 |  |  |  | 61.923 | 277.248 | 0 | 309 |  |  |  | 61.921 | 534.58 | 0.153 | 82 | 0
360.56 | 277.368 | 0 | 298 |  |  |  | 61.92 | 277.49 | 0 | 302 |  |  |  | 61.923 | 277.248 | 0 | 309 |  |  |  | 61.921 | 534.58 | 0.153 | 82 | 0
361.06 | 277.315 | 0 | 295 |  |  |  | 61.92 | 277.382 | 0 | 302 |  |  |  | 61.919 | 277.199 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.155 | 83 | 0
361.56 | 277.315 | 0 | 295 |  |  |  | 61.92 | 277.382 | 0 | 302 |  |  |  | 61.919 | 277.199 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.155 | 83 | 0
362.06 | 277.402 | 0 | 299 |  |  |  | 61.921 | 277.282 | 0 | 300 |  |  |  | 61.919 | 277.287 | 0 | 309 |  |  |  | 61.923 | 533.48 | 0.153 | 81 | 0
362.56 | 277.402 | 0 | 299 |  |  |  | 61.921 | 277.282 | 0 | 300 |  |  |  | 61.919 | 277.287 | 0 | 309 |  |  |  | 61.923 | 533.48 | 0.153 | 81 | 0
363.06 | 277.405 | 0 | 297 |  |  |  | 61.921 | 277.414 | 0 | 302 |  |  |  | 61.919 | 277.276 | 0 | 312 |  |  |  | 61.92 | 533.51 | 0.152 | 81 | 0
363.56 | 277.405 | 0 | 297 |  |  |  | 61.921 | 277.414 | 0 | 302 |  |  |  | 61.919 | 277.276 | 0 | 312 |  |  |  | 61.92 | 533.51 | 0.152 | 81 | 0
364.06 | 277.35 | 0 | 299 |  |  |  | 61.921 | 277.291 | 0 | 304 |  |  |  | 61.92 | 277.267 | 0 | 310 |  |  |  | 61.92 | 528.51 | 0.151 | 80 | 0
364.56 | 277.35 | 0 | 299 |  |  |  | 61.921 | 277.291 | 0 | 304 |  |  |  | 61.92 | 277.267 | 0 | 310 |  |  |  | 61.92 | 528.51 | 0.151 | 80 | 0
365.06 | 277.418 | 0 | 297 |  |  |  | 61.92 | 277.486 | 0 | 303 |  |  |  | 61.923 | 277.225 | 0 | 312 |  |  |  | 61.921 | 526.99 | 0.148 | 78 | 0
365.56 | 277.418 | 0 | 297 |  |  |  | 61.92 | 277.486 | 0 | 303 |  |  |  | 61.923 | 277.225 | 0 | 312 |  |  |  | 61.921 | 526.99 | 0.148 | 78 | 0
366.06 | 277.326 | 0 | 299 |  |  |  | 61.921 | 277.382 | 0 | 300 |  |  |  | 61.919 | 277.215 | 0 | 311 |  |  |  | 61.919 | 532.18 | 0.152 | 81 | 0
366.56 | 277.326 | 0 | 299 |  |  |  | 61.921 | 277.382 | 0 | 300 |  |  |  | 61.919 | 277.215 | 0 | 311 |  |  |  | 61.919 | 532.18 | 0.152 | 81 | 0
367.06 | 277.375 | 0 | 299 |  |  |  | 61.92 | 277.295 | 0 | 303 |  |  |  | 61.92 | 277.29 | 0 | 311 |  |  |  | 61.921 | 533.38 | 0.15 | 80 | 0
367.56 | 277.375 | 0 | 299 |  |  |  | 61.92 | 277.295 | 0 | 303 |  |  |  | 61.92 | 277.29 | 0 | 311 |  |  |  | 61.921 | 533.38 | 0.15 | 80 | 0
368.06 | 277.329 | 0 | 300 |  |  |  | 61.921 | 277.402 | 0 | 302 |  |  |  | 61.92 | 277.279 | 0 | 307 |  |  |  | 61.919 | 533.4 | 0.149 | 79 | 0
368.56 | 277.329 | 0 | 300 |  |  |  | 61.921 | 277.402 | 0 | 302 |  |  |  | 61.92 | 277.279 | 0 | 307 |  |  |  | 61.919 | 533.4 | 0.149 | 79 | 0
369.06 | 277.392 | 0 | 296 |  |  |  | 61.92 | 277.272 | 0 | 303 |  |  |  | 61.919 | 277.257 | 0 | 308 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 0
369.56 | 277.392 | 0 | 296 |  |  |  | 61.92 | 277.272 | 0 | 303 |  |  |  | 61.919 | 277.257 | 0 | 308 |  |  |  | 61.92 | 533.44 | 0.152 | 81 | 0
370.06 | 277.3 | 0 | 297 |  |  |  | 61.921 | 277.461 | 0 | 296 |  |  |  | 61.921 | 277.206 | 0 | 306 |  |  |  | 61.919 | 538.32 | 0.147 | 79 | 0
370.56 | 277.3 | 0 | 297 |  |  |  | 61.921 | 277.461 | 0 | 296 |  |  |  | 61.921 | 277.206 | 0 | 306 |  |  |  | 61.919 | 538.32 | 0.147 | 79 | 0
371.06 | 277.388 | 0 | 293 |  |  |  | 61.92 | 277.345 | 0 | 298 |  |  |  | 61.92 | 277.306 | 0 | 307 |  |  |  | 61.921 | 539.86 | 0.151 | 81 | 0
371.56 | 277.388 | 0 | 293 |  |  |  | 61.92 | 277.345 | 0 | 298 |  |  |  | 61.92 | 277.306 | 0 | 307 |  |  |  | 61.921 | 539.86 | 0.151 | 81 | 0
372.06 | 277.356 | 0 | 300 |  |  |  | 61.92 | 277.482 | 0 | 301 |  |  |  | 61.922 | 277.289 | 0 | 310 |  |  |  | 61.921 | 534.76 | 0.144 | 77 | 0
372.56 | 277.356 | 0 | 300 |  |  |  | 61.92 | 277.482 | 0 | 301 |  |  |  | 61.922 | 277.289 | 0 | 310 |  |  |  | 61.921 | 534.76 | 0.144 | 77 | 0
373.06 | 277.327 | 0 | 299 |  |  |  | 61.921 | 277.395 | 0 | 304 |  |  |  | 61.919 | 277.279 | 0 | 310 |  |  |  | 61.921 | 533.44 | 0.15 | 80 | 0
373.56 | 277.327 | 0 | 299 |  |  |  | 61.921 | 277.395 | 0 | 304 |  |  |  | 61.919 | 277.279 | 0 | 310 |  |  |  | 61.921 | 533.44 | 0.15 | 80 | 0
374.06 | 277.41 | 0 | 297 |  |  |  | 61.921 | 277.268 | 0 | 302 |  |  |  | 61.919 | 277.237 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 0
374.56 | 277.41 | 0 | 297 |  |  |  | 61.921 | 277.268 | 0 | 302 |  |  |  | 61.919 | 277.237 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 0
375.06 | 277.329 | 0 | 301 |  |  |  | 61.92 | 277.481 | 0 | 300 |  |  |  | 61.921 | 277.324 | 0 | 313 |  |  |  | 61.921 | 533.41 | 0.153 | 82 | 0
375.56 | 277.329 | 0 | 301 |  |  |  | 61.92 | 277.481 | 0 | 300 |  |  |  | 61.921 | 277.324 | 0 | 313 |  |  |  | 61.921 | 533.41 | 0.153 | 82 | 0
376.06 | 277.374 | 0 | 296 |  |  |  | 61.921 | 277.329 | 0 | 301 |  |  |  | 61.92 | 277.292 | 0 | 311 |  |  |  | 61.92 | 528.51 | 0.151 | 80 | 0
376.6 | 277.374 | 0 | 296 |  |  |  | 61.921 | 277.329 | 0 | 301 |  |  |  | 61.92 | 277.292 | 0 | 311 |  |  |  | 61.92 | 528.51 | 0.151 | 80 | 0
377.1 | 277.338 | 0 | 294 |  |  |  | 61.921 | 277.464 | 0 | 298 |  |  |  | 61.922 | 277.28 | 0 | 312 |  |  |  | 61.919 | 526.9 | 0.155 | 82 | 0
377.57 | 277.338 | 0 | 294 |  |  |  | 61.921 | 277.464 | 0 | 298 |  |  |  | 61.922 | 277.28 | 0 | 312 |  |  |  | 61.919 | 526.9 | 0.155 | 82 | 0
378.07 | 277.402 | 0 | 299 |  |  |  | 61.921 | 277.396 | 0 | 301 |  |  |  | 61.92 | 277.257 | 0 | 310 |  |  |  | 61.921 | 532.04 | 0.153 | 82 | 0
378.56 | 277.402 | 0 | 299 |  |  |  | 61.921 | 277.396 | 0 | 301 |  |  |  | 61.92 | 277.257 | 0 | 310 |  |  |  | 61.921 | 532.04 | 0.153 | 82 | 0
379.06 | 277.303 | 0 | 297 |  |  |  | 61.921 | 277.312 | 0 | 304 |  |  |  | 61.92 | 277.341 | 0 | 314 |  |  |  | 61.923 | 533.4 | 0.156 | 83 | 0
379.6 | 277.383 | 0 | 297 |  |  |  | 61.92 | 277.441 | 0 | 303 |  |  |  | 61.919 | 277.295 | 0 | 314 |  |  |  | 61.92 | 533.42 | 0.155 | 83 | 0
380.1 | 277.383 | 0 | 297 |  |  |  | 61.92 | 277.441 | 0 | 303 |  |  |  | 61.919 | 277.295 | 0 | 314 |  |  |  | 61.92 | 533.42 | 0.155 | 83 | 0
380.58 | 277.31 | 0 | 300 |  |  |  | 61.921 | 277.347 | 0 | 305 |  |  |  | 61.92 | 277.274 | 0 | 311 |  |  |  | 61.92 | 533.48 | 0.151 | 81 | 0
381.08 | 277.31 | 0 | 300 |  |  |  | 61.921 | 277.347 | 0 | 305 |  |  |  | 61.92 | 277.274 | 0 | 311 |  |  |  | 61.92 | 533.48 | 0.151 | 81 | 0
381.56 | 277.299 | 0 | 294 |  |  |  | 61.921 | 277.529 | 0 | 302 |  |  |  | 61.922 | 277.278 | 0 | 309 |  |  |  | 61.92 | 538.22 | 0.15 | 81 | 0
382.06 | 277.299 | 0 | 294 |  |  |  | 61.921 | 277.529 | 0 | 302 |  |  |  | 61.922 | 277.278 | 0 | 309 |  |  |  | 61.92 | 538.22 | 0.15 | 81 | 0
382.56 | 277.361 | 0 | 293 |  |  |  | 61.92 | 277.363 | 0 | 297 |  |  |  | 61.919 | 277.231 | 0 | 306 |  |  |  | 61.919 | 539.79 | 0.152 | 82 | 0
383.06 | 277.361 | 0 | 293 |  |  |  | 61.92 | 277.363 | 0 | 297 |  |  |  | 61.919 | 277.231 | 0 | 306 |  |  |  | 61.919 | 539.79 | 0.152 | 82 | 0
383.56 | 277.317 | 0 | 301 |  |  |  | 61.921 | 277.534 | 0 | 305 |  |  |  | 61.92 | 277.325 | 0 | 313 |  |  |  | 61.92 | 534.77 | 0.152 | 81 | 0
384.06 | 277.317 | 0 | 301 |  |  |  | 61.921 | 277.534 | 0 | 305 |  |  |  | 61.92 | 277.325 | 0 | 313 |  |  |  | 61.92 | 534.77 | 0.152 | 81 | 0
384.56 | 277.349 | 0 | 297 |  |  |  | 61.92 | 277.415 | 0 | 303 |  |  |  | 61.92 | 277.271 | 0 | 309 |  |  |  | 61.921 | 533.42 | 0.151 | 81 | 0
385.06 | 277.349 | 0 | 297 |  |  |  | 61.92 | 277.415 | 0 | 303 |  |  |  | 61.92 | 277.271 | 0 | 309 |  |  |  | 61.921 | 533.42 | 0.151 | 81 | 0
385.56 | 277.309 | 0 | 302 |  |  |  | 61.92 | 277.285 | 0 | 301 |  |  |  | 61.921 | 277.256 | 0 | 314 |  |  |  | 61.92 | 533.38 | 0.149 | 79 | 0
386.06 | 277.309 | 0 | 302 |  |  |  | 61.92 | 277.285 | 0 | 301 |  |  |  | 61.921 | 277.256 | 0 | 314 |  |  |  | 61.92 | 533.38 | 0.149 | 79 | 0
386.56 | 277.383 | 0 | 298 |  |  |  | 61.92 | 277.482 | 0 | 303 |  |  |  | 61.919 | 277.248 | 0 | 312 |  |  |  | 61.92 | 533.49 | 0.155 | 82 | 0
387.06 | 277.383 | 0 | 298 |  |  |  | 61.92 | 277.482 | 0 | 303 |  |  |  | 61.919 | 277.248 | 0 | 312 |  |  |  | 61.92 | 533.49 | 0.155 | 82 | 0
387.56 | 277.311 | 0 | 296 |  |  |  | 61.92 | 277.358 | 0 | 303 |  |  |  | 61.92 | 277.306 | 0 | 311 |  |  |  | 61.921 | 528.56 | 0.152 | 80 | 0
388.06 | 277.311 | 0 | 296 |  |  |  | 61.92 | 277.358 | 0 | 303 |  |  |  | 61.92 | 277.306 | 0 | 311 |  |  |  | 61.921 | 528.56 | 0.152 | 80 | 0
388.56 | 277.384 | 0 | 296 |  |  |  | 61.92 | 277.477 | 0 | 302 |  |  |  | 61.923 | 277.269 | 0 | 309 |  |  |  | 61.92 | 526.88 | 0.148 | 78 | 0
389.06 | 277.384 | 0 | 296 |  |  |  | 61.92 | 277.477 | 0 | 302 |  |  |  | 61.923 | 277.269 | 0 | 309 |  |  |  | 61.92 | 526.88 | 0.148 | 78 | 0
389.56 | 277.352 | 0 | 297 |  |  |  | 61.921 | 277.359 | 0 | 302 |  |  |  | 61.92 | 277.224 | 0 | 312 |  |  |  | 61.92 | 531.95 | 0.151 | 80 | 0
390.06 | 277.352 | 0 | 297 |  |  |  | 61.921 | 277.359 | 0 | 302 |  |  |  | 61.92 | 277.224 | 0 | 312 |  |  |  | 61.92 | 531.95 | 0.151 | 80 | 0
390.56 | 277.332 | 0 | 299 |  |  |  | 61.921 | 277.305 | 0 | 302 |  |  |  | 61.919 | 277.208 | 0 | 308 |  |  |  | 61.92 | 533.36 | 0.155 | 83 | 0
391.06 | 277.332 | 0 | 299 |  |  |  | 61.921 | 277.305 | 0 | 302 |  |  |  | 61.919 | 277.208 | 0 | 308 |  |  |  | 61.92 | 533.36 | 0.155 | 83 | 0
391.56 | 277.391 | 0 | 298 |  |  |  | 61.92 | 277.402 | 0 | 302 |  |  |  | 61.92 | 277.302 | 0 | 310 |  |  |  | 61.918 | 533.34 | 0.156 | 83 | 0
392.06 | 277.391 | 0 | 298 |  |  |  | 61.92 | 277.402 | 0 | 302 |  |  |  | 61.92 | 277.302 | 0 | 310 |  |  |  | 61.918 | 533.34 | 0.156 | 83 | 0
392.56 | 277.346 | 0 | 295 |  |  |  | 61.92 | 277.308 | 0 | 299 |  |  |  | 61.92 | 277.284 | 0 | 310 |  |  |  | 61.921 | 533.42 | 0.152 | 81 | 0
393.06 | 277.346 | 0 | 295 |  |  |  | 61.92 | 277.308 | 0 | 299 |  |  |  | 61.92 | 277.284 | 0 | 310 |  |  |  | 61.921 | 533.42 | 0.152 | 81 | 0
393.56 | 277.383 | 0 | 297 |  |  |  | 61.92 | 277.505 | 0 | 303 |  |  |  | 61.919 | 277.235 | 0 | 308 |  |  |  | 61.92 | 538.17 | 0.157 | 85 | 0
394.06 | 277.383 | 0 | 297 |  |  |  | 61.92 | 277.505 | 0 | 303 |  |  |  | 61.919 | 277.235 | 0 | 308 |  |  |  | 61.92 | 538.17 | 0.157 | 85 | 0
394.56 | 277.342 | 0 | 294 |  |  |  | 61.921 | 277.382 | 0 | 295 |  |  |  | 61.92 | 277.196 | 0 | 306 |  |  |  | 61.92 | 539.81 | 0.155 | 84 | 0
395.06 | 277.342 | 0 | 294 |  |  |  | 61.921 | 277.382 | 0 | 295 |  |  |  | 61.92 | 277.196 | 0 | 306 |  |  |  | 61.92 | 539.81 | 0.155 | 84 | 0
395.56 | 277.419 | 0 | 301 |  |  |  | 61.92 | 277.466 | 0 | 303 |  |  |  | 61.92 | 277.287 | 0 | 315 |  |  |  | 61.921 | 534.86 | 0.151 | 81 | 0
396.06 | 277.419 | 0 | 301 |  |  |  | 61.92 | 277.466 | 0 | 303 |  |  |  | 61.92 | 277.287 | 0 | 315 |  |  |  | 61.921 | 534.86 | 0.151 | 81 | 0
396.56 | 277.31 | 0 | 298 |  |  |  | 61.921 | 277.398 | 0 | 300 |  |  |  | 61.919 | 277.291 | 0 | 309 |  |  |  | 61.921 | 533.43 | 0.154 | 82 | 0
397.06 | 277.31 | 0 | 298 |  |  |  | 61.921 | 277.398 | 0 | 300 |  |  |  | 61.919 | 277.291 | 0 | 309 |  |  |  | 61.921 | 533.43 | 0.154 | 82 | 0
397.56 | 277.376 | 0 | 297 |  |  |  | 61.919 | 277.242 | 0 | 305 |  |  |  | 61.92 | 277.263 | 0 | 312 |  |  |  | 61.92 | 533.52 | 0.158 | 84 | 0
398.06 | 277.376 | 0 | 297 |  |  |  | 61.919 | 277.242 | 0 | 305 |  |  |  | 61.92 | 277.263 | 0 | 312 |  |  |  | 61.92 | 533.52 | 0.158 | 84 | 0
398.56 | 277.357 | 0 | 300 |  |  |  | 61.921 | 277.403 | 0 | 302 |  |  |  | 61.919 | 277.206 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.153 | 82 | 0
399.06 | 277.357 | 0 | 300 |  |  |  | 61.921 | 277.403 | 0 | 302 |  |  |  | 61.919 | 277.206 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.153 | 82 | 0
399.56 | 277.348 | 0 | 297 |  |  |  | 61.921 | 277.315 | 0 | 306 |  |  |  | 61.92 | 277.196 | 0 | 313 |  |  |  | 61.919 | 528.68 | 0.154 | 81 | 0
400.06 | 277.348 | 0 | 297 |  |  |  | 61.921 | 277.315 | 0 | 306 |  |  |  | 61.92 | 277.196 | 0 | 313 |  |  |  | 61.919 | 528.68 | 0.154 | 81 | 0
400.56 | 277.397 | 0 | 294 |  |  |  | 61.92 | 277.453 | 0 | 297 |  |  |  | 61.923 | 277.29 | 0 | 310 |  |  |  | 61.919 | 526.91 | 0.152 | 80 | 0
401.06 | 277.397 | 0 | 294 |  |  |  | 61.92 | 277.453 | 0 | 297 |  |  |  | 61.923 | 277.29 | 0 | 310 |  |  |  | 61.919 | 526.91 | 0.152 | 80 | 0
401.56 | 277.357 | 0 | 297 |  |  |  | 61.921 | 277.349 | 0 | 295 |  |  |  | 61.92 | 277.277 | 0 | 308 |  |  |  | 61.92 | 531.95 | 0.153 | 81 | 0
402.06 | 277.357 | 0 | 297 |  |  |  | 61.921 | 277.349 | 0 | 295 |  |  |  | 61.92 | 277.277 | 0 | 308 |  |  |  | 61.92 | 531.95 | 0.153 | 81 | 0
402.56 | 277.403 | 0 | 299 |  |  |  | 61.921 | 277.257 | 0 | 307 |  |  |  | 61.919 | 277.229 | 0 | 310 |  |  |  | 61.921 | 533.29 | 0.151 | 81 | 0
403.06 | 277.403 | 0 | 299 |  |  |  | 61.921 | 277.257 | 0 | 307 |  |  |  | 61.919 | 277.229 | 0 | 310 |  |  |  | 61.921 | 533.29 | 0.151 | 81 | 0
403.56 | 277.331 | 0 | 296 |  |  |  | 61.92 | 277.443 | 0 | 302 |  |  |  | 61.92 | 277.196 | 0 | 308 |  |  |  | 61.919 | 533.45 | 0.149 | 80 | 0
404.06 | 277.331 | 0 | 296 |  |  |  | 61.92 | 277.443 | 0 | 302 |  |  |  | 61.92 | 277.196 | 0 | 308 |  |  |  | 61.919 | 533.45 | 0.149 | 80 | 0
404.56 | 277.413 | 0 | 300 |  |  |  | 61.921 | 277.271 | 0 | 302 |  |  |  | 61.92 | 277.278 | 0 | 309 |  |  |  | 61.919 | 533.39 | 0.156 | 83 | 0
405.06 | 277.413 | 0 | 300 |  |  |  | 61.921 | 277.271 | 0 | 302 |  |  |  | 61.92 | 277.278 | 0 | 309 |  |  |  | 61.919 | 533.39 | 0.156 | 83 | 0
405.56 | 277.306 | 0 | 298 |  |  |  | 61.921 | 277.44 | 0 | 302 |  |  |  | 61.921 | 277.273 | 0 | 311 |  |  |  | 61.92 | 538.08 | 0.157 | 84 | 0
406.06 | 277.306 | 0 | 298 |  |  |  | 61.921 | 277.44 | 0 | 302 |  |  |  | 61.921 | 277.273 | 0 | 311 |  |  |  | 61.92 | 538.08 | 0.157 | 84 | 0
406.56 | 277.361 | 0 | 291 |  |  |  | 61.921 | 277.351 | 0 | 300 |  |  |  | 61.919 | 277.247 | 0 | 307 |  |  |  | 61.92 | 539.74 | 0.155 | 84 | 0
407.06 | 277.361 | 0 | 291 |  |  |  | 61.921 | 277.351 | 0 | 300 |  |  |  | 61.919 | 277.247 | 0 | 307 |  |  |  | 61.92 | 539.74 | 0.155 | 84 | 0
407.56 | 277.355 | 0 | 296 |  |  |  | 61.92 | 277.509 | 0 | 306 |  |  |  | 61.922 | 277.199 | 0 | 314 |  |  |  | 61.92 | 534.75 | 0.149 | 80 | 0
408.09 | 277.355 | 0 | 296 |  |  |  | 61.92 | 277.509 | 0 | 306 |  |  |  | 61.922 | 277.199 | 0 | 314 |  |  |  | 61.92 | 534.75 | 0.149 | 80 | 0
408.59 | 277.349 | 0 | 298 |  |  |  | 61.92 | 277.4 | 0 | 303 |  |  |  | 61.919 | 277.29 | 0 | 306 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 0
409.07 | 277.349 | 0 | 298 |  |  |  | 61.92 | 277.4 | 0 | 303 |  |  |  | 61.919 | 277.29 | 0 | 306 |  |  |  | 61.921 | 533.4 | 0.15 | 80 | 0
409.57 | 277.394 | 0 | 299 |  |  |  | 61.921 | 277.274 | 0 | 302 |  |  |  | 61.92 | 277.275 | 0 | 310 |  |  |  | 61.921 | 533.45 | 0.153 | 82 | 0
410.06 | 277.394 | 0 | 299 |  |  |  | 61.921 | 277.274 | 0 | 302 |  |  |  | 61.92 | 277.275 | 0 | 310 |  |  |  | 61.921 | 533.45 | 0.153 | 82 | 0
410.56 | 277.354 | 0 | 301 |  |  |  | 61.921 | 277.432 | 0 | 304 |  |  |  | 61.919 | 277.25 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.153 | 81 | 0
411.09 | 277.399 | 0 | 302 |  |  |  | 61.92 | 277.318 | 0 | 301 |  |  |  | 61.92 | 277.204 | 0 | 312 |  |  |  | 61.92 | 528.75 | 0.153 | 81 | 0
411.59 | 277.399 | 0 | 302 |  |  |  | 61.92 | 277.318 | 0 | 301 |  |  |  | 61.92 | 277.204 | 0 | 312 |  |  |  | 61.92 | 528.75 | 0.153 | 81 | 0
412.08 | 277.323 | 0 | 296 |  |  |  | 61.921 | 277.529 | 0 | 299 |  |  |  | 61.923 | 277.324 | 0 | 308 |  |  |  | 61.919 | 526.95 | 0.154 | 81 | 0
412.58 | 277.323 | 0 | 296 |  |  |  | 61.921 | 277.529 | 0 | 299 |  |  |  | 61.923 | 277.324 | 0 | 308 |  |  |  | 61.919 | 526.95 | 0.154 | 81 | 0
413.06 | 277.389 | 0 | 293 |  |  |  | 61.92 | 277.365 | 0 | 301 |  |  |  | 61.919 | 277.288 | 0 | 309 |  |  |  | 61.921 | 531.91 | 0.157 | 84 | 0
413.56 | 277.389 | 0 | 293 |  |  |  | 61.92 | 277.365 | 0 | 301 |  |  |  | 61.919 | 277.288 | 0 | 309 |  |  |  | 61.921 | 531.91 | 0.157 | 84 | 0
414.06 | 277.28 | 0 | 296 |  |  |  | 61.92 | 277.315 | 0 | 304 |  |  |  | 61.919 | 277.274 | 0 | 308 |  |  |  | 61.919 | 533.4 | 0.151 | 80 | 0
414.56 | 277.28 | 0 | 296 |  |  |  | 61.92 | 277.315 | 0 | 304 |  |  |  | 61.919 | 277.274 | 0 | 308 |  |  |  | 61.919 | 533.4 | 0.151 | 80 | 0
415.06 | 277.342 | 0 | 298 |  |  |  | 61.92 | 277.457 | 0 | 305 |  |  |  | 61.919 | 277.249 | 0 | 314 |  |  |  | 61.92 | 533.55 | 0.153 | 82 | 0
415.56 | 277.342 | 0 | 298 |  |  |  | 61.92 | 277.457 | 0 | 305 |  |  |  | 61.919 | 277.249 | 0 | 314 |  |  |  | 61.92 | 533.55 | 0.153 | 82 | 0
416.06 | 277.359 | 0 | 301 |  |  |  | 61.92 | 277.334 | 0 | 302 |  |  |  | 61.92 | 277.346 | 0 | 311 |  |  |  | 61.921 | 533.41 | 0.153 | 81 | 0
416.56 | 277.359 | 0 | 301 |  |  |  | 61.92 | 277.334 | 0 | 302 |  |  |  | 61.92 | 277.346 | 0 | 311 |  |  |  | 61.921 | 533.41 | 0.153 | 81 | 0
417.06 | 277.346 | 0 | 297 |  |  |  | 61.921 | 277.524 | 0 | 301 |  |  |  | 61.92 | 277.299 | 0 | 310 |  |  |  | 61.921 | 538.01 | 0.151 | 81 | 0
417.56 | 277.346 | 0 | 297 |  |  |  | 61.921 | 277.524 | 0 | 301 |  |  |  | 61.92 | 277.299 | 0 | 310 |  |  |  | 61.921 | 538.01 | 0.151 | 81 | 0
418.06 | 277.377 | 0 | 291 |  |  |  | 61.92 | 277.396 | 0 | 294 |  |  |  | 61.919 | 277.274 | 0 | 307 |  |  |  | 61.919 | 539.88 | 0.151 | 82 | 0
418.56 | 277.377 | 0 | 291 |  |  |  | 61.92 | 277.396 | 0 | 294 |  |  |  | 61.919 | 277.274 | 0 | 307 |  |  |  | 61.919 | 539.88 | 0.151 | 82 | 0
419.06 | 277.333 | 0 | 298 |  |  |  | 61.921 | 277.532 | 0 | 304 |  |  |  | 61.923 | 277.264 | 0 | 314 |  |  |  | 61.92 | 534.96 | 0.155 | 83 | 0
419.56 | 277.333 | 0 | 298 |  |  |  | 61.921 | 277.532 | 0 | 304 |  |  |  | 61.923 | 277.264 | 0 | 314 |  |  |  | 61.92 | 534.96 | 0.155 | 83 | 0
420.06 | 277.394 | 0 | 300 |  |  |  | 61.92 | 277.419 | 0 | 303 |  |  |  | 61.919 | 277.212 | 0 | 311 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 0
420.56 | 277.394 | 0 | 300 |  |  |  | 61.92 | 277.419 | 0 | 303 |  |  |  | 61.919 | 277.212 | 0 | 311 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 0
421.06 | 277.278 | 0 | 300 |  |  |  | 61.921 | 277.332 | 0 | 303 |  |  |  | 61.92 | 277.31 | 0 | 314 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 0
421.56 | 277.278 | 0 | 300 |  |  |  | 61.921 | 277.332 | 0 | 303 |  |  |  | 61.92 | 277.31 | 0 | 314 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 0
422.06 | 277.372 | 0 | 297 |  |  |  | 61.921 | 277.428 | 0 | 302 |  |  |  | 61.92 | 277.263 | 0 | 309 |  |  |  | 61.92 | 533.49 | 0.16 | 85 | 0
422.56 | 277.372 | 0 | 297 |  |  |  | 61.921 | 277.428 | 0 | 302 |  |  |  | 61.92 | 277.263 | 0 | 309 |  |  |  | 61.92 | 533.49 | 0.16 | 85 | 0
423.06 | 277.275 | 0 | 300 |  |  |  | 61.92 | 277.299 | 0 | 302 |  |  |  | 61.921 | 277.261 | 0 | 311 |  |  |  | 61.92 | 528.93 | 0.154 | 82 | 0
423.56 | 277.275 | 0 | 300 |  |  |  | 61.92 | 277.299 | 0 | 302 |  |  |  | 61.921 | 277.261 | 0 | 311 |  |  |  | 61.92 | 528.93 | 0.154 | 82 | 0
424.06 | 277.333 | 0 | 293 |  |  |  | 61.921 | 277.524 | 0 | 301 |  |  |  | 61.923 | 277.242 | 0 | 306 |  |  |  | 61.921 | 526.96 | 0.151 | 80 | 0
424.56 | 277.333 | 0 | 293 |  |  |  | 61.921 | 277.524 | 0 | 301 |  |  |  | 61.923 | 277.242 | 0 | 306 |  |  |  | 61.921 | 526.96 | 0.151 | 80 | 0
425.06 | 277.359 | 0 | 292 |  |  |  | 61.921 | 277.384 | 0 | 300 |  |  |  | 61.92 | 277.3 | 0 | 304 |  |  |  | 61.921 | 531.7 | 0.149 | 79 | 0
425.56 | 277.359 | 0 | 292 |  |  |  | 61.921 | 277.384 | 0 | 300 |  |  |  | 61.92 | 277.3 | 0 | 304 |  |  |  | 61.921 | 531.7 | 0.149 | 79 | 0
426.06 | 277.335 | 0 | 296 |  |  |  | 61.921 | 277.326 | 0 | 301 |  |  |  | 61.921 | 277.264 | 0 | 312 |  |  |  | 61.919 | 533.45 | 0.152 | 81 | 0
426.56 | 277.335 | 0 | 296 |  |  |  | 61.921 | 277.326 | 0 | 301 |  |  |  | 61.921 | 277.264 | 0 | 312 |  |  |  | 61.919 | 533.45 | 0.152 | 81 | 0
427.06 | 277.381 | 0 | 299 |  |  |  | 61.919 | 277.449 | 0 | 302 |  |  |  | 61.919 | 277.227 | 0 | 310 |  |  |  | 61.92 | 533.44 | 0.155 | 83 | 0
427.56 | 277.381 | 0 | 299 |  |  |  | 61.919 | 277.449 | 0 | 302 |  |  |  | 61.919 | 277.227 | 0 | 310 |  |  |  | 61.92 | 533.44 | 0.155 | 83 | 0
428.06 | 277.326 | 0 | 301 |  |  |  | 61.92 | 277.329 | 0 | 300 |  |  |  | 61.919 | 277.216 | 0 | 309 |  |  |  | 61.919 | 533.46 | 0.153 | 82 | 0
428.56 | 277.326 | 0 | 301 |  |  |  | 61.92 | 277.329 | 0 | 300 |  |  |  | 61.919 | 277.216 | 0 | 309 |  |  |  | 61.919 | 533.46 | 0.153 | 82 | 0
429.06 | 277.392 | 0 | 295 |  |  |  | 61.921 | 277.457 | 0 | 303 |  |  |  | 61.921 | 277.305 | 0 | 309 |  |  |  | 61.921 | 537.91 | 0.154 | 83 | 0
429.56 | 277.392 | 0 | 295 |  |  |  | 61.921 | 277.457 | 0 | 303 |  |  |  | 61.921 | 277.305 | 0 | 309 |  |  |  | 61.921 | 537.91 | 0.154 | 83 | 0
430.06 | 277.284 | 0 | 290 |  |  |  | 61.92 | 277.367 | 0 | 298 |  |  |  | 61.919 | 277.273 | 0 | 306 |  |  |  | 61.921 | 539.89 | 0.152 | 82 | 0
430.56 | 277.284 | 0 | 290 |  |  |  | 61.92 | 277.367 | 0 | 298 |  |  |  | 61.919 | 277.273 | 0 | 306 |  |  |  | 61.921 | 539.89 | 0.152 | 82 | 0
431.06 | 277.358 | 0 | 302 |  |  |  | 61.921 | 277.489 | 0 | 303 |  |  |  | 61.924 | 277.221 | 0 | 314 |  |  |  | 61.92 | 535.06 | 0.152 | 81 | 0
431.56 | 277.358 | 0 | 302 |  |  |  | 61.921 | 277.489 | 0 | 303 |  |  |  | 61.924 | 277.221 | 0 | 314 |  |  |  | 61.92 | 535.06 | 0.152 | 81 | 0
432.06 | 277.287 | 0 | 298 |  |  |  | 61.919 | 277.415 | 0 | 305 |  |  |  | 61.92 | 277.208 | 0 | 313 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 0
432.56 | 277.287 | 0 | 298 |  |  |  | 61.919 | 277.415 | 0 | 305 |  |  |  | 61.92 | 277.208 | 0 | 313 |  |  |  | 61.92 | 533.38 | 0.152 | 81 | 0
433.06 | 277.331 | 0 | 298 |  |  |  | 61.921 | 277.267 | 0 | 304 |  |  |  | 61.921 | 277.295 | 0 | 314 |  |  |  | 61.919 | 533.35 | 0.154 | 82 | 0
433.56 | 277.331 | 0 | 298 |  |  |  | 61.921 | 277.267 | 0 | 304 |  |  |  | 61.921 | 277.295 | 0 | 314 |  |  |  | 61.919 | 533.35 | 0.154 | 82 | 0
434.06 | 277.367 | 0 | 302 |  |  |  | 61.92 | 277.44 | 0 | 302 |  |  |  | 61.921 | 277.296 | 0 | 311 |  |  |  | 61.921 | 533.45 | 0.152 | 81 | 0
434.56 | 277.367 | 0 | 302 |  |  |  | 61.92 | 277.44 | 0 | 302 |  |  |  | 61.921 | 277.296 | 0 | 311 |  |  |  | 61.921 | 533.45 | 0.152 | 81 | 0
435.06 | 277.338 | 0 | 297 |  |  |  | 61.921 | 277.289 | 0 | 299 |  |  |  | 61.919 | 277.254 | 0 | 308 |  |  |  | 61.919 | 528.9 | 0.153 | 81 | 0
435.56 | 277.338 | 0 | 297 |  |  |  | 61.921 | 277.289 | 0 | 299 |  |  |  | 61.919 | 277.254 | 0 | 308 |  |  |  | 61.919 | 528.9 | 0.153 | 81 | 0
436.06 | 277.375 | 0 | 293 |  |  |  | 61.919 | 277.485 | 0 | 302 |  |  |  | 61.922 | 277.21 | 0 | 310 |  |  |  | 61.92 | 526.9 | 0.147 | 78 | 0
436.56 | 277.375 | 0 | 293 |  |  |  | 61.919 | 277.485 | 0 | 302 |  |  |  | 61.922 | 277.21 | 0 | 310 |  |  |  | 61.92 | 526.9 | 0.147 | 78 | 0
437.06 | 277.337 | 0 | 294 |  |  |  | 61.92 | 277.352 | 0 | 302 |  |  |  | 61.92 | 277.274 | 0 | 308 |  |  |  | 61.92 | 531.81 | 0.152 | 81 | 0
437.56 | 277.337 | 0 | 294 |  |  |  | 61.92 | 277.352 | 0 | 302 |  |  |  | 61.92 | 277.274 | 0 | 308 |  |  |  | 61.92 | 531.81 | 0.152 | 81 | 0
438.06 | 277.411 | 0 | 300 |  |  |  | 61.92 | 277.32 | 0 | 304 |  |  |  | 61.92 | 277.271 | 0 | 312 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 0
438.56 | 277.411 | 0 | 300 |  |  |  | 61.92 | 277.32 | 0 | 304 |  |  |  | 61.92 | 277.271 | 0 | 312 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 0
439.06 | 277.317 | 0 | 297 |  |  |  | 61.92 | 277.41 | 0 | 301 |  |  |  | 61.918 | 277.251 | 0 | 313 |  |  |  | 61.921 | 533.38 | 0.156 | 83 | 0
439.59 | 277.317 | 0 | 297 |  |  |  | 61.92 | 277.41 | 0 | 301 |  |  |  | 61.918 | 277.251 | 0 | 313 |  |  |  | 61.921 | 533.38 | 0.156 | 83 | 0
440.09 | 277.379 | 0 | 295 |  |  |  | 61.921 | 277.292 | 0 | 301 |  |  |  | 61.92 | 277.203 | 0 | 311 |  |  |  | 61.921 | 533.39 | 0.157 | 84 | 0
440.58 | 277.379 | 0 | 295 |  |  |  | 61.921 | 277.292 | 0 | 301 |  |  |  | 61.92 | 277.203 | 0 | 311 |  |  |  | 61.921 | 533.39 | 0.157 | 84 | 0
441.08 | 277.324 | 0 | 296 |  |  |  | 61.92 | 277.467 | 0 | 302 |  |  |  | 61.919 | 277.301 | 0 | 307 |  |  |  | 61.921 | 537.96 | 0.153 | 82 | 0
441.56 | 277.324 | 0 | 296 |  |  |  | 61.92 | 277.467 | 0 | 302 |  |  |  | 61.919 | 277.301 | 0 | 307 |  |  |  | 61.921 | 537.96 | 0.153 | 82 | 0
442.06 | 277.363 | 0 | 296 |  |  |  | 61.92 | 277.304 | 0 | 291 |  |  |  | 61.921 | 277.283 | 0 | 302 |  |  |  | 61.92 | 539.82 | 0.153 | 83 | 0
442.6 | 277.404 | 0 | 302 |  |  |  | 61.921 | 277.463 | 0 | 307 |  |  |  | 61.923 | 277.276 | 0 | 311 |  |  |  | 61.919 | 535.01 | 0.15 | 80 | 0
443.1 | 277.404 | 0 | 302 |  |  |  | 61.921 | 277.463 | 0 | 307 |  |  |  | 61.923 | 277.276 | 0 | 311 |  |  |  | 61.919 | 535.01 | 0.15 | 80 | 0
443.58 | 277.38 | 0 | 302 |  |  |  | 61.92 | 277.371 | 0 | 301 |  |  |  | 61.92 | 277.233 | 0 | 314 |  |  |  | 61.92 | 533.48 | 0.157 | 84 | 0
444.08 | 277.38 | 0 | 302 |  |  |  | 61.92 | 277.371 | 0 | 301 |  |  |  | 61.92 | 277.233 | 0 | 314 |  |  |  | 61.92 | 533.48 | 0.157 | 84 | 0
444.56 | 277.418 | 0 | 298 |  |  |  | 61.921 | 277.263 | 0 | 304 |  |  |  | 61.919 | 277.189 | 0 | 310 |  |  |  | 61.92 | 533.43 | 0.154 | 82 | 0
445.06 | 277.418 | 0 | 298 |  |  |  | 61.921 | 277.263 | 0 | 304 |  |  |  | 61.919 | 277.189 | 0 | 310 |  |  |  | 61.92 | 533.43 | 0.154 | 82 | 0
445.56 | 277.337 | 0 | 300 |  |  |  | 61.92 | 277.423 | 0 | 304 |  |  |  | 61.92 | 277.272 | 0 | 308 |  |  |  | 61.92 | 533.34 | 0.153 | 82 | 0
446.06 | 277.337 | 0 | 300 |  |  |  | 61.92 | 277.423 | 0 | 304 |  |  |  | 61.92 | 277.272 | 0 | 308 |  |  |  | 61.92 | 533.34 | 0.153 | 82 | 0
446.56 | 277.415 | 0 | 299 |  |  |  | 61.921 | 277.288 | 0 | 297 |  |  |  | 61.921 | 277.261 | 0 | 309 |  |  |  | 61.919 | 528.86 | 0.161 | 85 | 0
447.06 | 277.415 | 0 | 299 |  |  |  | 61.921 | 277.288 | 0 | 297 |  |  |  | 61.921 | 277.261 | 0 | 309 |  |  |  | 61.919 | 528.86 | 0.161 | 85 | 0
447.56 | 277.317 | 0 | 293 |  |  |  | 61.92 | 277.473 | 0 | 301 |  |  |  | 61.923 | 277.237 | 0 | 307 |  |  |  | 61.921 | 526.94 | 0.155 | 82 | 0
448.06 | 277.317 | 0 | 293 |  |  |  | 61.92 | 277.473 | 0 | 301 |  |  |  | 61.923 | 277.237 | 0 | 307 |  |  |  | 61.921 | 526.94 | 0.155 | 82 | 0
448.56 | 277.374 | 0 | 297 |  |  |  | 61.92 | 277.361 | 0 | 301 |  |  |  | 61.92 | 277.214 | 0 | 308 |  |  |  | 61.92 | 531.63 | 0.156 | 83 | 0
449.06 | 277.374 | 0 | 297 |  |  |  | 61.92 | 277.361 | 0 | 301 |  |  |  | 61.92 | 277.214 | 0 | 308 |  |  |  | 61.92 | 531.63 | 0.156 | 83 | 0
449.56 | 277.316 | 0 | 298 |  |  |  | 61.92 | 277.414 | 0 | 303 |  |  |  | 61.92 | 277.314 | 0 | 309 |  |  |  | 61.921 | 533.33 | 0.155 | 83 | 0
450.06 | 277.316 | 0 | 298 |  |  |  | 61.92 | 277.414 | 0 | 303 |  |  |  | 61.92 | 277.314 | 0 | 309 |  |  |  | 61.921 | 533.33 | 0.155 | 83 | 0
450.56 | 277.377 | 0 | 297 |  |  |  | 61.92 | 277.383 | 0 | 303 |  |  |  | 61.92 | 277.285 | 0 | 313 |  |  |  | 61.921 | 533.38 | 0.156 | 83 | 0
451.06 | 277.377 | 0 | 297 |  |  |  | 61.92 | 277.383 | 0 | 303 |  |  |  | 61.92 | 277.285 | 0 | 313 |  |  |  | 61.921 | 533.38 | 0.156 | 83 | 0
451.56 | 277.412 | 0 | 300 |  |  |  | 61.92 | 277.265 | 0 | 303 |  |  |  | 61.919 | 277.284 | 0 | 312 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
452.06 | 277.412 | 0 | 300 |  |  |  | 61.92 | 277.265 | 0 | 303 |  |  |  | 61.919 | 277.284 | 0 | 312 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
452.56 | 277.363 | 0 | 294 |  |  |  | 61.92 | 277.465 | 0 | 302 |  |  |  | 61.921 | 277.247 | 0 | 310 |  |  |  | 61.921 | 537.67 | 0.153 | 82 | 0
453.06 | 277.363 | 0 | 294 |  |  |  | 61.92 | 277.465 | 0 | 302 |  |  |  | 61.921 | 277.247 | 0 | 310 |  |  |  | 61.921 | 537.67 | 0.153 | 82 | 0
453.56 | 277.427 | 0 | 294 |  |  |  | 61.921 | 277.355 | 0 | 296 |  |  |  | 61.92 | 277.326 | 0 | 308 |  |  |  | 61.92 | 539.81 | 0.154 | 83 | 0
454.06 | 277.427 | 0 | 294 |  |  |  | 61.921 | 277.355 | 0 | 296 |  |  |  | 61.92 | 277.326 | 0 | 308 |  |  |  | 61.92 | 539.81 | 0.154 | 83 | 0
454.56 | 277.326 | 0 | 300 |  |  |  | 61.92 | 277.473 | 0 | 302 |  |  |  | 61.923 | 277.271 | 0 | 314 |  |  |  | 61.92 | 535.16 | 0.15 | 81 | 0
455.06 | 277.326 | 0 | 300 |  |  |  | 61.92 | 277.473 | 0 | 302 |  |  |  | 61.923 | 277.271 | 0 | 314 |  |  |  | 61.92 | 535.16 | 0.15 | 81 | 0
455.56 | 277.409 | 0 | 300 |  |  |  | 61.919 | 277.348 | 0 | 306 |  |  |  | 61.92 | 277.265 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.163 | 87 | 0
456.06 | 277.409 | 0 | 300 |  |  |  | 61.919 | 277.348 | 0 | 306 |  |  |  | 61.92 | 277.265 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.163 | 87 | 0
456.56 | 277.331 | 0 | 301 |  |  |  | 61.919 | 277.274 | 0 | 301 |  |  |  | 61.92 | 277.241 | 0 | 311 |  |  |  | 61.921 | 533.51 | 0.153 | 82 | 0
457.06 | 277.331 | 0 | 301 |  |  |  | 61.919 | 277.274 | 0 | 301 |  |  |  | 61.92 | 277.241 | 0 | 311 |  |  |  | 61.921 | 533.51 | 0.153 | 82 | 0
457.56 | 277.361 | 0 | 297 |  |  |  | 61.92 | 277.413 | 0 | 303 |  |  |  | 61.92 | 277.339 | 0 | 308 |  |  |  | 61.92 | 533.42 | 0.155 | 83 | 0
458.06 | 277.361 | 0 | 297 |  |  |  | 61.92 | 277.413 | 0 | 303 |  |  |  | 61.92 | 277.339 | 0 | 308 |  |  |  | 61.92 | 533.42 | 0.155 | 83 | 0
458.56 | 277.332 | 0 | 296 |  |  |  | 61.921 | 277.324 | 0 | 304 |  |  |  | 61.919 | 277.298 | 0 | 309 |  |  |  | 61.92 | 529 | 0.154 | 82 | 0
459.06 | 277.332 | 0 | 296 |  |  |  | 61.921 | 277.324 | 0 | 304 |  |  |  | 61.919 | 277.298 | 0 | 309 |  |  |  | 61.92 | 529 | 0.154 | 82 | 0
459.56 | 277.374 | 0 | 295 |  |  |  | 61.92 | 277.492 | 0 | 298 |  |  |  | 61.921 | 277.261 | 0 | 309 |  |  |  | 61.919 | 526.93 | 0.155 | 82 | 0
460.06 | 277.374 | 0 | 295 |  |  |  | 61.92 | 277.492 | 0 | 298 |  |  |  | 61.921 | 277.261 | 0 | 309 |  |  |  | 61.919 | 526.93 | 0.155 | 82 | 0
460.56 | 277.402 | 0 | 294 |  |  |  | 61.921 | 277.358 | 0 | 302 |  |  |  | 61.921 | 277.25 | 0 | 311 |  |  |  | 61.919 | 531.41 | 0.151 | 80 | 0
461.06 | 277.402 | 0 | 294 |  |  |  | 61.921 | 277.358 | 0 | 302 |  |  |  | 61.921 | 277.25 | 0 | 311 |  |  |  | 61.919 | 531.41 | 0.151 | 80 | 0
461.56 | 277.366 | 0 | 295 |  |  |  | 61.921 | 277.425 | 0 | 303 |  |  |  | 61.92 | 277.327 | 0 | 309 |  |  |  | 61.92 | 533.39 | 0.155 | 82 | 0
462.06 | 277.366 | 0 | 295 |  |  |  | 61.921 | 277.425 | 0 | 303 |  |  |  | 61.92 | 277.327 | 0 | 309 |  |  |  | 61.92 | 533.39 | 0.155 | 82 | 0
462.56 | 277.418 | 0 | 299 |  |  |  | 61.921 | 277.445 | 0 | 301 |  |  |  | 61.919 | 277.316 | 0 | 306 |  |  |  | 61.92 | 533.31 | 0.152 | 81 | 0
463.06 | 277.418 | 0 | 299 |  |  |  | 61.921 | 277.445 | 0 | 301 |  |  |  | 61.919 | 277.316 | 0 | 306 |  |  |  | 61.92 | 533.31 | 0.152 | 81 | 0
463.56 | 277.336 | 0 | 299 |  |  |  | 61.92 | 277.304 | 0 | 305 |  |  |  | 61.921 | 277.253 | 0 | 313 |  |  |  | 61.921 | 533.46 | 0.151 | 80 | 0
464.06 | 277.336 | 0 | 299 |  |  |  | 61.92 | 277.304 | 0 | 305 |  |  |  | 61.921 | 277.253 | 0 | 313 |  |  |  | 61.921 | 533.46 | 0.151 | 80 | 0
464.56 | 277.414 | 0 | 299 |  |  |  | 61.921 | 277.45 | 0 | 303 |  |  |  | 61.921 | 277.226 | 0 | 312 |  |  |  | 61.92 | 537.74 | 0.16 | 86 | 0
465.06 | 277.414 | 0 | 299 |  |  |  | 61.921 | 277.45 | 0 | 303 |  |  |  | 61.921 | 277.226 | 0 | 312 |  |  |  | 61.92 | 537.74 | 0.16 | 86 | 0
465.56 | 277.33 | 0 | 292 |  |  |  | 61.921 | 277.365 | 0 | 294 |  |  |  | 61.919 | 277.317 | 0 | 304 |  |  |  | 61.924 | 539.76 | 0.156 | 84 | 0
466.06 | 277.33 | 0 | 292 |  |  |  | 61.921 | 277.365 | 0 | 294 |  |  |  | 61.919 | 277.317 | 0 | 304 |  |  |  | 61.924 | 539.76 | 0.156 | 84 | 0
466.56 | 277.387 | 0 | 297 |  |  |  | 61.92 | 277.542 | 0 | 306 |  |  |  | 61.922 | 277.328 | 0 | 312 |  |  |  | 61.921 | 535.21 | 0.152 | 81 | 0
467.06 | 277.387 | 0 | 297 |  |  |  | 61.92 | 277.542 | 0 | 306 |  |  |  | 61.922 | 277.328 | 0 | 312 |  |  |  | 61.921 | 535.21 | 0.152 | 81 | 0
467.56 | 277.311 | 0 | 294 |  |  |  | 61.918 | 277.376 | 0 | 304 |  |  |  | 61.92 | 277.291 | 0 | 312 |  |  |  | 61.92 | 533.45 | 0.155 | 83 | 0
468.06 | 277.311 | 0 | 294 |  |  |  | 61.918 | 277.376 | 0 | 304 |  |  |  | 61.92 | 277.291 | 0 | 312 |  |  |  | 61.92 | 533.45 | 0.155 | 83 | 0
468.56 | 277.374 | 0 | 296 |  |  |  | 61.92 | 277.264 | 0 | 305 |  |  |  | 61.919 | 277.241 | 0 | 312 |  |  |  | 61.92 | 533.3 | 0.153 | 81 | 0
469.06 | 277.374 | 0 | 296 |  |  |  | 61.92 | 277.264 | 0 | 305 |  |  |  | 61.919 | 277.241 | 0 | 312 |  |  |  | 61.92 | 533.3 | 0.153 | 81 | 0
469.56 | 277.418 | 0 | 296 |  |  |  | 61.921 | 277.438 | 0 | 303 |  |  |  | 61.919 | 277.23 | 0 | 311 |  |  |  | 61.92 | 533.29 | 0.156 | 83 | 0
470.1 | 277.418 | 0 | 296 |  |  |  | 61.921 | 277.438 | 0 | 303 |  |  |  | 61.919 | 277.23 | 0 | 311 |  |  |  | 61.92 | 533.29 | 0.156 | 83 | 0
470.6 | 277.351 | 0 | 300 |  |  |  | 61.92 | 277.294 | 0 | 299 |  |  |  | 61.921 | 277.314 | 0 | 309 |  |  |  | 61.92 | 529.05 | 0.154 | 82 | 0
471.08 | 277.351 | 0 | 300 |  |  |  | 61.92 | 277.294 | 0 | 299 |  |  |  | 61.921 | 277.314 | 0 | 309 |  |  |  | 61.92 | 529.05 | 0.154 | 82 | 0
471.58 | 277.421 | 0 | 291 |  |  |  | 61.921 | 277.509 | 0 | 298 |  |  |  | 61.922 | 277.303 | 0 | 310 |  |  |  | 61.92 | 526.94 | 0.154 | 81 | 0
472.07 | 277.421 | 0 | 291 |  |  |  | 61.921 | 277.509 | 0 | 298 |  |  |  | 61.922 | 277.303 | 0 | 310 |  |  |  | 61.92 | 526.94 | 0.154 | 81 | 0
472.57 | 277.321 | 0 | 297 |  |  |  | 61.921 | 277.394 | 0 | 304 |  |  |  | 61.919 | 277.249 | 0 | 307 |  |  |  | 61.921 | 531.43 | 0.153 | 82 | 0
473.06 | 277.321 | 0 | 297 |  |  |  | 61.921 | 277.394 | 0 | 304 |  |  |  | 61.919 | 277.249 | 0 | 307 |  |  |  | 61.921 | 531.43 | 0.153 | 82 | 0
473.56 | 277.382 | 0 | 298 |  |  |  | 61.92 | 277.474 | 0 | 304 |  |  |  | 61.92 | 277.212 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.152 | 81 | 0
474.09 | 277.332 | 0 | 300 |  |  |  | 61.92 | 277.424 | 0 | 304 |  |  |  | 61.92 | 277.306 | 0 | 311 |  |  |  | 61.92 | 533.39 | 0.157 | 84 | 0
474.59 | 277.332 | 0 | 300 |  |  |  | 61.92 | 277.424 | 0 | 304 |  |  |  | 61.92 | 277.306 | 0 | 311 |  |  |  | 61.92 | 533.39 | 0.157 | 84 | 0
475.08 | 277.375 | 0 | 300 |  |  |  | 61.92 | 277.303 | 0 | 302 |  |  |  | 61.921 | 277.298 | 0 | 308 |  |  |  | 61.92 | 533.36 | 0.148 | 79 | 0
475.58 | 277.375 | 0 | 300 |  |  |  | 61.92 | 277.303 | 0 | 302 |  |  |  | 61.921 | 277.298 | 0 | 308 |  |  |  | 61.92 | 533.36 | 0.148 | 79 | 0
476.07 | 277.321 | 0 | 296 |  |  |  | 61.918 | 277.434 | 0 | 302 |  |  |  | 61.92 | 277.28 | 0 | 311 |  |  |  | 61.92 | 537.63 | 0.151 | 81 | 0
476.57 | 277.321 | 0 | 296 |  |  |  | 61.918 | 277.434 | 0 | 302 |  |  |  | 61.92 | 277.28 | 0 | 311 |  |  |  | 61.92 | 537.63 | 0.151 | 81 | 0
477.06 | 277.381 | 0 | 291 |  |  |  | 61.92 | 277.314 | 0 | 297 |  |  |  | 61.92 | 277.225 | 0 | 308 |  |  |  | 61.92 | 539.84 | 0.153 | 83 | 0
477.56 | 277.381 | 0 | 291 |  |  |  | 61.92 | 277.314 | 0 | 297 |  |  |  | 61.92 | 277.225 | 0 | 308 |  |  |  | 61.92 | 539.84 | 0.153 | 83 | 0
478.06 | 277.414 | 0 | 304 |  |  |  | 61.921 | 277.5 | 0 | 305 |  |  |  | 61.922 | 277.318 | 0 | 311 |  |  |  | 61.919 | 535.43 | 0.148 | 79 | 0
478.56 | 277.414 | 0 | 304 |  |  |  | 61.921 | 277.5 | 0 | 305 |  |  |  | 61.922 | 277.318 | 0 | 311 |  |  |  | 61.919 | 535.43 | 0.148 | 79 | 0
479.06 | 277.368 | 0 | 296 |  |  |  | 61.92 | 277.347 | 0 | 303 |  |  |  | 61.919 | 277.292 | 0 | 310 |  |  |  | 61.919 | 533.29 | 0.154 | 82 | 0
479.56 | 277.368 | 0 | 296 |  |  |  | 61.92 | 277.347 | 0 | 303 |  |  |  | 61.919 | 277.292 | 0 | 310 |  |  |  | 61.919 | 533.29 | 0.154 | 82 | 0
480.06 | 277.444 | 0 | 300 |  |  |  | 61.921 | 277.245 | 0 | 305 |  |  |  | 61.921 | 277.273 | 0 | 310 |  |  |  | 61.92 | 533.46 | 0.154 | 82 | 0
480.56 | 277.444 | 0 | 300 |  |  |  | 61.921 | 277.245 | 0 | 305 |  |  |  | 61.921 | 277.273 | 0 | 310 |  |  |  | 61.92 | 533.46 | 0.154 | 82 | 0
481.06 | 277.351 | 0 | 301 |  |  |  | 61.921 | 277.433 | 0 | 306 |  |  |  | 61.921 | 277.221 | 0 | 311 |  |  |  | 61.921 | 533.41 | 0.157 | 84 | 0
481.56 | 277.351 | 0 | 301 |  |  |  | 61.921 | 277.433 | 0 | 306 |  |  |  | 61.921 | 277.221 | 0 | 311 |  |  |  | 61.921 | 533.41 | 0.157 | 84 | 0
482.06 | 277.401 | 0 | 298 |  |  |  | 61.92 | 277.312 | 0 | 301 |  |  |  | 61.919 | 277.317 | 0 | 311 |  |  |  | 61.92 | 529.11 | 0.153 | 81 | 0
482.56 | 277.401 | 0 | 298 |  |  |  | 61.92 | 277.312 | 0 | 301 |  |  |  | 61.919 | 277.317 | 0 | 311 |  |  |  | 61.92 | 529.11 | 0.153 | 81 | 0
483.06 | 277.361 | 0 | 297 |  |  |  | 61.92 | 277.455 | 0 | 300 |  |  |  | 61.919 | 277.288 | 0 | 306 |  |  |  | 61.92 | 526.91 | 0.153 | 81 | 0
483.56 | 277.361 | 0 | 297 |  |  |  | 61.92 | 277.455 | 0 | 300 |  |  |  | 61.919 | 277.288 | 0 | 306 |  |  |  | 61.92 | 526.91 | 0.153 | 81 | 0
484.06 | 277.414 | 0 | 296 |  |  |  | 61.919 | 277.338 | 0 | 301 |  |  |  | 61.921 | 277.271 | 0 | 310 |  |  |  | 61.921 | 531.52 | 0.15 | 80 | 0
484.56 | 277.414 | 0 | 296 |  |  |  | 61.919 | 277.338 | 0 | 301 |  |  |  | 61.921 | 277.271 | 0 | 310 |  |  |  | 61.921 | 531.52 | 0.15 | 80 | 0
485.06 | 277.337 | 0 | 299 |  |  |  | 61.918 | 277.41 | 0 | 306 |  |  |  | 61.919 | 277.242 | 0 | 309 |  |  |  | 61.921 | 533.49 | 0.155 | 83 | 0
485.56 | 277.337 | 0 | 299 |  |  |  | 61.918 | 277.41 | 0 | 306 |  |  |  | 61.919 | 277.242 | 0 | 309 |  |  |  | 61.921 | 533.49 | 0.155 | 83 | 0
486.06 | 277.404 | 0 | 300 |  |  |  | 61.92 | 277.353 | 0 | 305 |  |  |  | 61.921 | 277.331 | 0 | 309 |  |  |  | 61.92 | 533.39 | 0.153 | 82 | 0
486.56 | 277.404 | 0 | 300 |  |  |  | 61.92 | 277.353 | 0 | 305 |  |  |  | 61.921 | 277.331 | 0 | 309 |  |  |  | 61.92 | 533.39 | 0.153 | 82 | 0
487.06 | 277.459 | 0 | 301 |  |  |  | 61.92 | 277.281 | 0 | 300 |  |  |  | 61.92 | 277.294 | 0 | 309 |  |  |  | 61.92 | 533.4 | 0.148 | 79 | 0
487.56 | 277.459 | 0 | 301 |  |  |  | 61.92 | 277.281 | 0 | 300 |  |  |  | 61.92 | 277.294 | 0 | 309 |  |  |  | 61.92 | 533.4 | 0.148 | 79 | 0
488.06 | 277.37 | 0 | 296 |  |  |  | 61.921 | 277.413 | 0 | 301 |  |  |  | 61.921 | 277.265 | 0 | 307 |  |  |  | 61.921 | 537.65 | 0.155 | 83 | 0
488.56 | 277.37 | 0 | 296 |  |  |  | 61.921 | 277.413 | 0 | 301 |  |  |  | 61.921 | 277.265 | 0 | 307 |  |  |  | 61.921 | 537.65 | 0.155 | 83 | 0
489.06 | 277.437 | 0 | 291 |  |  |  | 61.921 | 277.301 | 0 | 300 |  |  |  | 61.919 | 277.243 | 0 | 304 |  |  |  | 61.92 | 539.84 | 0.156 | 84 | 0
489.56 | 277.437 | 0 | 291 |  |  |  | 61.921 | 277.301 | 0 | 300 |  |  |  | 61.919 | 277.243 | 0 | 304 |  |  |  | 61.92 | 539.84 | 0.156 | 84 | 0
490.06 | 277.346 | 0 | 300 |  |  |  | 61.921 | 277.53 | 0 | 308 |  |  |  | 61.922 | 277.34 | 0 | 316 |  |  |  | 61.922 | 535.23 | 0.156 | 84 | 0
490.56 | 277.346 | 0 | 300 |  |  |  | 61.921 | 277.53 | 0 | 308 |  |  |  | 61.922 | 277.34 | 0 | 316 |  |  |  | 61.922 | 535.23 | 0.156 | 84 | 0
491.06 | 277.401 | 0 | 300 |  |  |  | 61.921 | 277.403 | 0 | 300 |  |  |  | 61.92 | 277.306 | 0 | 312 |  |  |  | 61.921 | 533.42 | 0.157 | 84 | 0
491.56 | 277.401 | 0 | 300 |  |  |  | 61.921 | 277.403 | 0 | 300 |  |  |  | 61.92 | 277.306 | 0 | 312 |  |  |  | 61.921 | 533.42 | 0.157 | 84 | 0
492.06 | 277.334 | 0 | 300 |  |  |  | 61.921 | 277.274 | 0 | 304 |  |  |  | 61.92 | 277.265 | 0 | 314 |  |  |  | 61.92 | 533.49 | 0.154 | 82 | 0
492.56 | 277.334 | 0 | 300 |  |  |  | 61.921 | 277.274 | 0 | 304 |  |  |  | 61.92 | 277.265 | 0 | 314 |  |  |  | 61.92 | 533.49 | 0.154 | 82 | 0
493.06 | 277.398 | 0 | 301 |  |  |  | 61.921 | 277.416 | 0 | 305 |  |  |  | 61.919 | 277.257 | 0 | 313 |  |  |  | 61.921 | 533.47 | 0.158 | 84 | 0
493.56 | 277.398 | 0 | 301 |  |  |  | 61.921 | 277.416 | 0 | 305 |  |  |  | 61.919 | 277.257 | 0 | 313 |  |  |  | 61.921 | 533.47 | 0.158 | 84 | 0
494.06 | 277.307 | 0 | 299 |  |  |  | 61.919 | 277.325 | 0 | 302 |  |  |  | 61.92 | 277.243 | 0 | 313 |  |  |  | 61.92 | 529.15 | 0.152 | 81 | 0
494.56 | 277.307 | 0 | 299 |  |  |  | 61.919 | 277.325 | 0 | 302 |  |  |  | 61.92 | 277.243 | 0 | 313 |  |  |  | 61.92 | 529.15 | 0.152 | 81 | 0
495.06 | 277.382 | 0 | 296 |  |  |  | 61.919 | 277.478 | 0 | 302 |  |  |  | 61.92 | 277.329 | 0 | 309 |  |  |  | 61.92 | 527.04 | 0.156 | 82 | 0
495.56 | 277.382 | 0 | 296 |  |  |  | 61.919 | 277.478 | 0 | 302 |  |  |  | 61.92 | 277.329 | 0 | 309 |  |  |  | 61.92 | 527.04 | 0.156 | 82 | 0
496.06 | 277.423 | 0 | 297 |  |  |  | 61.921 | 277.374 | 0 | 304 |  |  |  | 61.919 | 277.281 | 0 | 309 |  |  |  | 61.921 | 531.49 | 0.149 | 79 | 0
496.56 | 277.423 | 0 | 297 |  |  |  | 61.921 | 277.374 | 0 | 304 |  |  |  | 61.919 | 277.281 | 0 | 309 |  |  |  | 61.921 | 531.49 | 0.149 | 79 | 0
497.06 | 277.308 | 0 | 298 |  |  |  | 61.921 | 277.464 | 0 | 306 |  |  |  | 61.922 | 277.251 | 0 | 312 |  |  |  | 61.92 | 533.44 | 0.153 | 82 | 0
497.56 | 277.308 | 0 | 298 |  |  |  | 61.921 | 277.464 | 0 | 306 |  |  |  | 61.922 | 277.251 | 0 | 312 |  |  |  | 61.92 | 533.44 | 0.153 | 82 | 0
498.06 | 277.387 | 0 | 296 |  |  |  | 61.921 | 277.4 | 0 | 302 |  |  |  | 61.918 | 277.247 | 0 | 310 |  |  |  | 61.919 | 533.45 | 0.152 | 81 | 0
498.56 | 277.387 | 0 | 296 |  |  |  | 61.921 | 277.4 | 0 | 302 |  |  |  | 61.918 | 277.247 | 0 | 310 |  |  |  | 61.919 | 533.45 | 0.152 | 81 | 0
499.06 | 277.311 | 0 | 299 |  |  |  | 61.92 | 277.287 | 0 | 302 |  |  |  | 61.92 | 277.334 | 0 | 308 |  |  |  | 61.921 | 533.39 | 0.152 | 81 | 0
499.56 | 277.311 | 0 | 299 |  |  |  | 61.92 | 277.287 | 0 | 302 |  |  |  | 61.92 | 277.334 | 0 | 308 |  |  |  | 61.921 | 533.39 | 0.152 | 81 | 0
500.06 | 277.366 | 0 | 295 |  |  |  | 61.92 | 277.508 | 0 | 301 |  |  |  | 61.921 | 277.299 | 0 | 309 |  |  |  | 61.92 | 537.58 | 0.156 | 84 | 0
500.56 | 277.366 | 0 | 295 |  |  |  | 61.92 | 277.508 | 0 | 301 |  |  |  | 61.921 | 277.299 | 0 | 309 |  |  |  | 61.92 | 537.58 | 0.156 | 84 | 0
501.06 | 277.313 | 0 | 293 |  |  |  | 61.921 | 277.328 | 0 | 293 |  |  |  | 61.92 | 277.247 | 0 | 305 |  |  |  | 61.92 | 539.84 | 0.15 | 81 | 0
501.56 | 277.313 | 0 | 293 |  |  |  | 61.921 | 277.328 | 0 | 293 |  |  |  | 61.92 | 277.247 | 0 | 305 |  |  |  | 61.92 | 539.84 | 0.15 | 81 | 0
502.06 | 277.376 | 0 | 302 |  |  |  | 61.92 | 277.54 | 0 | 305 |  |  |  | 61.922 | 277.232 | 0 | 311 |  |  |  | 61.92 | 535.38 | 0.154 | 82 | 0
502.6 | 277.376 | 0 | 302 |  |  |  | 61.92 | 277.54 | 0 | 305 |  |  |  | 61.922 | 277.232 | 0 | 311 |  |  |  | 61.92 | 535.38 | 0.154 | 82 | 0
503.1 | 277.262 | 0 | 294 |  |  |  | 61.92 | 277.437 | 0 | 303 |  |  |  | 61.919 | 277.321 | 0 | 311 |  |  |  | 61.921 | 533.4 | 0.153 | 81 | 0
503.58 | 277.262 | 0 | 294 |  |  |  | 61.92 | 277.437 | 0 | 303 |  |  |  | 61.919 | 277.321 | 0 | 311 |  |  |  | 61.921 | 533.4 | 0.153 | 81 | 0
504.08 | 277.346 | 0 | 298 |  |  |  | 61.919 | 277.315 | 0 | 304 |  |  |  | 61.919 | 277.315 | 0 | 313 |  |  |  | 61.921 | 533.41 | 0.146 | 78 | 0
504.57 | 277.346 | 0 | 298 |  |  |  | 61.919 | 277.315 | 0 | 304 |  |  |  | 61.919 | 277.315 | 0 | 313 |  |  |  | 61.921 | 533.41 | 0.146 | 78 | 0
505.07 | 277.408 | 0 | 301 |  |  |  | 61.921 | 277.474 | 0 | 303 |  |  |  | 61.92 | 277.267 | 0 | 314 |  |  |  | 61.92 | 533.51 | 0.152 | 81 | 0
505.56 | 277.408 | 0 | 301 |  |  |  | 61.921 | 277.474 | 0 | 303 |  |  |  | 61.92 | 277.267 | 0 | 314 |  |  |  | 61.92 | 533.51 | 0.152 | 81 | 0
506.06 | 277.303 | 0 | 298 |  |  |  | 61.921 | 277.315 | 0 | 301 |  |  |  | 61.92 | 277.213 | 0 | 310 |  |  |  | 61.92 | 529.08 | 0.146 | 77 | 0
506.6 | 277.303 | 0 | 298 |  |  |  | 61.921 | 277.315 | 0 | 301 |  |  |  | 61.92 | 277.213 | 0 | 310 |  |  |  | 61.92 | 529.08 | 0.146 | 77 | 0
507.1 | 277.374 | 0 | 296 |  |  |  | 61.921 | 277.482 | 0 | 300 |  |  |  | 61.92 | 277.308 | 0 | 306 |  |  |  | 61.92 | 526.92 | 0.15 | 79 | 0
507.58 | 277.323 | 0 | 296 |  |  |  | 61.921 | 277.349 | 0 | 299 |  |  |  | 61.919 | 277.3 | 0 | 311 |  |  |  | 61.921 | 531.39 | 0.156 | 83 | 0
508.08 | 277.323 | 0 | 296 |  |  |  | 61.921 | 277.349 | 0 | 299 |  |  |  | 61.919 | 277.3 | 0 | 311 |  |  |  | 61.921 | 531.39 | 0.156 | 83 | 0
508.56 | 277.362 | 0 | 300 |  |  |  | 61.921 | 277.481 | 0 | 303 |  |  |  | 61.921 | 277.271 | 0 | 311 |  |  |  | 61.92 | 533.42 | 0.151 | 81 | 0
509.06 | 277.362 | 0 | 300 |  |  |  | 61.921 | 277.481 | 0 | 303 |  |  |  | 61.921 | 277.271 | 0 | 311 |  |  |  | 61.92 | 533.42 | 0.151 | 81 | 0
509.56 | 277.314 | 0 | 297 |  |  |  | 61.921 | 277.433 | 0 | 303 |  |  |  | 61.919 | 277.22 | 0 | 313 |  |  |  | 61.92 | 533.4 | 0.158 | 84 | 0
510.06 | 277.314 | 0 | 297 |  |  |  | 61.921 | 277.433 | 0 | 303 |  |  |  | 61.919 | 277.22 | 0 | 313 |  |  |  | 61.92 | 533.4 | 0.158 | 84 | 0
510.56 | 277.37 | 0 | 297 |  |  |  | 61.921 | 277.302 | 0 | 299 |  |  |  | 61.919 | 277.319 | 0 | 316 |  |  |  | 61.921 | 533.48 | 0.156 | 83 | 0
511.06 | 277.37 | 0 | 297 |  |  |  | 61.921 | 277.302 | 0 | 299 |  |  |  | 61.919 | 277.319 | 0 | 316 |  |  |  | 61.921 | 533.48 | 0.156 | 83 | 0
511.56 | 277.265 | 0 | 297 |  |  |  | 61.921 | 277.475 | 0 | 304 |  |  |  | 61.92 | 277.299 | 0 | 315 |  |  |  | 61.92 | 537.62 | 0.156 | 84 | 0
512.06 | 277.265 | 0 | 297 |  |  |  | 61.921 | 277.475 | 0 | 304 |  |  |  | 61.92 | 277.299 | 0 | 315 |  |  |  | 61.92 | 537.62 | 0.156 | 84 | 0
512.56 | 277.36 | 0 | 293 |  |  |  | 61.92 | 277.337 | 0 | 298 |  |  |  | 61.92 | 277.281 | 0 | 305 |  |  |  | 61.919 | 539.84 | 0.159 | 86 | 0
513.06 | 277.36 | 0 | 293 |  |  |  | 61.92 | 277.337 | 0 | 298 |  |  |  | 61.92 | 277.281 | 0 | 305 |  |  |  | 61.919 | 539.84 | 0.159 | 86 | 0
513.56 | 277.42 | 0 | 300 |  |  |  | 61.921 | 277.481 | 0 | 303 |  |  |  | 61.922 | 277.244 | 0 | 311 |  |  |  | 61.921 | 535.34 | 0.156 | 83 | 0
514.06 | 277.42 | 0 | 300 |  |  |  | 61.921 | 277.481 | 0 | 303 |  |  |  | 61.922 | 277.244 | 0 | 311 |  |  |  | 61.921 | 535.34 | 0.156 | 83 | 0
514.56 | 277.337 | 0 | 301 |  |  |  | 61.921 | 277.341 | 0 | 303 |  |  |  | 61.92 | 277.326 | 0 | 314 |  |  |  | 61.92 | 533.39 | 0.158 | 84 | 0
515.06 | 277.337 | 0 | 301 |  |  |  | 61.921 | 277.341 | 0 | 303 |  |  |  | 61.92 | 277.326 | 0 | 314 |  |  |  | 61.92 | 533.39 | 0.158 | 84 | 0
515.56 | 277.396 | 0 | 298 |  |  |  | 61.92 | 277.271 | 0 | 301 |  |  |  | 61.92 | 277.288 | 0 | 309 |  |  |  | 61.92 | 533.37 | 0.15 | 80 | 0
516.06 | 277.396 | 0 | 298 |  |  |  | 61.92 | 277.271 | 0 | 301 |  |  |  | 61.92 | 277.288 | 0 | 309 |  |  |  | 61.92 | 533.37 | 0.15 | 80 | 0
516.56 | 277.378 | 0 | 297 |  |  |  | 61.921 | 277.369 | 0 | 302 |  |  |  | 61.92 | 277.277 | 0 | 310 |  |  |  | 61.92 | 533.32 | 0.152 | 81 | 0
517.06 | 277.378 | 0 | 297 |  |  |  | 61.921 | 277.369 | 0 | 302 |  |  |  | 61.92 | 277.277 | 0 | 310 |  |  |  | 61.92 | 533.32 | 0.152 | 81 | 0
517.56 | 277.411 | 0 | 299 |  |  |  | 61.919 | 277.279 | 0 | 301 |  |  |  | 61.92 | 277.255 | 0 | 311 |  |  |  | 61.92 | 529.29 | 0.155 | 82 | 0
518.06 | 277.411 | 0 | 299 |  |  |  | 61.919 | 277.279 | 0 | 301 |  |  |  | 61.92 | 277.255 | 0 | 311 |  |  |  | 61.92 | 529.29 | 0.155 | 82 | 0
518.56 | 277.338 | 0 | 294 |  |  |  | 61.921 | 277.499 | 0 | 297 |  |  |  | 61.923 | 277.332 | 0 | 307 |  |  |  | 61.922 | 526.89 | 0.156 | 82 | 0
519.06 | 277.338 | 0 | 294 |  |  |  | 61.921 | 277.499 | 0 | 297 |  |  |  | 61.923 | 277.332 | 0 | 307 |  |  |  | 61.922 | 526.89 | 0.156 | 82 | 0
519.56 | 277.401 | 0 | 295 |  |  |  | 61.92 | 277.373 | 0 | 302 |  |  |  | 61.92 | 277.304 | 0 | 310 |  |  |  | 61.92 | 531.3 | 0.151 | 80 | 0
520.06 | 277.401 | 0 | 295 |  |  |  | 61.92 | 277.373 | 0 | 302 |  |  |  | 61.92 | 277.304 | 0 | 310 |  |  |  | 61.92 | 531.3 | 0.151 | 80 | 0
520.56 | 277.299 | 0 | 298 |  |  |  | 61.921 | 277.426 | 0 | 299 |  |  |  | 61.92 | 277.275 | 0 | 309 |  |  |  | 61.92 | 533.25 | 0.15 | 80 | 0
521.06 | 277.299 | 0 | 298 |  |  |  | 61.921 | 277.426 | 0 | 299 |  |  |  | 61.92 | 277.275 | 0 | 309 |  |  |  | 61.92 | 533.25 | 0.15 | 80 | 0
521.56 | 277.387 | 0 | 299 |  |  |  | 61.921 | 277.369 | 0 | 301 |  |  |  | 61.919 | 277.269 | 0 | 310 |  |  |  | 61.92 | 533.45 | 0.155 | 83 | 0
522.06 | 277.387 | 0 | 299 |  |  |  | 61.921 | 277.369 | 0 | 301 |  |  |  | 61.919 | 277.269 | 0 | 310 |  |  |  | 61.92 | 533.45 | 0.155 | 83 | 0
522.56 | 277.446 | 0 | 299 |  |  |  | 61.921 | 277.28 | 0 | 303 |  |  |  | 61.92 | 277.228 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.155 | 83 | 0
523.06 | 277.446 | 0 | 299 |  |  |  | 61.921 | 277.28 | 0 | 303 |  |  |  | 61.92 | 277.228 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.155 | 83 | 0
523.56 | 277.364 | 0 | 298 |  |  |  | 61.921 | 277.426 | 0 | 301 |  |  |  | 61.921 | 277.32 | 0 | 308 |  |  |  | 61.92 | 537.48 | 0.153 | 82 | 0
524.06 | 277.364 | 0 | 298 |  |  |  | 61.921 | 277.426 | 0 | 301 |  |  |  | 61.921 | 277.32 | 0 | 308 |  |  |  | 61.92 | 537.48 | 0.153 | 82 | 0
524.56 | 277.421 | 0 | 291 |  |  |  | 61.92 | 277.301 | 0 | 296 |  |  |  | 61.92 | 277.275 | 0 | 301 |  |  |  | 61.92 | 539.9 | 0.153 | 83 | 0
525.06 | 277.421 | 0 | 291 |  |  |  | 61.92 | 277.301 | 0 | 296 |  |  |  | 61.92 | 277.275 | 0 | 301 |  |  |  | 61.92 | 539.9 | 0.153 | 83 | 0
525.56 | 277.393 | 0 | 300 |  |  |  | 61.921 | 277.436 | 0 | 304 |  |  |  | 61.922 | 277.256 | 0 | 312 |  |  |  | 61.919 | 535.55 | 0.153 | 82 | 0
526.06 | 277.393 | 0 | 300 |  |  |  | 61.921 | 277.436 | 0 | 304 |  |  |  | 61.922 | 277.256 | 0 | 312 |  |  |  | 61.919 | 535.55 | 0.153 | 82 | 0
526.56 | 277.44 | 0 | 303 |  |  |  | 61.92 | 277.324 | 0 | 302 |  |  |  | 61.92 | 277.227 | 0 | 312 |  |  |  | 61.919 | 533.43 | 0.151 | 80 | 0
527.06 | 277.44 | 0 | 303 |  |  |  | 61.92 | 277.324 | 0 | 302 |  |  |  | 61.92 | 277.227 | 0 | 312 |  |  |  | 61.919 | 533.43 | 0.151 | 80 | 0
527.56 | 277.348 | 0 | 300 |  |  |  | 61.92 | 277.227 | 0 | 306 |  |  |  | 61.919 | 277.344 | 0 | 312 |  |  |  | 61.919 | 533.47 | 0.154 | 82 | 0
528.06 | 277.348 | 0 | 300 |  |  |  | 61.92 | 277.227 | 0 | 306 |  |  |  | 61.919 | 277.344 | 0 | 312 |  |  |  | 61.919 | 533.47 | 0.154 | 82 | 0
528.56 | 277.423 | 0 | 299 |  |  |  | 61.92 | 277.425 | 0 | 299 |  |  |  | 61.92 | 277.298 | 0 | 307 |  |  |  | 61.92 | 533.47 | 0.151 | 81 | 0
529.06 | 277.423 | 0 | 299 |  |  |  | 61.92 | 277.425 | 0 | 299 |  |  |  | 61.92 | 277.298 | 0 | 307 |  |  |  | 61.92 | 533.47 | 0.151 | 81 | 0
529.56 | 277.288 | 0 | 298 |  |  |  | 61.919 | 277.266 | 0 | 305 |  |  |  | 61.921 | 277.259 | 0 | 313 |  |  |  | 61.92 | 529.34 | 0.153 | 81 | 0
530.06 | 277.288 | 0 | 298 |  |  |  | 61.919 | 277.266 | 0 | 305 |  |  |  | 61.921 | 277.259 | 0 | 313 |  |  |  | 61.92 | 529.34 | 0.153 | 81 | 0
530.56 | 277.343 | 0 | 296 |  |  |  | 61.921 | 277.408 | 0 | 297 |  |  |  | 61.922 | 277.241 | 0 | 311 |  |  |  | 61.921 | 526.97 | 0.156 | 82 | 0
531.06 | 277.343 | 0 | 296 |  |  |  | 61.921 | 277.408 | 0 | 297 |  |  |  | 61.922 | 277.241 | 0 | 311 |  |  |  | 61.921 | 526.97 | 0.156 | 82 | 0
531.56 | 277.394 | 0 | 295 |  |  |  | 61.921 | 277.32 | 0 | 301 |  |  |  | 61.92 | 277.317 | 0 | 309 |  |  |  | 61.92 | 531.19 | 0.157 | 83 | 0
532.06 | 277.394 | 0 | 295 |  |  |  | 61.921 | 277.32 | 0 | 301 |  |  |  | 61.92 | 277.317 | 0 | 309 |  |  |  | 61.92 | 531.19 | 0.157 | 83 | 0
532.56 | 277.352 | 0 | 298 |  |  |  | 61.921 | 277.47 | 0 | 304 |  |  |  | 61.92 | 277.306 | 0 | 304 |  |  |  | 61.921 | 533.29 | 0.152 | 81 | 0
533.06 | 277.352 | 0 | 298 |  |  |  | 61.921 | 277.47 | 0 | 304 |  |  |  | 61.92 | 277.306 | 0 | 304 |  |  |  | 61.921 | 533.29 | 0.152 | 81 | 0
533.56 | 277.39 | 0 | 300 |  |  |  | 61.919 | 277.392 | 0 | 303 |  |  |  | 61.921 | 277.247 | 0 | 312 |  |  |  | 61.92 | 533.49 | 0.156 | 83 | 0
534.06 | 277.39 | 0 | 300 |  |  |  | 61.919 | 277.392 | 0 | 303 |  |  |  | 61.921 | 277.247 | 0 | 312 |  |  |  | 61.92 | 533.49 | 0.156 | 83 | 0
534.56 | 277.372 | 0 | 296 |  |  |  | 61.921 | 277.261 | 0 | 301 |  |  |  | 61.919 | 277.223 | 0 | 313 |  |  |  | 61.92 | 533.3 | 0.152 | 81 | 0
535.08 | 277.372 | 0 | 296 |  |  |  | 61.921 | 277.261 | 0 | 301 |  |  |  | 61.919 | 277.223 | 0 | 313 |  |  |  | 61.92 | 533.3 | 0.152 | 81 | 0
535.58 | 277.406 | 0 | 296 |  |  |  | 61.92 | 277.474 | 0 | 302 |  |  |  | 61.92 | 277.314 | 0 | 309 |  |  |  | 61.921 | 537.42 | 0.157 | 84 | 0
536.07 | 277.406 | 0 | 296 |  |  |  | 61.92 | 277.474 | 0 | 302 |  |  |  | 61.92 | 277.314 | 0 | 309 |  |  |  | 61.921 | 537.42 | 0.157 | 84 | 0
536.57 | 277.313 | 0 | 291 |  |  |  | 61.921 | 277.305 | 0 | 295 |  |  |  | 61.921 | 277.316 | 0 | 308 |  |  |  | 61.92 | 539.87 | 0.156 | 84 | 0
537.06 | 277.313 | 0 | 291 |  |  |  | 61.921 | 277.305 | 0 | 295 |  |  |  | 61.921 | 277.316 | 0 | 308 |  |  |  | 61.92 | 539.87 | 0.156 | 84 | 0
537.56 | 277.408 | 0 | 302 |  |  |  | 61.92 | 277.513 | 0 | 305 |  |  |  | 61.923 | 277.272 | 0 | 317 |  |  |  | 61.92 | 535.49 | 0.15 | 81 | 0
538.09 | 277.265 | 0 | 298 |  |  |  | 61.92 | 277.383 | 0 | 303 |  |  |  | 61.92 | 277.227 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.155 | 83 | 0
538.59 | 277.265 | 0 | 298 |  |  |  | 61.92 | 277.383 | 0 | 303 |  |  |  | 61.92 | 277.227 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.155 | 83 | 0
539.08 | 277.324 | 0 | 301 |  |  |  | 61.921 | 277.287 | 0 | 303 |  |  |  | 61.92 | 277.308 | 0 | 310 |  |  |  | 61.92 | 533.48 | 0.155 | 83 | 0
539.58 | 277.324 | 0 | 301 |  |  |  | 61.921 | 277.287 | 0 | 303 |  |  |  | 61.92 | 277.308 | 0 | 310 |  |  |  | 61.92 | 533.48 | 0.155 | 83 | 0
540.07 | 277.356 | 0 | 297 |  |  |  | 61.92 | 277.421 | 0 | 305 |  |  |  | 61.92 | 277.296 | 0 | 314 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 0
540.57 | 277.356 | 0 | 297 |  |  |  | 61.92 | 277.421 | 0 | 305 |  |  |  | 61.92 | 277.296 | 0 | 314 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 0
541.06 | 277.34 | 0 | 301 |  |  |  | 61.921 | 277.31 | 0 | 303 |  |  |  | 61.919 | 277.28 | 0 | 313 |  |  |  | 61.921 | 529.44 | 0.148 | 78 | 0
541.56 | 277.34 | 0 | 301 |  |  |  | 61.921 | 277.31 | 0 | 303 |  |  |  | 61.919 | 277.28 | 0 | 313 |  |  |  | 61.921 | 529.44 | 0.148 | 78 | 0
542.06 | 277.368 | 0 | 294 |  |  |  | 61.922 | 277.494 | 0 | 302 |  |  |  | 61.923 | 277.23 | 0 | 306 |  |  |  | 61.92 | 526.87 | 0.153 | 81 | 0
542.56 | 277.368 | 0 | 294 |  |  |  | 61.922 | 277.494 | 0 | 302 |  |  |  | 61.923 | 277.23 | 0 | 306 |  |  |  | 61.92 | 526.87 | 0.153 | 81 | 0
543.06 | 277.336 | 0 | 301 |  |  |  | 61.921 | 277.361 | 0 | 301 |  |  |  | 61.92 | 277.268 | 0 | 310 |  |  |  | 61.922 | 531.27 | 0.157 | 83 | 0
543.56 | 277.336 | 0 | 301 |  |  |  | 61.921 | 277.361 | 0 | 301 |  |  |  | 61.92 | 277.268 | 0 | 310 |  |  |  | 61.922 | 531.27 | 0.157 | 83 | 0
544.06 | 277.389 | 0 | 297 |  |  |  | 61.921 | 277.495 | 0 | 303 |  |  |  | 61.919 | 277.306 | 0 | 307 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 0
544.56 | 277.389 | 0 | 297 |  |  |  | 61.921 | 277.495 | 0 | 303 |  |  |  | 61.919 | 277.306 | 0 | 307 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 0
545.06 | 277.287 | 0 | 298 |  |  |  | 61.92 | 277.412 | 0 | 301 |  |  |  | 61.919 | 277.306 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 0
545.56 | 277.287 | 0 | 298 |  |  |  | 61.92 | 277.412 | 0 | 301 |  |  |  | 61.919 | 277.306 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.154 | 82 | 0
546.06 | 277.368 | 0 | 296 |  |  |  | 61.919 | 277.312 | 0 | 301 |  |  |  | 61.921 | 277.26 | 0 | 310 |  |  |  | 61.92 | 533.27 | 0.152 | 81 | 0
546.56 | 277.368 | 0 | 296 |  |  |  | 61.919 | 277.312 | 0 | 301 |  |  |  | 61.921 | 277.26 | 0 | 310 |  |  |  | 61.92 | 533.27 | 0.152 | 81 | 0
547.06 | 277.284 | 0 | 297 |  |  |  | 61.919 | 277.533 | 0 | 301 |  |  |  | 61.92 | 277.216 | 0 | 310 |  |  |  | 61.921 | 537.35 | 0.152 | 82 | 0
547.56 | 277.284 | 0 | 297 |  |  |  | 61.919 | 277.533 | 0 | 301 |  |  |  | 61.92 | 277.216 | 0 | 310 |  |  |  | 61.921 | 537.35 | 0.152 | 82 | 0
548.06 | 277.328 | 0 | 289 |  |  |  | 61.921 | 277.414 | 0 | 296 |  |  |  | 61.919 | 277.29 | 0 | 306 |  |  |  | 61.92 | 539.84 | 0.156 | 84 | 0
548.56 | 277.328 | 0 | 289 |  |  |  | 61.921 | 277.414 | 0 | 296 |  |  |  | 61.919 | 277.29 | 0 | 306 |  |  |  | 61.92 | 539.84 | 0.156 | 84 | 0
549.06 | 277.326 | 0 | 303 |  |  |  | 61.92 | 277.522 | 0 | 302 |  |  |  | 61.923 | 277.283 | 0 | 311 |  |  |  | 61.92 | 535.56 | 0.155 | 83 | 0
549.56 | 277.326 | 0 | 303 |  |  |  | 61.92 | 277.522 | 0 | 302 |  |  |  | 61.923 | 277.283 | 0 | 311 |  |  |  | 61.92 | 535.56 | 0.155 | 83 | 0
550.06 | 277.347 | 0 | 296 |  |  |  | 61.921 | 277.403 | 0 | 301 |  |  |  | 61.921 | 277.275 | 0 | 314 |  |  |  | 61.921 | 533.43 | 0.155 | 82 | 0
550.56 | 277.347 | 0 | 296 |  |  |  | 61.921 | 277.403 | 0 | 301 |  |  |  | 61.921 | 277.275 | 0 | 314 |  |  |  | 61.921 | 533.43 | 0.155 | 82 | 0
551.06 | 277.38 | 0 | 295 |  |  |  | 61.92 | 277.259 | 0 | 302 |  |  |  | 61.919 | 277.222 | 0 | 316 |  |  |  | 61.92 | 533.33 | 0.153 | 81 | 0
551.56 | 277.38 | 0 | 295 |  |  |  | 61.92 | 277.259 | 0 | 302 |  |  |  | 61.919 | 277.222 | 0 | 316 |  |  |  | 61.92 | 533.33 | 0.153 | 81 | 0
552.06 | 277.341 | 0 | 297 |  |  |  | 61.921 | 277.41 | 0 | 303 |  |  |  | 61.919 | 277.312 | 0 | 309 |  |  |  | 61.92 | 533.38 | 0.156 | 83 | 0
552.56 | 277.341 | 0 | 297 |  |  |  | 61.921 | 277.41 | 0 | 303 |  |  |  | 61.919 | 277.312 | 0 | 309 |  |  |  | 61.92 | 533.38 | 0.156 | 83 | 0
553.06 | 277.393 | 0 | 297 |  |  |  | 61.92 | 277.319 | 0 | 301 |  |  |  | 61.92 | 277.281 | 0 | 310 |  |  |  | 61.921 | 529.32 | 0.153 | 81 | 0
553.56 | 277.393 | 0 | 297 |  |  |  | 61.92 | 277.319 | 0 | 301 |  |  |  | 61.92 | 277.281 | 0 | 310 |  |  |  | 61.921 | 529.32 | 0.153 | 81 | 0
554.06 | 277.299 | 0 | 296 |  |  |  | 61.921 | 277.443 | 0 | 300 |  |  |  | 61.921 | 277.275 | 0 | 305 |  |  |  | 61.921 | 527 | 0.16 | 84 | 0
554.56 | 277.299 | 0 | 296 |  |  |  | 61.921 | 277.443 | 0 | 300 |  |  |  | 61.921 | 277.275 | 0 | 305 |  |  |  | 61.921 | 527 | 0.16 | 84 | 0
555.06 | 277.383 | 0 | 299 |  |  |  | 61.919 | 277.297 | 0 | 300 |  |  |  | 61.919 | 277.244 | 0 | 309 |  |  |  | 61.921 | 531.17 | 0.153 | 81 | 0
555.56 | 277.383 | 0 | 299 |  |  |  | 61.919 | 277.297 | 0 | 300 |  |  |  | 61.919 | 277.244 | 0 | 309 |  |  |  | 61.921 | 531.17 | 0.153 | 81 | 0
556.06 | 277.313 | 0 | 298 |  |  |  | 61.92 | 277.475 | 0 | 304 |  |  |  | 61.921 | 277.323 | 0 | 310 |  |  |  | 61.92 | 533.23 | 0.16 | 85 | 0
556.56 | 277.313 | 0 | 298 |  |  |  | 61.92 | 277.475 | 0 | 304 |  |  |  | 61.921 | 277.323 | 0 | 310 |  |  |  | 61.92 | 533.23 | 0.16 | 85 | 0
557.06 | 277.358 | 0 | 298 |  |  |  | 61.921 | 277.439 | 0 | 303 |  |  |  | 61.92 | 277.264 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
557.56 | 277.358 | 0 | 298 |  |  |  | 61.921 | 277.439 | 0 | 303 |  |  |  | 61.92 | 277.264 | 0 | 310 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
558.06 | 277.323 | 0 | 296 |  |  |  | 61.918 | 277.268 | 0 | 301 |  |  |  | 61.921 | 277.234 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.155 | 83 | 0
558.56 | 277.323 | 0 | 296 |  |  |  | 61.918 | 277.268 | 0 | 301 |  |  |  | 61.921 | 277.234 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.155 | 83 | 0
559.06 | 277.388 | 0 | 296 |  |  |  | 61.921 | 277.428 | 0 | 301 |  |  |  | 61.92 | 277.225 | 0 | 305 |  |  |  | 61.92 | 537.33 | 0.159 | 86 | 0
559.56 | 277.388 | 0 | 296 |  |  |  | 61.921 | 277.428 | 0 | 301 |  |  |  | 61.92 | 277.225 | 0 | 305 |  |  |  | 61.92 | 537.33 | 0.159 | 86 | 0
560.06 | 277.417 | 0 | 291 |  |  |  | 61.919 | 277.351 | 0 | 295 |  |  |  | 61.92 | 277.311 | 0 | 303 |  |  |  | 61.921 | 539.82 | 0.155 | 84 | 0
560.56 | 277.417 | 0 | 291 |  |  |  | 61.919 | 277.351 | 0 | 295 |  |  |  | 61.92 | 277.311 | 0 | 303 |  |  |  | 61.921 | 539.82 | 0.155 | 84 | 0
561.06 | 277.365 | 0 | 297 |  |  |  | 61.92 | 277.517 | 0 | 306 |  |  |  | 61.923 | 277.29 | 0 | 312 |  |  |  | 61.919 | 535.63 | 0.156 | 84 | 0
561.56 | 277.365 | 0 | 297 |  |  |  | 61.92 | 277.517 | 0 | 306 |  |  |  | 61.923 | 277.29 | 0 | 312 |  |  |  | 61.919 | 535.63 | 0.156 | 84 | 0
562.06 | 277.429 | 0 | 299 |  |  |  | 61.92 | 277.376 | 0 | 303 |  |  |  | 61.919 | 277.249 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.154 | 82 | 0
562.56 | 277.429 | 0 | 299 |  |  |  | 61.92 | 277.376 | 0 | 303 |  |  |  | 61.919 | 277.249 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.154 | 82 | 0
563.06 | 277.304 | 0 | 299 |  |  |  | 61.921 | 277.25 | 0 | 304 |  |  |  | 61.92 | 277.226 | 0 | 312 |  |  |  | 61.92 | 533.4 | 0.151 | 80 | 0
563.56 | 277.304 | 0 | 299 |  |  |  | 61.921 | 277.25 | 0 | 304 |  |  |  | 61.92 | 277.226 | 0 | 312 |  |  |  | 61.92 | 533.4 | 0.151 | 80 | 0
564.06 | 277.394 | 0 | 298 |  |  |  | 61.92 | 277.373 | 0 | 301 |  |  |  | 61.92 | 277.209 | 0 | 313 |  |  |  | 61.919 | 533.28 | 0.156 | 83 | 0
564.56 | 277.394 | 0 | 298 |  |  |  | 61.92 | 277.373 | 0 | 301 |  |  |  | 61.92 | 277.209 | 0 | 313 |  |  |  | 61.919 | 533.28 | 0.156 | 83 | 0
565.06 | 277.32 | 0 | 295 |  |  |  | 61.921 | 277.251 | 0 | 304 |  |  |  | 61.919 | 277.3 | 0 | 310 |  |  |  | 61.919 | 529.49 | 0.155 | 82 | 0
565.6 | 277.32 | 0 | 295 |  |  |  | 61.921 | 277.251 | 0 | 304 |  |  |  | 61.919 | 277.3 | 0 | 310 |  |  |  | 61.919 | 529.49 | 0.155 | 82 | 0
566.1 | 277.375 | 0 | 295 |  |  |  | 61.92 | 277.487 | 0 | 299 |  |  |  | 61.924 | 277.25 | 0 | 310 |  |  |  | 61.921 | 526.89 | 0.149 | 78 | 0
566.58 | 277.375 | 0 | 295 |  |  |  | 61.92 | 277.487 | 0 | 299 |  |  |  | 61.924 | 277.25 | 0 | 310 |  |  |  | 61.921 | 526.89 | 0.149 | 78 | 0
567.08 | 277.324 | 0 | 295 |  |  |  | 61.918 | 277.315 | 0 | 298 |  |  |  | 61.919 | 277.218 | 0 | 313 |  |  |  | 61.919 | 531 | 0.159 | 85 | 0
567.57 | 277.324 | 0 | 295 |  |  |  | 61.918 | 277.315 | 0 | 298 |  |  |  | 61.919 | 277.218 | 0 | 313 |  |  |  | 61.919 | 531 | 0.159 | 85 | 0
568.07 | 277.377 | 0 | 297 |  |  |  | 61.921 | 277.376 | 0 | 301 |  |  |  | 61.92 | 277.209 | 0 | 308 |  |  |  | 61.919 | 533.39 | 0.151 | 81 | 0
568.56 | 277.377 | 0 | 297 |  |  |  | 61.921 | 277.376 | 0 | 301 |  |  |  | 61.92 | 277.209 | 0 | 308 |  |  |  | 61.919 | 533.39 | 0.151 | 81 | 0
569.06 | 277.433 | 0 | 297 |  |  |  | 61.921 | 277.402 | 0 | 308 |  |  |  | 61.919 | 277.312 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.153 | 82 | 0
569.6 | 277.433 | 0 | 297 |  |  |  | 61.921 | 277.402 | 0 | 308 |  |  |  | 61.919 | 277.312 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.153 | 82 | 0
570.1 | 277.34 | 0 | 297 |  |  |  | 61.921 | 277.278 | 0 | 298 |  |  |  | 61.92 | 277.286 | 0 | 311 |  |  |  | 61.921 | 533.41 | 0.152 | 81 | 0
570.58 | 277.426 | 0 | 297 |  |  |  | 61.92 | 277.443 | 0 | 299 |  |  |  | 61.92 | 277.219 | 0 | 307 |  |  |  | 61.919 | 537.16 | 0.153 | 82 | 0
571.08 | 277.426 | 0 | 297 |  |  |  | 61.92 | 277.443 | 0 | 299 |  |  |  | 61.92 | 277.219 | 0 | 307 |  |  |  | 61.919 | 537.16 | 0.153 | 82 | 0
571.56 | 277.289 | 0 | 292 |  |  |  | 61.921 | 277.324 | 0 | 294 |  |  |  | 61.92 | 277.21 | 0 | 304 |  |  |  | 61.921 | 539.83 | 0.158 | 85 | 0
572.06 | 277.289 | 0 | 292 |  |  |  | 61.921 | 277.324 | 0 | 294 |  |  |  | 61.92 | 277.21 | 0 | 304 |  |  |  | 61.921 | 539.83 | 0.158 | 85 | 0
572.56 | 277.351 | 0 | 302 |  |  |  | 61.921 | 277.457 | 0 | 304 |  |  |  | 61.923 | 277.293 | 0 | 313 |  |  |  | 61.92 | 535.53 | 0.155 | 83 | 0
573.06 | 277.351 | 0 | 302 |  |  |  | 61.921 | 277.457 | 0 | 304 |  |  |  | 61.923 | 277.293 | 0 | 313 |  |  |  | 61.92 | 535.53 | 0.155 | 83 | 0
573.56 | 277.318 | 0 | 300 |  |  |  | 61.92 | 277.354 | 0 | 304 |  |  |  | 61.919 | 277.286 | 0 | 312 |  |  |  | 61.921 | 533.46 | 0.152 | 81 | 0
574.06 | 277.318 | 0 | 300 |  |  |  | 61.92 | 277.354 | 0 | 304 |  |  |  | 61.919 | 277.286 | 0 | 312 |  |  |  | 61.921 | 533.46 | 0.152 | 81 | 0
574.56 | 277.351 | 0 | 300 |  |  |  | 61.921 | 277.305 | 0 | 301 |  |  |  | 61.92 | 277.247 | 0 | 308 |  |  |  | 61.92 | 533.32 | 0.153 | 81 | 0
575.06 | 277.351 | 0 | 300 |  |  |  | 61.921 | 277.305 | 0 | 301 |  |  |  | 61.92 | 277.247 | 0 | 308 |  |  |  | 61.92 | 533.32 | 0.153 | 81 | 0
575.56 | 277.299 | 0 | 298 |  |  |  | 61.919 | 277.424 | 0 | 303 |  |  |  | 61.919 | 277.2 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.158 | 84 | 0
576.06 | 277.299 | 0 | 298 |  |  |  | 61.919 | 277.424 | 0 | 303 |  |  |  | 61.919 | 277.2 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.158 | 84 | 0
576.56 | 277.38 | 0 | 297 |  |  |  | 61.921 | 277.285 | 0 | 304 |  |  |  | 61.92 | 277.292 | 0 | 311 |  |  |  | 61.924 | 529.44 | 0.155 | 82 | 0
577.06 | 277.38 | 0 | 297 |  |  |  | 61.921 | 277.285 | 0 | 304 |  |  |  | 61.92 | 277.292 | 0 | 311 |  |  |  | 61.924 | 529.44 | 0.155 | 82 | 0
577.56 | 277.413 | 0 | 295 |  |  |  | 61.92 | 277.49 | 0 | 302 |  |  |  | 61.922 | 277.28 | 0 | 308 |  |  |  | 61.921 | 526.96 | 0.152 | 80 | 0
578.06 | 277.413 | 0 | 295 |  |  |  | 61.92 | 277.49 | 0 | 302 |  |  |  | 61.922 | 277.28 | 0 | 308 |  |  |  | 61.921 | 526.96 | 0.152 | 80 | 0
578.56 | 277.325 | 0 | 298 |  |  |  | 61.921 | 277.369 | 0 | 303 |  |  |  | 61.92 | 277.279 | 0 | 310 |  |  |  | 61.92 | 531.2 | 0.159 | 85 | 0
579.06 | 277.325 | 0 | 298 |  |  |  | 61.921 | 277.369 | 0 | 303 |  |  |  | 61.92 | 277.279 | 0 | 310 |  |  |  | 61.92 | 531.2 | 0.159 | 85 | 0
579.56 | 277.4 | 0 | 298 |  |  |  | 61.92 | 277.455 | 0 | 303 |  |  |  | 61.919 | 277.222 | 0 | 311 |  |  |  | 61.919 | 533.49 | 0.155 | 83 | 0
580.06 | 277.4 | 0 | 298 |  |  |  | 61.92 | 277.455 | 0 | 303 |  |  |  | 61.919 | 277.222 | 0 | 311 |  |  |  | 61.919 | 533.49 | 0.155 | 83 | 0
580.56 | 277.298 | 0 | 300 |  |  |  | 61.92 | 277.418 | 0 | 303 |  |  |  | 61.921 | 277.185 | 0 | 309 |  |  |  | 61.921 | 533.36 | 0.154 | 82 | 0
581.06 | 277.298 | 0 | 300 |  |  |  | 61.92 | 277.418 | 0 | 303 |  |  |  | 61.921 | 277.185 | 0 | 309 |  |  |  | 61.921 | 533.36 | 0.154 | 82 | 0
581.56 | 277.351 | 0 | 298 |  |  |  | 61.92 | 277.315 | 0 | 303 |  |  |  | 61.919 | 277.264 | 0 | 307 |  |  |  | 61.921 | 533.38 | 0.155 | 83 | 0
582.06 | 277.351 | 0 | 298 |  |  |  | 61.92 | 277.315 | 0 | 303 |  |  |  | 61.919 | 277.264 | 0 | 307 |  |  |  | 61.921 | 533.38 | 0.155 | 83 | 0
582.56 | 277.311 | 0 | 297 |  |  |  | 61.92 | 277.457 | 0 | 305 |  |  |  | 61.919 | 277.267 | 0 | 308 |  |  |  | 61.92 | 537.19 | 0.158 | 85 | 0
583.06 | 277.311 | 0 | 297 |  |  |  | 61.92 | 277.457 | 0 | 305 |  |  |  | 61.919 | 277.267 | 0 | 308 |  |  |  | 61.92 | 537.19 | 0.158 | 85 | 0
583.56 | 277.359 | 0 | 295 |  |  |  | 61.921 | 277.348 | 0 | 297 |  |  |  | 61.92 | 277.242 | 0 | 307 |  |  |  | 61.92 | 539.83 | 0.155 | 84 | 0
584.06 | 277.359 | 0 | 295 |  |  |  | 61.921 | 277.348 | 0 | 297 |  |  |  | 61.92 | 277.242 | 0 | 307 |  |  |  | 61.92 | 539.83 | 0.155 | 84 | 0
584.56 | 277.288 | 0 | 301 |  |  |  | 61.92 | 277.524 | 0 | 307 |  |  |  | 61.923 | 277.183 | 0 | 313 |  |  |  | 61.921 | 535.69 | 0.154 | 82 | 0
585.06 | 277.288 | 0 | 301 |  |  |  | 61.92 | 277.524 | 0 | 307 |  |  |  | 61.923 | 277.183 | 0 | 313 |  |  |  | 61.921 | 535.69 | 0.154 | 82 | 0
585.56 | 277.379 | 0 | 294 |  |  |  | 61.92 | 277.411 | 0 | 303 |  |  |  | 61.921 | 277.274 | 0 | 311 |  |  |  | 61.921 | 533.28 | 0.155 | 83 | 0
586.06 | 277.379 | 0 | 294 |  |  |  | 61.92 | 277.411 | 0 | 303 |  |  |  | 61.921 | 277.274 | 0 | 311 |  |  |  | 61.921 | 533.28 | 0.155 | 83 | 0
586.56 | 277.422 | 0 | 295 |  |  |  | 61.92 | 277.296 | 0 | 305 |  |  |  | 61.919 | 277.269 | 0 | 312 |  |  |  | 61.92 | 533.37 | 0.151 | 81 | 0
587.06 | 277.422 | 0 | 295 |  |  |  | 61.92 | 277.296 | 0 | 305 |  |  |  | 61.919 | 277.269 | 0 | 312 |  |  |  | 61.92 | 533.37 | 0.151 | 81 | 0
587.56 | 277.314 | 0 | 294 |  |  |  | 61.921 | 277.461 | 0 | 301 |  |  |  | 61.92 | 277.262 | 0 | 312 |  |  |  | 61.919 | 533.45 | 0.155 | 83 | 0
588.06 | 277.314 | 0 | 294 |  |  |  | 61.921 | 277.461 | 0 | 301 |  |  |  | 61.92 | 277.262 | 0 | 312 |  |  |  | 61.919 | 533.45 | 0.155 | 83 | 0
588.56 | 277.394 | 0 | 297 |  |  |  | 61.919 | 277.353 | 0 | 302 |  |  |  | 61.92 | 277.22 | 0 | 308 |  |  |  | 61.921 | 529.49 | 0.157 | 83 | 0
589.06 | 277.394 | 0 | 297 |  |  |  | 61.919 | 277.353 | 0 | 302 |  |  |  | 61.92 | 277.22 | 0 | 308 |  |  |  | 61.921 | 529.49 | 0.157 | 83 | 0
589.56 | 277.299 | 0 | 295 |  |  |  | 61.921 | 277.539 | 0 | 301 |  |  |  | 61.922 | 277.296 | 0 | 307 |  |  |  | 61.921 | 526.93 | 0.151 | 79 | 0
590.06 | 277.299 | 0 | 295 |  |  |  | 61.921 | 277.539 | 0 | 301 |  |  |  | 61.922 | 277.296 | 0 | 307 |  |  |  | 61.921 | 526.93 | 0.151 | 79 | 0
590.56 | 277.347 | 0 | 294 |  |  |  | 61.921 | 277.393 | 0 | 299 |  |  |  | 61.92 | 277.266 | 0 | 311 |  |  |  | 61.921 | 531.12 | 0.155 | 82 | 0
591.06 | 277.347 | 0 | 294 |  |  |  | 61.921 | 277.393 | 0 | 299 |  |  |  | 61.92 | 277.266 | 0 | 311 |  |  |  | 61.921 | 531.12 | 0.155 | 82 | 0
591.56 | 277.31 | 0 | 303 |  |  |  | 61.92 | 277.351 | 0 | 300 |  |  |  | 61.92 | 277.252 | 0 | 309 |  |  |  | 61.92 | 533.39 | 0.154 | 82 | 0
592.06 | 277.31 | 0 | 303 |  |  |  | 61.92 | 277.351 | 0 | 300 |  |  |  | 61.92 | 277.252 | 0 | 309 |  |  |  | 61.92 | 533.39 | 0.154 | 82 | 0
592.56 | 277.363 | 0 | 296 |  |  |  | 61.92 | 277.449 | 0 | 300 |  |  |  | 61.92 | 277.227 | 0 | 309 |  |  |  | 61.921 | 533.34 | 0.155 | 83 | 0
593.06 | 277.363 | 0 | 296 |  |  |  | 61.92 | 277.449 | 0 | 300 |  |  |  | 61.92 | 277.227 | 0 | 309 |  |  |  | 61.921 | 533.34 | 0.155 | 83 | 0
593.56 | 277.279 | 0 | 299 |  |  |  | 61.921 | 277.302 | 0 | 304 |  |  |  | 61.918 | 277.183 | 0 | 312 |  |  |  | 61.92 | 533.45 | 0.157 | 84 | 0
594.06 | 277.279 | 0 | 299 |  |  |  | 61.921 | 277.302 | 0 | 304 |  |  |  | 61.918 | 277.183 | 0 | 312 |  |  |  | 61.92 | 533.45 | 0.157 | 84 | 0
594.56 | 277.372 | 0 | 294 |  |  |  | 61.921 | 277.463 | 0 | 302 |  |  |  | 61.919 | 277.288 | 0 | 311 |  |  |  | 61.921 | 537.24 | 0.154 | 83 | 0
595.06 | 277.372 | 0 | 294 |  |  |  | 61.921 | 277.463 | 0 | 302 |  |  |  | 61.919 | 277.288 | 0 | 311 |  |  |  | 61.921 | 537.24 | 0.154 | 83 | 0
595.56 | 277.423 | 0 | 290 |  |  |  | 61.919 | 277.338 | 0 | 295 |  |  |  | 61.92 | 277.262 | 0 | 305 |  |  |  | 61.92 | 539.83 | 0.155 | 84 | 0
596.06 | 277.423 | 0 | 290 |  |  |  | 61.919 | 277.338 | 0 | 295 |  |  |  | 61.92 | 277.262 | 0 | 305 |  |  |  | 61.92 | 539.83 | 0.155 | 84 | 0
596.56 | 277.312 | 0 | 301 |  |  |  | 61.921 | 277.488 | 0 | 310 |  |  |  | 61.922 | 277.255 | 0 | 312 |  |  |  | 61.92 | 535.75 | 0.155 | 83 | 0
597.06 | 277.312 | 0 | 301 |  |  |  | 61.921 | 277.488 | 0 | 310 |  |  |  | 61.922 | 277.255 | 0 | 312 |  |  |  | 61.92 | 535.75 | 0.155 | 83 | 0
597.56 | 277.382 | 0 | 299 |  |  |  | 61.92 | 277.375 | 0 | 307 |  |  |  | 61.92 | 277.208 | 0 | 314 |  |  |  | 61.92 | 533.52 | 0.153 | 81 | 0
598.06 | 277.382 | 0 | 299 |  |  |  | 61.92 | 277.375 | 0 | 307 |  |  |  | 61.92 | 277.208 | 0 | 314 |  |  |  | 61.92 | 533.52 | 0.153 | 81 | 0
598.56 | 277.325 | 0 | 297 |  |  |  | 61.921 | 277.265 | 0 | 304 |  |  |  | 61.919 | 277.298 | 0 | 307 |  |  |  | 61.92 | 533.39 | 0.156 | 83 | 0
599.09 | 277.325 | 0 | 297 |  |  |  | 61.921 | 277.265 | 0 | 304 |  |  |  | 61.919 | 277.298 | 0 | 307 |  |  |  | 61.92 | 533.39 | 0.156 | 83 | 0
599.59 | 277.358 | 0 | 296 |  |  |  | 61.921 | 277.449 | 0 | 300 |  |  |  | 61.92 | 277.258 | 0 | 308 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
600.07 | 277.358 | 0 | 296 |  |  |  | 61.921 | 277.449 | 0 | 300 |  |  |  | 61.92 | 277.258 | 0 | 308 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
600.57 | 277.303 | 0 | 295 |  |  |  | 61.92 | 277.289 | 0 | 304 |  |  |  | 61.92 | 277.24 | 0 | 311 |  |  |  | 61.92 | 529.56 | 0.157 | 83 | 0
601.06 | 277.303 | 0 | 295 |  |  |  | 61.92 | 277.289 | 0 | 304 |  |  |  | 61.92 | 277.24 | 0 | 311 |  |  |  | 61.92 | 529.56 | 0.157 | 83 | 0
601.56 | 277.378 | 0 | 294 |  |  |  | 61.921 | 277.492 | 0 | 304 |  |  |  | 61.921 | 277.223 | 0 | 309 |  |  |  | 61.919 | 526.93 | 0.152 | 80 | 0
602.1 | 277.261 | 0 | 296 |  |  |  | 61.92 | 277.378 | 0 | 302 |  |  |  | 61.921 | 277.316 | 0 | 309 |  |  |  | 61.919 | 531.08 | 0.159 | 84 | 0
602.6 | 277.261 | 0 | 296 |  |  |  | 61.92 | 277.378 | 0 | 302 |  |  |  | 61.921 | 277.316 | 0 | 309 |  |  |  | 61.919 | 531.08 | 0.159 | 84 | 0
603.08 | 277.348 | 0 | 301 |  |  |  | 61.921 | 277.281 | 0 | 299 |  |  |  | 61.919 | 277.28 | 0 | 314 |  |  |  | 61.92 | 533.42 | 0.153 | 81 | 0
603.58 | 277.348 | 0 | 301 |  |  |  | 61.921 | 277.281 | 0 | 299 |  |  |  | 61.919 | 277.28 | 0 | 314 |  |  |  | 61.92 | 533.42 | 0.153 | 81 | 0
604.07 | 277.423 | 0 | 298 |  |  |  | 61.919 | 277.436 | 0 | 301 |  |  |  | 61.919 | 277.247 | 0 | 315 |  |  |  | 61.92 | 533.45 | 0.154 | 82 | 0
604.57 | 277.423 | 0 | 298 |  |  |  | 61.919 | 277.436 | 0 | 301 |  |  |  | 61.919 | 277.247 | 0 | 315 |  |  |  | 61.92 | 533.45 | 0.154 | 82 | 0
605.06 | 277.307 | 0 | 296 |  |  |  | 61.92 | 277.288 | 0 | 305 |  |  |  | 61.92 | 277.242 | 0 | 310 |  |  |  | 61.92 | 533.33 | 0.157 | 83 | 0
605.56 | 277.307 | 0 | 296 |  |  |  | 61.92 | 277.288 | 0 | 305 |  |  |  | 61.92 | 277.242 | 0 | 310 |  |  |  | 61.92 | 533.33 | 0.157 | 83 | 0
606.06 | 277.371 | 0 | 299 |  |  |  | 61.919 | 277.431 | 0 | 299 |  |  |  | 61.921 | 277.272 | 0 | 310 |  |  |  | 61.921 | 537.22 | 0.157 | 84 | 0
606.56 | 277.371 | 0 | 299 |  |  |  | 61.919 | 277.431 | 0 | 299 |  |  |  | 61.921 | 277.272 | 0 | 310 |  |  |  | 61.921 | 537.22 | 0.157 | 84 | 0
607.06 | 277.325 | 0 | 292 |  |  |  | 61.921 | 277.319 | 0 | 299 |  |  |  | 61.919 | 277.301 | 0 | 303 |  |  |  | 61.921 | 539.86 | 0.153 | 83 | 0
607.56 | 277.325 | 0 | 292 |  |  |  | 61.921 | 277.319 | 0 | 299 |  |  |  | 61.919 | 277.301 | 0 | 303 |  |  |  | 61.921 | 539.86 | 0.153 | 83 | 0
608.06 | 277.367 | 0 | 300 |  |  |  | 61.921 | 277.428 | 0 | 304 |  |  |  | 61.92 | 277.251 | 0 | 315 |  |  |  | 61.921 | 535.85 | 0.156 | 84 | 0
608.56 | 277.367 | 0 | 300 |  |  |  | 61.921 | 277.428 | 0 | 304 |  |  |  | 61.92 | 277.251 | 0 | 315 |  |  |  | 61.921 | 535.85 | 0.156 | 84 | 0
609.06 | 277.31 | 0 | 299 |  |  |  | 61.921 | 277.384 | 0 | 308 |  |  |  | 61.92 | 277.215 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.156 | 83 | 0
609.56 | 277.31 | 0 | 299 |  |  |  | 61.921 | 277.384 | 0 | 308 |  |  |  | 61.92 | 277.215 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.156 | 83 | 0
610.06 | 277.382 | 0 | 299 |  |  |  | 61.921 | 277.247 | 0 | 303 |  |  |  | 61.92 | 277.204 | 0 | 312 |  |  |  | 61.921 | 533.49 | 0.157 | 84 | 0
610.56 | 277.382 | 0 | 299 |  |  |  | 61.921 | 277.247 | 0 | 303 |  |  |  | 61.92 | 277.204 | 0 | 312 |  |  |  | 61.921 | 533.49 | 0.157 | 84 | 0
611.06 | 277.286 | 0 | 297 |  |  |  | 61.921 | 277.469 | 0 | 302 |  |  |  | 61.921 | 277.303 | 0 | 309 |  |  |  | 61.919 | 533.4 | 0.153 | 81 | 0
611.56 | 277.286 | 0 | 297 |  |  |  | 61.921 | 277.469 | 0 | 302 |  |  |  | 61.921 | 277.303 | 0 | 309 |  |  |  | 61.919 | 533.4 | 0.153 | 81 | 0
612.06 | 277.339 | 0 | 292 |  |  |  | 61.921 | 277.348 | 0 | 306 |  |  |  | 61.921 | 277.287 | 0 | 308 |  |  |  | 61.921 | 529.71 | 0.157 | 83 | 0
612.56 | 277.339 | 0 | 292 |  |  |  | 61.921 | 277.348 | 0 | 306 |  |  |  | 61.921 | 277.287 | 0 | 308 |  |  |  | 61.921 | 529.71 | 0.157 | 83 | 0
613.06 | 277.408 | 0 | 297 |  |  |  | 61.92 | 277.497 | 0 | 302 |  |  |  | 61.924 | 277.233 | 0 | 307 |  |  |  | 61.919 | 527 | 0.157 | 83 | 0
613.56 | 277.408 | 0 | 297 |  |  |  | 61.92 | 277.497 | 0 | 302 |  |  |  | 61.924 | 277.233 | 0 | 307 |  |  |  | 61.919 | 527 | 0.157 | 83 | 0
614.06 | 277.318 | 0 | 295 |  |  |  | 61.92 | 277.388 | 0 | 299 |  |  |  | 61.919 | 277.199 | 0 | 307 |  |  |  | 61.92 | 531.01 | 0.152 | 81 | 0
614.56 | 277.318 | 0 | 295 |  |  |  | 61.92 | 277.388 | 0 | 299 |  |  |  | 61.919 | 277.199 | 0 | 307 |  |  |  | 61.92 | 531.01 | 0.152 | 81 | 0
615.06 | 277.348 | 0 | 299 |  |  |  | 61.919 | 277.299 | 0 | 302 |  |  |  | 61.921 | 277.287 | 0 | 313 |  |  |  | 61.92 | 533.41 | 0.157 | 84 | 0
615.56 | 277.348 | 0 | 299 |  |  |  | 61.919 | 277.299 | 0 | 302 |  |  |  | 61.921 | 277.287 | 0 | 313 |  |  |  | 61.92 | 533.41 | 0.157 | 84 | 0
616.06 | 277.338 | 0 | 293 |  |  |  | 61.921 | 277.415 | 0 | 302 |  |  |  | 61.92 | 277.285 | 0 | 311 |  |  |  | 61.92 | 533.46 | 0.156 | 83 | 0
616.56 | 277.338 | 0 | 293 |  |  |  | 61.921 | 277.415 | 0 | 302 |  |  |  | 61.92 | 277.285 | 0 | 311 |  |  |  | 61.92 | 533.46 | 0.156 | 83 | 0
617.06 | 277.365 | 0 | 296 |  |  |  | 61.92 | 277.336 | 0 | 301 |  |  |  | 61.919 | 277.243 | 0 | 310 |  |  |  | 61.92 | 533.51 | 0.155 | 83 | 0
617.56 | 277.365 | 0 | 296 |  |  |  | 61.92 | 277.336 | 0 | 301 |  |  |  | 61.919 | 277.243 | 0 | 310 |  |  |  | 61.92 | 533.51 | 0.155 | 83 | 0
618.06 | 277.309 | 0 | 297 |  |  |  | 61.92 | 277.465 | 0 | 305 |  |  |  | 61.923 | 277.197 | 0 | 310 |  |  |  | 61.921 | 536.98 | 0.147 | 79 | 0
618.56 | 277.309 | 0 | 297 |  |  |  | 61.92 | 277.465 | 0 | 305 |  |  |  | 61.923 | 277.197 | 0 | 310 |  |  |  | 61.921 | 536.98 | 0.147 | 79 | 0
619.06 | 277.4 | 0 | 292 |  |  |  | 61.92 | 277.356 | 0 | 294 |  |  |  | 61.92 | 277.278 | 0 | 303 |  |  |  | 61.922 | 539.79 | 0.156 | 84 | 0
619.56 | 277.4 | 0 | 292 |  |  |  | 61.92 | 277.356 | 0 | 294 |  |  |  | 61.92 | 277.278 | 0 | 303 |  |  |  | 61.922 | 539.79 | 0.156 | 84 | 0
620.06 | 277.279 | 0 | 302 |  |  |  | 61.921 | 277.356 | 0 | 303 |  |  |  | 61.921 | 277.286 | 0 | 315 |  |  |  | 61.92 | 535.98 | 0.157 | 84 | 0
620.56 | 277.279 | 0 | 302 |  |  |  | 61.921 | 277.356 | 0 | 303 |  |  |  | 61.921 | 277.286 | 0 | 315 |  |  |  | 61.92 | 535.98 | 0.157 | 84 | 0
621.06 | 277.348 | 0 | 299 |  |  |  | 61.92 | 277.454 | 0 | 301 |  |  |  | 61.919 | 277.275 | 0 | 313 |  |  |  | 61.92 | 533.43 | 0.153 | 81 | 0
621.56 | 277.348 | 0 | 299 |  |  |  | 61.92 | 277.454 | 0 | 301 |  |  |  | 61.919 | 277.275 | 0 | 313 |  |  |  | 61.92 | 533.43 | 0.153 | 81 | 0
622.06 | 277.388 | 0 | 296 |  |  |  | 61.92 | 277.293 | 0 | 299 |  |  |  | 61.919 | 277.23 | 0 | 310 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 0
622.56 | 277.388 | 0 | 296 |  |  |  | 61.92 | 277.293 | 0 | 299 |  |  |  | 61.919 | 277.23 | 0 | 310 |  |  |  | 61.92 | 533.4 | 0.153 | 82 | 0
623.06 | 277.315 | 0 | 297 |  |  |  | 61.921 | 277.503 | 0 | 307 |  |  |  | 61.919 | 277.197 | 0 | 312 |  |  |  | 61.919 | 533.41 | 0.152 | 81 | 0
623.88 | 277.375 | 0 | 297 |  |  |  | 61.921 | 277.384 | 0 | 300 |  |  |  | 61.92 | 277.283 | 0 | 312 |  |  |  | 61.921 | 529.81 | 0.156 | 83 | 0
624.07 | 277.375 | 0 | 297 |  |  |  | 61.921 | 277.384 | 0 | 300 |  |  |  | 61.92 | 277.283 | 0 | 312 |  |  |  | 61.921 | 529.81 | 0.156 | 83 | 0
624.56 | 277.375 | 0 | 297 |  |  |  | 61.921 | 277.384 | 0 | 300 |  |  |  | 61.92 | 277.283 | 0 | 312 |  |  |  | 61.921 | 529.81 | 0.156 | 83 | 0
625.06 | 277.561 | 0 | 296 |  |  |  | 58.581 | 277.684 | 0 | 300 |  |  |  | 58.583 | 277.455 | 0 | 311 |  |  |  | 58.58 | 526.95 | 0.153 | 81 | 0
625.56 | 277.561 | 0 | 296 |  |  |  | 58.581 | 277.684 | 0 | 300 |  |  |  | 58.583 | 277.455 | 0 | 311 |  |  |  | 58.58 | 526.95 | 0.153 | 81 | 0
626.06 | 278.626 | 0 | 296 |  |  |  | 58.58 | 278.691 | 0 | 302 |  |  |  | 58.579 | 278.415 | 0 | 310 |  |  |  | 58.58 | 530.27 | 0.156 | 83 | 0
626.56 | 278.626 | 0 | 296 |  |  |  | 58.58 | 278.691 | 0 | 302 |  |  |  | 58.579 | 278.415 | 0 | 310 |  |  |  | 58.58 | 530.27 | 0.156 | 83 | 0
627.06 | 277.985 | 0 | 297 |  |  |  | 58.58 | 277.992 | 0 | 303 |  |  |  | 58.58 | 277.897 | 0 | 310 |  |  |  | 58.58 | 533.38 | 0.154 | 82 | 0
627.56 | 277.985 | 0 | 297 |  |  |  | 58.58 | 277.992 | 0 | 303 |  |  |  | 58.58 | 277.897 | 0 | 310 |  |  |  | 58.58 | 533.38 | 0.154 | 82 | 0
628.06 | 277.78 | 0 | 295 |  |  |  | 58.581 | 277.873 | 0 | 299 |  |  |  | 58.581 | 277.719 | 0 | 311 |  |  |  | 58.581 | 533.42 | 0.154 | 82 | 0
628.56 | 277.78 | 0 | 295 |  |  |  | 58.581 | 277.873 | 0 | 299 |  |  |  | 58.581 | 277.719 | 0 | 311 |  |  |  | 58.581 | 533.42 | 0.154 | 82 | 0
629.06 | 277.486 | 0 | 296 |  |  |  | 58.58 | 277.522 | 0 | 303 |  |  |  | 58.58 | 277.511 | 0 | 312 |  |  |  | 58.58 | 533.37 | 0.153 | 82 | 0
629.56 | 277.486 | 0 | 296 |  |  |  | 58.58 | 277.522 | 0 | 303 |  |  |  | 58.58 | 277.511 | 0 | 312 |  |  |  | 58.58 | 533.37 | 0.153 | 82 | 0
630.06 | 277.515 | 0 | 298 |  |  |  | 58.58 | 277.644 | 0 | 302 |  |  |  | 58.583 | 277.413 | 0 | 305 |  |  |  | 58.58 | 534.84 | 0.16 | 86 | 0
630.59 | 277.515 | 0 | 298 |  |  |  | 58.58 | 277.644 | 0 | 302 |  |  |  | 58.583 | 277.413 | 0 | 305 |  |  |  | 58.58 | 534.84 | 0.16 | 86 | 0
631.09 | 277.488 | 0 | 290 |  |  |  | 58.581 | 277.434 | 0 | 295 |  |  |  | 58.58 | 277.363 | 0 | 306 |  |  |  | 58.581 | 539.88 | 0.156 | 84 | 0
631.57 | 277.488 | 0 | 290 |  |  |  | 58.581 | 277.434 | 0 | 295 |  |  |  | 58.58 | 277.363 | 0 | 306 |  |  |  | 58.581 | 539.88 | 0.156 | 84 | 0
632.07 | 277.445 | 0 | 294 |  |  |  | 58.58 | 277.368 | 0 | 301 |  |  |  | 58.58 | 277.439 | 0 | 311 |  |  |  | 58.583 | 539.16 | 0.153 | 82 | 0
632.56 | 277.445 | 0 | 294 |  |  |  | 58.58 | 277.368 | 0 | 301 |  |  |  | 58.58 | 277.439 | 0 | 311 |  |  |  | 58.583 | 539.16 | 0.153 | 82 | 0
633.06 | 277.476 | 0 | 298 |  |  |  | 58.58 | 277.493 | 0 | 302 |  |  |  | 58.58 | 277.384 | 0 | 313 |  |  |  | 58.58 | 533.47 | 0.158 | 84 | 0
633.56 | 277.476 | 0 | 298 |  |  |  | 58.58 | 277.493 | 0 | 302 |  |  |  | 58.58 | 277.384 | 0 | 313 |  |  |  | 58.58 | 533.47 | 0.158 | 84 | 0
634.08 | 277.439 | 0 | 298 |  |  |  | 58.58 | 277.331 | 0 | 303 |  |  |  | 58.58 | 277.36 | 0 | 309 |  |  |  | 58.58 | 533.52 | 0.152 | 81 | 0
634.58 | 275.782 | 0 | 302 |  |  |  | 61.921 | 275.842 | 0 | 301 |  |  |  | 61.92 | 275.72 | 0 | 312 |  |  |  | 61.921 | 533.57 | 0.157 | 84 | 0
635.08 | 275.782 | 0 | 302 |  |  |  | 61.921 | 275.842 | 0 | 301 |  |  |  | 61.92 | 275.72 | 0 | 312 |  |  |  | 61.921 | 533.57 | 0.157 | 84 | 0
635.57 | 276.426 | 0 | 300 |  |  |  | 61.921 | 276.292 | 0 | 306 |  |  |  | 61.921 | 276.308 | 0 | 308 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
636.07 | 276.426 | 0 | 300 |  |  |  | 61.921 | 276.292 | 0 | 306 |  |  |  | 61.921 | 276.308 | 0 | 308 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
636.56 | 276.925 | 0 | 294 |  |  |  | 61.92 | 276.941 | 0 | 303 |  |  |  | 61.922 | 276.806 | 0 | 307 |  |  |  | 61.92 | 526.94 | 0.155 | 82 | 0
637.06 | 276.925 | 0 | 294 |  |  |  | 61.92 | 276.941 | 0 | 303 |  |  |  | 61.922 | 276.806 | 0 | 307 |  |  |  | 61.92 | 526.94 | 0.155 | 82 | 0
637.56 | 277.075 | 0 | 297 |  |  |  | 61.921 | 277.046 | 0 | 299 |  |  |  | 61.92 | 276.985 | 0 | 305 |  |  |  | 61.92 | 527.05 | 0.155 | 82 | 0
638.06 | 277.075 | 0 | 297 |  |  |  | 61.921 | 277.046 | 0 | 299 |  |  |  | 61.92 | 276.985 | 0 | 305 |  |  |  | 61.92 | 527.05 | 0.155 | 82 | 0
638.56 | 277.26 | 0 | 298 |  |  |  | 61.92 | 277.105 | 0 | 300 |  |  |  | 61.92 | 277.104 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.152 | 81 | 0
639.06 | 277.26 | 0 | 298 |  |  |  | 61.92 | 277.105 | 0 | 300 |  |  |  | 61.92 | 277.104 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.152 | 81 | 0
639.56 | 277.349 | 0 | 299 |  |  |  | 61.921 | 277.328 | 0 | 302 |  |  |  | 61.921 | 277.143 | 0 | 312 |  |  |  | 61.921 | 533.33 | 0.152 | 81 | 0
640.06 | 277.349 | 0 | 299 |  |  |  | 61.921 | 277.328 | 0 | 302 |  |  |  | 61.921 | 277.143 | 0 | 312 |  |  |  | 61.921 | 533.33 | 0.152 | 81 | 0
640.56 | 277.341 | 0 | 299 |  |  |  | 61.919 | 277.259 | 0 | 301 |  |  |  | 61.919 | 277.277 | 0 | 307 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 0
641.06 | 277.341 | 0 | 299 |  |  |  | 61.919 | 277.259 | 0 | 301 |  |  |  | 61.919 | 277.277 | 0 | 307 |  |  |  | 61.92 | 533.39 | 0.15 | 80 | 0
641.56 | 277.385 | 0 | 298 |  |  |  | 61.921 | 277.479 | 0 | 298 |  |  |  | 61.922 | 277.238 | 0 | 314 |  |  |  | 61.92 | 533.3 | 0.154 | 82 | 0
642.06 | 277.385 | 0 | 298 |  |  |  | 61.921 | 277.479 | 0 | 298 |  |  |  | 61.922 | 277.238 | 0 | 314 |  |  |  | 61.92 | 533.3 | 0.154 | 82 | 0
642.56 | 277.332 | 0 | 289 |  |  |  | 61.921 | 277.332 | 0 | 295 |  |  |  | 61.92 | 277.22 | 0 | 303 |  |  |  | 61.921 | 539.77 | 0.152 | 82 | 0
643.06 | 277.332 | 0 | 289 |  |  |  | 61.921 | 277.332 | 0 | 295 |  |  |  | 61.92 | 277.22 | 0 | 303 |  |  |  | 61.921 | 539.77 | 0.152 | 82 | 0
643.56 | 277.405 | 0 | 291 |  |  |  | 61.921 | 277.311 | 0 | 298 |  |  |  | 61.919 | 277.209 | 0 | 301 |  |  |  | 61.92 | 539.9 | 0.157 | 85 | 0
644.06 | 277.405 | 0 | 291 |  |  |  | 61.921 | 277.311 | 0 | 298 |  |  |  | 61.919 | 277.209 | 0 | 301 |  |  |  | 61.92 | 539.9 | 0.157 | 85 | 0
644.56 | 277.299 | 0 | 298 |  |  |  | 61.92 | 277.388 | 0 | 304 |  |  |  | 61.919 | 277.301 | 0 | 311 |  |  |  | 61.92 | 533.34 | 0.152 | 81 | 0
645.06 | 277.299 | 0 | 298 |  |  |  | 61.92 | 277.388 | 0 | 304 |  |  |  | 61.919 | 277.301 | 0 | 311 |  |  |  | 61.92 | 533.34 | 0.152 | 81 | 0
645.56 | 277.376 | 0 | 295 |  |  |  | 61.921 | 277.276 | 0 | 304 |  |  |  | 61.919 | 277.276 | 0 | 314 |  |  |  | 61.92 | 533.46 | 0.154 | 82 | 0
646.06 | 277.376 | 0 | 295 |  |  |  | 61.921 | 277.276 | 0 | 304 |  |  |  | 61.919 | 277.276 | 0 | 314 |  |  |  | 61.92 | 533.46 | 0.154 | 82 | 0
646.56 | 277.305 | 0 | 298 |  |  |  | 61.921 | 277.407 | 0 | 301 |  |  |  | 61.92 | 277.241 | 0 | 313 |  |  |  | 61.92 | 533.5 | 0.154 | 82 | 0
647.06 | 277.305 | 0 | 298 |  |  |  | 61.921 | 277.407 | 0 | 301 |  |  |  | 61.92 | 277.241 | 0 | 313 |  |  |  | 61.92 | 533.5 | 0.154 | 82 | 0
647.56 | 277.365 | 0 | 296 |  |  |  | 61.921 | 277.289 | 0 | 308 |  |  |  | 61.919 | 277.231 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.156 | 83 | 0
648.06 | 277.365 | 0 | 296 |  |  |  | 61.921 | 277.289 | 0 | 308 |  |  |  | 61.919 | 277.231 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.156 | 83 | 0
648.56 | 277.384 | 0 | 295 |  |  |  | 61.92 | 277.454 | 0 | 299 |  |  |  | 61.923 | 277.196 | 0 | 308 |  |  |  | 61.921 | 526.94 | 0.155 | 82 | 0
649.06 | 277.384 | 0 | 295 |  |  |  | 61.92 | 277.454 | 0 | 299 |  |  |  | 61.923 | 277.196 | 0 | 308 |  |  |  | 61.921 | 526.94 | 0.155 | 82 | 0
649.56 | 277.356 | 0 | 299 |  |  |  | 61.921 | 277.351 | 0 | 299 |  |  |  | 61.92 | 277.294 | 0 | 308 |  |  |  | 61.92 | 526.9 | 0.157 | 83 | 0
650.06 | 277.356 | 0 | 299 |  |  |  | 61.921 | 277.351 | 0 | 299 |  |  |  | 61.92 | 277.294 | 0 | 308 |  |  |  | 61.92 | 526.9 | 0.157 | 83 | 0
650.56 | 277.399 | 0 | 300 |  |  |  | 61.921 | 277.241 | 0 | 305 |  |  |  | 61.92 | 277.246 | 0 | 312 |  |  |  | 61.92 | 533.45 | 0.155 | 83 | 0
651.06 | 277.399 | 0 | 300 |  |  |  | 61.921 | 277.241 | 0 | 305 |  |  |  | 61.92 | 277.246 | 0 | 312 |  |  |  | 61.92 | 533.45 | 0.155 | 83 | 0
651.56 | 277.331 | 0 | 298 |  |  |  | 61.92 | 277.403 | 0 | 302 |  |  |  | 61.92 | 277.216 | 0 | 308 |  |  |  | 61.92 | 533.43 | 0.159 | 85 | 0
652.06 | 277.331 | 0 | 298 |  |  |  | 61.92 | 277.403 | 0 | 302 |  |  |  | 61.92 | 277.216 | 0 | 308 |  |  |  | 61.92 | 533.43 | 0.159 | 85 | 0
652.56 | 277.406 | 0 | 303 |  |  |  | 61.921 | 277.265 | 0 | 305 |  |  |  | 61.919 | 277.206 | 0 | 312 |  |  |  | 61.92 | 533.51 | 0.159 | 85 | 0
653.06 | 277.406 | 0 | 303 |  |  |  | 61.921 | 277.265 | 0 | 305 |  |  |  | 61.919 | 277.206 | 0 | 312 |  |  |  | 61.92 | 533.51 | 0.159 | 85 | 0
653.56 | 277.307 | 0 | 298 |  |  |  | 61.921 | 277.468 | 0 | 302 |  |  |  | 61.923 | 277.288 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.156 | 83 | 0
654.06 | 277.307 | 0 | 298 |  |  |  | 61.921 | 277.468 | 0 | 302 |  |  |  | 61.923 | 277.288 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.156 | 83 | 0
654.56 | 277.367 | 0 | 289 |  |  |  | 61.92 | 277.356 | 0 | 295 |  |  |  | 61.919 | 277.26 | 0 | 303 |  |  |  | 61.92 | 539.86 | 0.153 | 83 | 0
655.06 | 277.367 | 0 | 289 |  |  |  | 61.92 | 277.356 | 0 | 295 |  |  |  | 61.919 | 277.26 | 0 | 303 |  |  |  | 61.92 | 539.86 | 0.153 | 83 | 0
655.56 | 277.314 | 0 | 290 |  |  |  | 61.921 | 277.344 | 0 | 295 |  |  |  | 61.921 | 277.223 | 0 | 307 |  |  |  | 61.921 | 539.87 | 0.158 | 85 | 0
656.06 | 277.314 | 0 | 290 |  |  |  | 61.921 | 277.344 | 0 | 295 |  |  |  | 61.921 | 277.223 | 0 | 307 |  |  |  | 61.921 | 539.87 | 0.158 | 85 | 0
656.56 | 277.357 | 0 | 298 |  |  |  | 61.921 | 277.41 | 0 | 299 |  |  |  | 61.92 | 277.205 | 0 | 309 |  |  |  | 61.92 | 533.25 | 0.158 | 84 | 0
657.06 | 277.357 | 0 | 298 |  |  |  | 61.921 | 277.41 | 0 | 299 |  |  |  | 61.92 | 277.205 | 0 | 309 |  |  |  | 61.92 | 533.25 | 0.158 | 84 | 0
657.56 | 277.394 | 0 | 297 |  |  |  | 61.92 | 277.28 | 0 | 304 |  |  |  | 61.919 | 277.293 | 0 | 312 |  |  |  | 61.921 | 533.42 | 0.155 | 83 | 0
658.06 | 277.394 | 0 | 297 |  |  |  | 61.92 | 277.28 | 0 | 304 |  |  |  | 61.919 | 277.293 | 0 | 312 |  |  |  | 61.921 | 533.42 | 0.155 | 83 | 0
658.56 | 277.364 | 0 | 297 |  |  |  | 61.92 | 277.483 | 0 | 301 |  |  |  | 61.92 | 277.273 | 0 | 311 |  |  |  | 61.92 | 533.46 | 0.158 | 84 | 0
659.06 | 277.364 | 0 | 297 |  |  |  | 61.92 | 277.483 | 0 | 301 |  |  |  | 61.92 | 277.273 | 0 | 311 |  |  |  | 61.92 | 533.46 | 0.158 | 84 | 0
659.56 | 277.402 | 0 | 299 |  |  |  | 61.921 | 277.317 | 0 | 303 |  |  |  | 61.919 | 277.224 | 0 | 313 |  |  |  | 61.92 | 533.4 | 0.156 | 83 | 0
660.06 | 277.402 | 0 | 299 |  |  |  | 61.921 | 277.317 | 0 | 303 |  |  |  | 61.919 | 277.224 | 0 | 313 |  |  |  | 61.92 | 533.4 | 0.156 | 83 | 0
660.56 | 277.339 | 0 | 294 |  |  |  | 61.921 | 277.471 | 0 | 297 |  |  |  | 61.923 | 277.187 | 0 | 309 |  |  |  | 61.921 | 526.88 | 0.156 | 82 | 0
661.06 | 277.339 | 0 | 294 |  |  |  | 61.921 | 277.471 | 0 | 297 |  |  |  | 61.923 | 277.187 | 0 | 309 |  |  |  | 61.921 | 526.88 | 0.156 | 82 | 0
661.56 | 277.403 | 0 | 297 |  |  |  | 61.92 | 277.376 | 0 | 301 |  |  |  | 61.919 | 277.176 | 0 | 310 |  |  |  | 61.919 | 526.94 | 0.16 | 84 | 0
662.09 | 277.403 | 0 | 297 |  |  |  | 61.92 | 277.376 | 0 | 301 |  |  |  | 61.919 | 277.176 | 0 | 310 |  |  |  | 61.919 | 526.94 | 0.16 | 84 | 0
662.59 | 277.309 | 0 | 301 |  |  |  | 61.92 | 277.267 | 0 | 302 |  |  |  | 61.921 | 277.279 | 0 | 311 |  |  |  | 61.919 | 533.4 | 0.157 | 84 | 0
663.07 | 277.309 | 0 | 301 |  |  |  | 61.92 | 277.267 | 0 | 302 |  |  |  | 61.921 | 277.279 | 0 | 311 |  |  |  | 61.919 | 533.4 | 0.157 | 84 | 0
663.57 | 277.363 | 0 | 295 |  |  |  | 61.921 | 277.442 | 0 | 302 |  |  |  | 61.92 | 277.256 | 0 | 313 |  |  |  | 61.92 | 533.42 | 0.156 | 83 | 0
664.06 | 277.363 | 0 | 295 |  |  |  | 61.921 | 277.442 | 0 | 302 |  |  |  | 61.92 | 277.256 | 0 | 313 |  |  |  | 61.92 | 533.42 | 0.156 | 83 | 0
664.56 | 277.322 | 0 | 305 |  |  |  | 61.92 | 277.318 | 0 | 303 |  |  |  | 61.92 | 277.201 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.159 | 85 | 0
665.1 | 277.366 | 0 | 295 |  |  |  | 61.919 | 277.504 | 0 | 301 |  |  |  | 61.922 | 277.185 | 0 | 315 |  |  |  | 61.92 | 533.44 | 0.156 | 83 | 0
665.6 | 277.366 | 0 | 295 |  |  |  | 61.919 | 277.504 | 0 | 301 |  |  |  | 61.922 | 277.185 | 0 | 315 |  |  |  | 61.92 | 533.44 | 0.156 | 83 | 0
666.09 | 277.364 | 0 | 294 |  |  |  | 61.92 | 277.34 | 0 | 299 |  |  |  | 61.92 | 277.266 | 0 | 305 |  |  |  | 61.92 | 539.77 | 0.156 | 84 | 0
666.59 | 277.364 | 0 | 294 |  |  |  | 61.92 | 277.34 | 0 | 299 |  |  |  | 61.92 | 277.266 | 0 | 305 |  |  |  | 61.92 | 539.77 | 0.156 | 84 | 0
667.08 | 277.356 | 0 | 290 |  |  |  | 61.921 | 277.431 | 0 | 295 |  |  |  | 61.919 | 277.263 | 0 | 300 |  |  |  | 61.921 | 539.84 | 0.156 | 84 | 0
667.58 | 277.356 | 0 | 290 |  |  |  | 61.921 | 277.431 | 0 | 295 |  |  |  | 61.919 | 277.263 | 0 | 300 |  |  |  | 61.921 | 539.84 | 0.156 | 84 | 0
668.06 | 277.402 | 0 | 297 |  |  |  | 61.919 | 277.449 | 0 | 304 |  |  |  | 61.919 | 277.226 | 0 | 309 |  |  |  | 61.919 | 533.41 | 0.154 | 82 | 0
668.56 | 277.402 | 0 | 297 |  |  |  | 61.919 | 277.449 | 0 | 304 |  |  |  | 61.919 | 277.226 | 0 | 309 |  |  |  | 61.919 | 533.41 | 0.154 | 82 | 0
669.06 | 277.328 | 0 | 297 |  |  |  | 61.921 | 277.331 | 0 | 304 |  |  |  | 61.92 | 277.182 | 0 | 311 |  |  |  | 61.921 | 533.34 | 0.149 | 80 | 0
669.56 | 277.328 | 0 | 297 |  |  |  | 61.921 | 277.331 | 0 | 304 |  |  |  | 61.92 | 277.182 | 0 | 311 |  |  |  | 61.921 | 533.34 | 0.149 | 80 | 0
670.06 | 277.408 | 0 | 299 |  |  |  | 61.921 | 277.488 | 0 | 304 |  |  |  | 61.92 | 277.264 | 0 | 311 |  |  |  | 61.921 | 533.46 | 0.154 | 82 | 0
670.56 | 277.408 | 0 | 299 |  |  |  | 61.921 | 277.488 | 0 | 304 |  |  |  | 61.92 | 277.264 | 0 | 311 |  |  |  | 61.921 | 533.46 | 0.154 | 82 | 0
671.06 | 277.329 | 0 | 301 |  |  |  | 61.921 | 277.372 | 0 | 302 |  |  |  | 61.92 | 277.261 | 0 | 312 |  |  |  | 61.92 | 533.37 | 0.154 | 82 | 0
671.56 | 277.329 | 0 | 301 |  |  |  | 61.921 | 277.372 | 0 | 302 |  |  |  | 61.92 | 277.261 | 0 | 312 |  |  |  | 61.92 | 533.37 | 0.154 | 82 | 0
672.06 | 277.372 | 0 | 295 |  |  |  | 61.921 | 277.492 | 0 | 301 |  |  |  | 61.922 | 277.24 | 0 | 309 |  |  |  | 61.921 | 526.97 | 0.155 | 82 | 0
672.56 | 277.372 | 0 | 295 |  |  |  | 61.921 | 277.492 | 0 | 301 |  |  |  | 61.922 | 277.24 | 0 | 309 |  |  |  | 61.921 | 526.97 | 0.155 | 82 | 0
673.06 | 277.328 | 0 | 293 |  |  |  | 61.919 | 277.38 | 0 | 299 |  |  |  | 61.919 | 277.193 | 0 | 308 |  |  |  | 61.92 | 526.95 | 0.157 | 83 | 0
673.56 | 277.328 | 0 | 293 |  |  |  | 61.919 | 277.38 | 0 | 299 |  |  |  | 61.919 | 277.193 | 0 | 308 |  |  |  | 61.92 | 526.95 | 0.157 | 83 | 0
674.06 | 277.37 | 0 | 295 |  |  |  | 61.921 | 277.293 | 0 | 305 |  |  |  | 61.918 | 277.27 | 0 | 311 |  |  |  | 61.922 | 533.31 | 0.152 | 81 | 0
674.56 | 277.37 | 0 | 295 |  |  |  | 61.921 | 277.293 | 0 | 305 |  |  |  | 61.918 | 277.27 | 0 | 311 |  |  |  | 61.922 | 533.31 | 0.152 | 81 | 0
675.06 | 277.373 | 0 | 299 |  |  |  | 61.92 | 277.421 | 0 | 308 |  |  |  | 61.92 | 277.263 | 0 | 306 |  |  |  | 61.92 | 533.48 | 0.161 | 86 | 0
675.56 | 277.373 | 0 | 299 |  |  |  | 61.92 | 277.421 | 0 | 308 |  |  |  | 61.92 | 277.263 | 0 | 306 |  |  |  | 61.92 | 533.48 | 0.161 | 86 | 0
676.06 | 277.362 | 0 | 299 |  |  |  | 61.921 | 277.291 | 0 | 299 |  |  |  | 61.92 | 277.25 | 0 | 312 |  |  |  | 61.92 | 533.42 | 0.153 | 81 | 0
676.56 | 277.362 | 0 | 299 |  |  |  | 61.921 | 277.291 | 0 | 299 |  |  |  | 61.92 | 277.25 | 0 | 312 |  |  |  | 61.92 | 533.42 | 0.153 | 81 | 0
677.06 | 277.418 | 0 | 300 |  |  |  | 61.92 | 277.486 | 0 | 300 |  |  |  | 61.923 | 277.217 | 0 | 310 |  |  |  | 61.92 | 533.43 | 0.157 | 84 | 0
677.56 | 277.418 | 0 | 300 |  |  |  | 61.92 | 277.486 | 0 | 300 |  |  |  | 61.923 | 277.217 | 0 | 310 |  |  |  | 61.92 | 533.43 | 0.157 | 84 | 0
678.06 | 277.355 | 0 | 292 |  |  |  | 61.92 | 277.363 | 0 | 296 |  |  |  | 61.919 | 277.162 | 0 | 307 |  |  |  | 61.921 | 539.76 | 0.154 | 83 | 0
678.56 | 277.355 | 0 | 292 |  |  |  | 61.92 | 277.363 | 0 | 296 |  |  |  | 61.919 | 277.162 | 0 | 307 |  |  |  | 61.921 | 539.76 | 0.154 | 83 | 0
679.06 | 277.426 | 0 | 292 |  |  |  | 61.921 | 277.439 | 0 | 301 |  |  |  | 61.92 | 277.263 | 0 | 306 |  |  |  | 61.92 | 539.84 | 0.152 | 82 | 0
679.56 | 277.426 | 0 | 292 |  |  |  | 61.921 | 277.439 | 0 | 301 |  |  |  | 61.92 | 277.263 | 0 | 306 |  |  |  | 61.92 | 539.84 | 0.152 | 82 | 0
680.06 | 277.355 | 0 | 299 |  |  |  | 61.92 | 277.397 | 0 | 302 |  |  |  | 61.92 | 277.259 | 0 | 310 |  |  |  | 61.92 | 533.27 | 0.154 | 82 | 0
680.56 | 277.355 | 0 | 299 |  |  |  | 61.92 | 277.397 | 0 | 302 |  |  |  | 61.92 | 277.259 | 0 | 310 |  |  |  | 61.92 | 533.27 | 0.154 | 82 | 0
681.06 | 277.399 | 0 | 297 |  |  |  | 61.921 | 277.25 | 0 | 306 |  |  |  | 61.919 | 277.241 | 0 | 308 |  |  |  | 61.921 | 533.38 | 0.157 | 84 | 0
681.56 | 277.399 | 0 | 297 |  |  |  | 61.921 | 277.25 | 0 | 306 |  |  |  | 61.919 | 277.241 | 0 | 308 |  |  |  | 61.921 | 533.38 | 0.157 | 84 | 0
682.06 | 277.341 | 0 | 297 |  |  |  | 61.92 | 277.421 | 0 | 304 |  |  |  | 61.92 | 277.183 | 0 | 309 |  |  |  | 61.92 | 533.42 | 0.157 | 84 | 0
682.56 | 277.341 | 0 | 297 |  |  |  | 61.92 | 277.421 | 0 | 304 |  |  |  | 61.92 | 277.183 | 0 | 309 |  |  |  | 61.92 | 533.42 | 0.157 | 84 | 0
683.06 | 277.408 | 0 | 296 |  |  |  | 61.921 | 277.327 | 0 | 300 |  |  |  | 61.919 | 277.285 | 0 | 312 |  |  |  | 61.921 | 533.44 | 0.153 | 82 | 0
683.56 | 277.408 | 0 | 296 |  |  |  | 61.921 | 277.327 | 0 | 300 |  |  |  | 61.919 | 277.285 | 0 | 312 |  |  |  | 61.921 | 533.44 | 0.153 | 82 | 0
684.06 | 277.379 | 0 | 299 |  |  |  | 61.921 | 277.478 | 0 | 299 |  |  |  | 61.922 | 277.245 | 0 | 310 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 0
684.56 | 277.379 | 0 | 299 |  |  |  | 61.921 | 277.478 | 0 | 299 |  |  |  | 61.922 | 277.245 | 0 | 310 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 0
685.06 | 277.385 | 0 | 297 |  |  |  | 61.92 | 277.305 | 0 | 301 |  |  |  | 61.919 | 277.247 | 0 | 304 |  |  |  | 61.919 | 526.95 | 0.155 | 82 | 0
685.56 | 277.385 | 0 | 297 |  |  |  | 61.92 | 277.305 | 0 | 301 |  |  |  | 61.919 | 277.247 | 0 | 304 |  |  |  | 61.919 | 526.95 | 0.155 | 82 | 0
686.06 | 277.446 | 0 | 298 |  |  |  | 61.92 | 277.211 | 0 | 305 |  |  |  | 61.92 | 277.219 | 0 | 311 |  |  |  | 61.921 | 533.27 | 0.151 | 80 | 0
686.56 | 277.446 | 0 | 298 |  |  |  | 61.92 | 277.211 | 0 | 305 |  |  |  | 61.92 | 277.219 | 0 | 311 |  |  |  | 61.921 | 533.27 | 0.151 | 80 | 0
687.06 | 277.361 | 0 | 297 |  |  |  | 61.92 | 277.438 | 0 | 306 |  |  |  | 61.921 | 277.301 | 0 | 312 |  |  |  | 61.921 | 533.45 | 0.156 | 83 | 0
687.56 | 277.361 | 0 | 297 |  |  |  | 61.92 | 277.438 | 0 | 306 |  |  |  | 61.921 | 277.301 | 0 | 312 |  |  |  | 61.921 | 533.45 | 0.156 | 83 | 0
688.06 | 277.432 | 0 | 300 |  |  |  | 61.92 | 277.264 | 0 | 304 |  |  |  | 61.919 | 277.257 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.154 | 82 | 0
688.56 | 277.432 | 0 | 300 |  |  |  | 61.92 | 277.264 | 0 | 304 |  |  |  | 61.919 | 277.257 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.154 | 82 | 0
689.06 | 277.351 | 0 | 300 |  |  |  | 61.92 | 277.461 | 0 | 303 |  |  |  | 61.919 | 277.235 | 0 | 305 |  |  |  | 61.921 | 533.23 | 0.149 | 79 | 0
689.56 | 277.351 | 0 | 300 |  |  |  | 61.92 | 277.461 | 0 | 303 |  |  |  | 61.919 | 277.235 | 0 | 305 |  |  |  | 61.921 | 533.23 | 0.149 | 79 | 0
690.06 | 277.406 | 0 | 288 |  |  |  | 61.92 | 277.333 | 0 | 295 |  |  |  | 61.921 | 277.227 | 0 | 307 |  |  |  | 61.921 | 539.72 | 0.15 | 81 | 0
690.56 | 277.406 | 0 | 288 |  |  |  | 61.92 | 277.333 | 0 | 295 |  |  |  | 61.921 | 277.227 | 0 | 307 |  |  |  | 61.921 | 539.72 | 0.15 | 81 | 0
691.06 | 277.345 | 0 | 291 |  |  |  | 61.92 | 277.47 | 0 | 297 |  |  |  | 61.923 | 277.187 | 0 | 301 |  |  |  | 61.92 | 539.78 | 0.154 | 83 | 0
691.56 | 277.345 | 0 | 291 |  |  |  | 61.92 | 277.47 | 0 | 297 |  |  |  | 61.923 | 277.187 | 0 | 301 |  |  |  | 61.92 | 539.78 | 0.154 | 83 | 0
692.06 | 277.405 | 0 | 297 |  |  |  | 61.92 | 277.391 | 0 | 301 |  |  |  | 61.919 | 277.316 | 0 | 308 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 0
692.56 | 277.405 | 0 | 297 |  |  |  | 61.92 | 277.391 | 0 | 301 |  |  |  | 61.919 | 277.316 | 0 | 308 |  |  |  | 61.92 | 533.42 | 0.154 | 82 | 0
693.06 | 277.312 | 0 | 298 |  |  |  | 61.918 | 277.273 | 0 | 305 |  |  |  | 61.919 | 277.276 | 0 | 314 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 0
693.56 | 277.312 | 0 | 298 |  |  |  | 61.918 | 277.273 | 0 | 305 |  |  |  | 61.919 | 277.276 | 0 | 314 |  |  |  | 61.92 | 533.43 | 0.149 | 80 | 0
694.06 | 277.376 | 0 | 299 |  |  |  | 61.92 | 277.383 | 0 | 304 |  |  |  | 61.921 | 277.25 | 0 | 308 |  |  |  | 61.921 | 533.32 | 0.153 | 82 | 0
694.59 | 277.376 | 0 | 299 |  |  |  | 61.92 | 277.383 | 0 | 304 |  |  |  | 61.921 | 277.25 | 0 | 308 |  |  |  | 61.921 | 533.32 | 0.153 | 82 | 0
695.09 | 277.447 | 0 | 304 |  |  |  | 61.921 | 277.264 | 0 | 303 |  |  |  | 61.919 | 277.235 | 0 | 309 |  |  |  | 61.92 | 533.38 | 0.153 | 82 | 0
695.57 | 277.447 | 0 | 304 |  |  |  | 61.921 | 277.264 | 0 | 303 |  |  |  | 61.919 | 277.235 | 0 | 309 |  |  |  | 61.92 | 533.38 | 0.153 | 82 | 0
696.07 | 277.337 | 0 | 293 |  |  |  | 61.921 | 277.501 | 0 | 302 |  |  |  | 61.922 | 277.328 | 0 | 310 |  |  |  | 61.92 | 526.86 | 0.151 | 80 | 0
696.56 | 277.337 | 0 | 293 |  |  |  | 61.921 | 277.501 | 0 | 302 |  |  |  | 61.922 | 277.328 | 0 | 310 |  |  |  | 61.92 | 526.86 | 0.151 | 80 | 0
697.06 | 277.393 | 0 | 297 |  |  |  | 61.92 | 277.336 | 0 | 301 |  |  |  | 61.919 | 277.284 | 0 | 311 |  |  |  | 61.921 | 526.96 | 0.154 | 81 | 0
697.56 | 277.393 | 0 | 297 |  |  |  | 61.92 | 277.336 | 0 | 301 |  |  |  | 61.919 | 277.284 | 0 | 311 |  |  |  | 61.921 | 526.96 | 0.154 | 81 | 0
698.06 | 277.342 | 0 | 301 |  |  |  | 61.92 | 277.356 | 0 | 305 |  |  |  | 61.92 | 277.25 | 0 | 311 |  |  |  | 61.921 | 533.45 | 0.154 | 82 | 0
698.6 | 277.342 | 0 | 301 |  |  |  | 61.92 | 277.356 | 0 | 305 |  |  |  | 61.92 | 277.25 | 0 | 311 |  |  |  | 61.921 | 533.45 | 0.154 | 82 | 0
699.1 | 277.392 | 0 | 301 |  |  |  | 61.921 | 277.425 | 0 | 299 |  |  |  | 61.92 | 277.231 | 0 | 309 |  |  |  | 61.921 | 533.5 | 0.153 | 82 | 0
699.58 | 277.312 | 0 | 298 |  |  |  | 61.92 | 277.318 | 0 | 301 |  |  |  | 61.919 | 277.328 | 0 | 309 |  |  |  | 61.921 | 533.42 | 0.155 | 83 | 0
700.08 | 277.312 | 0 | 298 |  |  |  | 61.92 | 277.318 | 0 | 301 |  |  |  | 61.919 | 277.328 | 0 | 309 |  |  |  | 61.921 | 533.42 | 0.155 | 83 | 0
700.56 | 277.381 | 0 | 297 |  |  |  | 61.921 | 277.489 | 0 | 305 |  |  |  | 61.92 | 277.304 | 0 | 309 |  |  |  | 61.92 | 533.36 | 0.157 | 84 | 0
701.06 | 277.381 | 0 | 297 |  |  |  | 61.921 | 277.489 | 0 | 305 |  |  |  | 61.92 | 277.304 | 0 | 309 |  |  |  | 61.92 | 533.36 | 0.157 | 84 | 0
701.56 | 277.27 | 0 | 295 |  |  |  | 61.917 | 277.352 | 0 | 293 |  |  |  | 61.92 | 277.254 | 0 | 302 |  |  |  | 61.921 | 539.82 | 0.158 | 85 | 0
702.06 | 277.27 | 0 | 295 |  |  |  | 61.917 | 277.352 | 0 | 293 |  |  |  | 61.92 | 277.254 | 0 | 302 |  |  |  | 61.921 | 539.82 | 0.158 | 85 | 0
702.56 | 277.346 | 0 | 293 |  |  |  | 61.921 | 277.525 | 0 | 297 |  |  |  | 61.923 | 277.231 | 0 | 300 |  |  |  | 61.92 | 539.89 | 0.157 | 85 | 0
703.06 | 277.346 | 0 | 293 |  |  |  | 61.921 | 277.525 | 0 | 297 |  |  |  | 61.923 | 277.231 | 0 | 300 |  |  |  | 61.92 | 539.89 | 0.157 | 85 | 0
703.56 | 277.422 | 0 | 297 |  |  |  | 61.92 | 277.376 | 0 | 300 |  |  |  | 61.919 | 277.308 | 0 | 311 |  |  |  | 61.923 | 533.36 | 0.154 | 82 | 0
704.06 | 277.422 | 0 | 297 |  |  |  | 61.92 | 277.376 | 0 | 300 |  |  |  | 61.919 | 277.308 | 0 | 311 |  |  |  | 61.923 | 533.36 | 0.154 | 82 | 0
704.56 | 277.342 | 0 | 301 |  |  |  | 61.921 | 277.31 | 0 | 298 |  |  |  | 61.921 | 277.3 | 0 | 311 |  |  |  | 61.921 | 533.48 | 0.159 | 85 | 0
705.06 | 277.342 | 0 | 301 |  |  |  | 61.921 | 277.31 | 0 | 298 |  |  |  | 61.921 | 277.3 | 0 | 311 |  |  |  | 61.921 | 533.48 | 0.159 | 85 | 0
705.56 | 277.384 | 0 | 294 |  |  |  | 61.92 | 277.448 | 0 | 304 |  |  |  | 61.919 | 277.263 | 0 | 310 |  |  |  | 61.92 | 533.43 | 0.156 | 83 | 0
706.06 | 277.384 | 0 | 294 |  |  |  | 61.92 | 277.448 | 0 | 304 |  |  |  | 61.919 | 277.263 | 0 | 310 |  |  |  | 61.92 | 533.43 | 0.156 | 83 | 0
706.56 | 277.347 | 0 | 300 |  |  |  | 61.921 | 277.325 | 0 | 302 |  |  |  | 61.919 | 277.231 | 0 | 313 |  |  |  | 61.92 | 533.37 | 0.157 | 84 | 0
707.06 | 277.347 | 0 | 300 |  |  |  | 61.921 | 277.325 | 0 | 302 |  |  |  | 61.919 | 277.231 | 0 | 313 |  |  |  | 61.92 | 533.37 | 0.157 | 84 | 0
707.56 | 277.39 | 0 | 297 |  |  |  | 61.92 | 277.525 | 0 | 301 |  |  |  | 61.923 | 277.211 | 0 | 310 |  |  |  | 61.92 | 526.95 | 0.15 | 79 | 0
708.06 | 277.39 | 0 | 297 |  |  |  | 61.92 | 277.525 | 0 | 301 |  |  |  | 61.923 | 277.211 | 0 | 310 |  |  |  | 61.92 | 526.95 | 0.15 | 79 | 0
708.56 | 277.311 | 0 | 295 |  |  |  | 61.921 | 277.385 | 0 | 299 |  |  |  | 61.92 | 277.311 | 0 | 309 |  |  |  | 61.92 | 527.03 | 0.155 | 82 | 0
709.06 | 277.311 | 0 | 295 |  |  |  | 61.921 | 277.385 | 0 | 299 |  |  |  | 61.92 | 277.311 | 0 | 309 |  |  |  | 61.92 | 527.03 | 0.155 | 82 | 0
709.56 | 277.386 | 0 | 299 |  |  |  | 61.921 | 277.427 | 0 | 302 |  |  |  | 61.92 | 277.292 | 0 | 315 |  |  |  | 61.92 | 533.42 | 0.156 | 83 | 0
710.06 | 277.386 | 0 | 299 |  |  |  | 61.921 | 277.427 | 0 | 302 |  |  |  | 61.92 | 277.292 | 0 | 315 |  |  |  | 61.92 | 533.42 | 0.156 | 83 | 0
710.56 | 277.285 | 0 | 298 |  |  |  | 61.918 | 277.43 | 0 | 304 |  |  |  | 61.92 | 277.243 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 0
711.06 | 277.285 | 0 | 298 |  |  |  | 61.918 | 277.43 | 0 | 304 |  |  |  | 61.92 | 277.243 | 0 | 312 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 0
711.56 | 277.349 | 0 | 298 |  |  |  | 61.921 | 277.334 | 0 | 301 |  |  |  | 61.92 | 277.213 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
712.06 | 277.349 | 0 | 298 |  |  |  | 61.921 | 277.334 | 0 | 301 |  |  |  | 61.92 | 277.213 | 0 | 311 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
712.56 | 277.415 | 0 | 300 |  |  |  | 61.921 | 277.444 | 0 | 305 |  |  |  | 61.919 | 277.293 | 0 | 311 |  |  |  | 61.921 | 533.42 | 0.154 | 82 | 0
713.06 | 277.415 | 0 | 300 |  |  |  | 61.921 | 277.444 | 0 | 305 |  |  |  | 61.919 | 277.293 | 0 | 311 |  |  |  | 61.921 | 533.42 | 0.154 | 82 | 0
713.56 | 277.344 | 0 | 294 |  |  |  | 61.921 | 277.354 | 0 | 298 |  |  |  | 61.919 | 277.296 | 0 | 305 |  |  |  | 61.92 | 539.83 | 0.155 | 84 | 0
714.06 | 277.344 | 0 | 294 |  |  |  | 61.921 | 277.354 | 0 | 298 |  |  |  | 61.919 | 277.296 | 0 | 305 |  |  |  | 61.92 | 539.83 | 0.155 | 84 | 0
714.56 | 277.385 | 0 | 295 |  |  |  | 61.92 | 277.5 | 0 | 295 |  |  |  | 61.923 | 277.263 | 0 | 306 |  |  |  | 61.919 | 539.85 | 0.15 | 81 | 0
715.06 | 277.385 | 0 | 295 |  |  |  | 61.92 | 277.5 | 0 | 295 |  |  |  | 61.923 | 277.263 | 0 | 306 |  |  |  | 61.919 | 539.85 | 0.15 | 81 | 0
715.56 | 277.342 | 0 | 300 |  |  |  | 61.92 | 277.394 | 0 | 304 |  |  |  | 61.919 | 277.211 | 0 | 310 |  |  |  | 61.921 | 533.46 | 0.153 | 81 | 0
716.06 | 277.342 | 0 | 300 |  |  |  | 61.92 | 277.394 | 0 | 304 |  |  |  | 61.919 | 277.211 | 0 | 310 |  |  |  | 61.921 | 533.46 | 0.153 | 81 | 0
716.56 | 277.399 | 0 | 298 |  |  |  | 61.921 | 277.267 | 0 | 303 |  |  |  | 61.92 | 277.31 | 0 | 314 |  |  |  | 61.921 | 533.47 | 0.156 | 83 | 0
717.06 | 277.399 | 0 | 298 |  |  |  | 61.921 | 277.267 | 0 | 303 |  |  |  | 61.92 | 277.31 | 0 | 314 |  |  |  | 61.921 | 533.47 | 0.156 | 83 | 0
717.56 | 277.297 | 0 | 300 |  |  |  | 61.92 | 277.433 | 0 | 304 |  |  |  | 61.92 | 277.305 | 0 | 309 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
718.06 | 277.297 | 0 | 300 |  |  |  | 61.92 | 277.433 | 0 | 304 |  |  |  | 61.92 | 277.305 | 0 | 309 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
718.56 | 277.389 | 0 | 300 |  |  |  | 61.921 | 277.261 | 0 | 303 |  |  |  | 61.921 | 277.293 | 0 | 308 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 0
719.06 | 277.389 | 0 | 300 |  |  |  | 61.921 | 277.261 | 0 | 303 |  |  |  | 61.921 | 277.293 | 0 | 308 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 0
719.56 | 277.284 | 0 | 296 |  |  |  | 61.917 | 277.492 | 0 | 296 |  |  |  | 61.923 | 277.238 | 0 | 309 |  |  |  | 61.92 | 526.96 | 0.153 | 80 | 0
720.06 | 277.284 | 0 | 296 |  |  |  | 61.917 | 277.492 | 0 | 296 |  |  |  | 61.923 | 277.238 | 0 | 309 |  |  |  | 61.92 | 526.96 | 0.153 | 80 | 0
720.56 | 277.372 | 0 | 295 |  |  |  | 61.921 | 277.373 | 0 | 302 |  |  |  | 61.92 | 277.291 | 0 | 310 |  |  |  | 61.922 | 526.92 | 0.152 | 80 | 0
721.06 | 277.372 | 0 | 295 |  |  |  | 61.921 | 277.373 | 0 | 302 |  |  |  | 61.92 | 277.291 | 0 | 310 |  |  |  | 61.922 | 526.92 | 0.152 | 80 | 0
721.56 | 277.436 | 0 | 299 |  |  |  | 61.92 | 277.444 | 0 | 303 |  |  |  | 61.921 | 277.289 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.15 | 80 | 0
722.06 | 277.436 | 0 | 299 |  |  |  | 61.92 | 277.444 | 0 | 303 |  |  |  | 61.921 | 277.289 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.15 | 80 | 0
722.56 | 277.358 | 0 | 297 |  |  |  | 61.921 | 277.366 | 0 | 302 |  |  |  | 61.919 | 277.284 | 0 | 311 |  |  |  | 61.92 | 533.43 | 0.154 | 82 | 0
723.06 | 277.358 | 0 | 297 |  |  |  | 61.921 | 277.366 | 0 | 302 |  |  |  | 61.919 | 277.284 | 0 | 311 |  |  |  | 61.92 | 533.43 | 0.154 | 82 | 0
723.56 | 277.419 | 0 | 301 |  |  |  | 61.919 | 277.247 | 0 | 303 |  |  |  | 61.921 | 277.257 | 0 | 312 |  |  |  | 61.921 | 533.39 | 0.156 | 83 | 0
724.06 | 277.419 | 0 | 301 |  |  |  | 61.919 | 277.247 | 0 | 303 |  |  |  | 61.921 | 277.257 | 0 | 312 |  |  |  | 61.921 | 533.39 | 0.156 | 83 | 0
724.56 | 277.36 | 0 | 294 |  |  |  | 61.921 | 277.441 | 0 | 307 |  |  |  | 61.919 | 277.2 | 0 | 313 |  |  |  | 61.921 | 533.39 | 0.156 | 83 | 0
725.06 | 277.36 | 0 | 294 |  |  |  | 61.921 | 277.441 | 0 | 307 |  |  |  | 61.919 | 277.2 | 0 | 313 |  |  |  | 61.921 | 533.39 | 0.156 | 83 | 0
725.56 | 277.425 | 0 | 295 |  |  |  | 61.92 | 277.292 | 0 | 297 |  |  |  | 61.92 | 277.303 | 0 | 306 |  |  |  | 61.92 | 539.73 | 0.151 | 81 | 0
726.06 | 277.425 | 0 | 295 |  |  |  | 61.92 | 277.292 | 0 | 297 |  |  |  | 61.92 | 277.303 | 0 | 306 |  |  |  | 61.92 | 539.73 | 0.151 | 81 | 0
726.56 | 277.322 | 0 | 294 |  |  |  | 61.92 | 277.481 | 0 | 300 |  |  |  | 61.922 | 277.285 | 0 | 302 |  |  |  | 61.92 | 539.79 | 0.153 | 82 | 0
727.09 | 277.322 | 0 | 294 |  |  |  | 61.92 | 277.481 | 0 | 300 |  |  |  | 61.922 | 277.285 | 0 | 302 |  |  |  | 61.92 | 539.79 | 0.153 | 82 | 0
727.59 | 277.397 | 0 | 297 |  |  |  | 61.921 | 277.315 | 0 | 306 |  |  |  | 61.918 | 277.273 | 0 | 308 |  |  |  | 61.92 | 533.38 | 0.153 | 82 | 0
728.08 | 277.397 | 0 | 297 |  |  |  | 61.921 | 277.315 | 0 | 306 |  |  |  | 61.918 | 277.273 | 0 | 308 |  |  |  | 61.92 | 533.38 | 0.153 | 82 | 0
728.58 | 277.334 | 0 | 303 |  |  |  | 61.919 | 277.229 | 0 | 303 |  |  |  | 61.92 | 277.223 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.153 | 81 | 0
729.06 | 277.334 | 0 | 303 |  |  |  | 61.919 | 277.229 | 0 | 303 |  |  |  | 61.92 | 277.223 | 0 | 310 |  |  |  | 61.921 | 533.35 | 0.153 | 81 | 0
729.56 | 277.369 | 0 | 300 |  |  |  | 61.921 | 277.422 | 0 | 301 |  |  |  | 61.919 | 277.314 | 0 | 312 |  |  |  | 61.92 | 533.46 | 0.152 | 81 | 0
730.09 | 277.429 | 0 | 296 |  |  |  | 61.92 | 277.293 | 0 | 303 |  |  |  | 61.919 | 277.273 | 0 | 313 |  |  |  | 61.92 | 533.43 | 0.153 | 82 | 0
730.59 | 277.429 | 0 | 296 |  |  |  | 61.92 | 277.293 | 0 | 303 |  |  |  | 61.919 | 277.273 | 0 | 313 |  |  |  | 61.92 | 533.43 | 0.153 | 82 | 0
731.08 | 277.384 | 0 | 294 |  |  |  | 61.921 | 277.447 | 0 | 299 |  |  |  | 61.921 | 277.255 | 0 | 309 |  |  |  | 61.92 | 526.94 | 0.15 | 79 | 0
731.58 | 277.384 | 0 | 294 |  |  |  | 61.921 | 277.447 | 0 | 299 |  |  |  | 61.921 | 277.255 | 0 | 309 |  |  |  | 61.92 | 526.94 | 0.15 | 79 | 0
732.06 | 277.419 | 0 | 295 |  |  |  | 61.92 | 277.326 | 0 | 299 |  |  |  | 61.921 | 277.237 | 0 | 307 |  |  |  | 61.921 | 526.84 | 0.147 | 77 | 0
732.56 | 277.419 | 0 | 295 |  |  |  | 61.92 | 277.326 | 0 | 299 |  |  |  | 61.921 | 277.237 | 0 | 307 |  |  |  | 61.921 | 526.84 | 0.147 | 77 | 0
733.06 | 277.373 | 0 | 296 |  |  |  | 61.921 | 277.461 | 0 | 302 |  |  |  | 61.918 | 277.338 | 0 | 312 |  |  |  | 61.92 | 533.37 | 0.154 | 82 | 0
733.56 | 277.373 | 0 | 296 |  |  |  | 61.921 | 277.461 | 0 | 302 |  |  |  | 61.918 | 277.338 | 0 | 312 |  |  |  | 61.92 | 533.37 | 0.154 | 82 | 0
734.06 | 277.436 | 0 | 298 |  |  |  | 61.919 | 277.374 | 0 | 302 |  |  |  | 61.919 | 277.3 | 0 | 311 |  |  |  | 61.921 | 533.33 | 0.153 | 82 | 0
734.56 | 277.436 | 0 | 298 |  |  |  | 61.919 | 277.374 | 0 | 302 |  |  |  | 61.919 | 277.3 | 0 | 311 |  |  |  | 61.921 | 533.33 | 0.153 | 82 | 0
735.06 | 277.295 | 0 | 301 |  |  |  | 61.92 | 277.289 | 0 | 305 |  |  |  | 61.92 | 277.266 | 0 | 308 |  |  |  | 61.92 | 533.52 | 0.153 | 81 | 0
735.56 | 277.295 | 0 | 301 |  |  |  | 61.92 | 277.289 | 0 | 305 |  |  |  | 61.92 | 277.266 | 0 | 308 |  |  |  | 61.92 | 533.52 | 0.153 | 81 | 0
736.06 | 277.372 | 0 | 298 |  |  |  | 61.92 | 277.455 | 0 | 303 |  |  |  | 61.92 | 277.252 | 0 | 312 |  |  |  | 61.92 | 533.38 | 0.156 | 83 | 0
736.56 | 277.372 | 0 | 298 |  |  |  | 61.92 | 277.455 | 0 | 303 |  |  |  | 61.92 | 277.252 | 0 | 312 |  |  |  | 61.92 | 533.38 | 0.156 | 83 | 0
737.06 | 277.311 | 0 | 289 |  |  |  | 61.919 | 277.33 | 0 | 297 |  |  |  | 61.92 | 277.204 | 0 | 303 |  |  |  | 61.92 | 539.7 | 0.152 | 82 | 0
737.56 | 277.311 | 0 | 289 |  |  |  | 61.919 | 277.33 | 0 | 297 |  |  |  | 61.92 | 277.204 | 0 | 303 |  |  |  | 61.92 | 539.7 | 0.152 | 82 | 0
738.06 | 277.353 | 0 | 291 |  |  |  | 61.921 | 277.52 | 0 | 296 |  |  |  | 61.923 | 277.308 | 0 | 306 |  |  |  | 61.92 | 539.85 | 0.155 | 84 | 0
738.56 | 277.353 | 0 | 291 |  |  |  | 61.921 | 277.52 | 0 | 296 |  |  |  | 61.923 | 277.308 | 0 | 306 |  |  |  | 61.92 | 539.85 | 0.155 | 84 | 0
739.06 | 277.396 | 0 | 299 |  |  |  | 61.919 | 277.4 | 0 | 303 |  |  |  | 61.919 | 277.26 | 0 | 310 |  |  |  | 61.921 | 533.32 | 0.151 | 80 | 0
739.56 | 277.396 | 0 | 299 |  |  |  | 61.919 | 277.4 | 0 | 303 |  |  |  | 61.919 | 277.26 | 0 | 310 |  |  |  | 61.921 | 533.32 | 0.151 | 80 | 0
740.06 | 277.38 | 0 | 300 |  |  |  | 61.921 | 277.288 | 0 | 303 |  |  |  | 61.92 | 277.242 | 0 | 309 |  |  |  | 61.921 | 533.4 | 0.151 | 81 | 0
740.56 | 277.38 | 0 | 300 |  |  |  | 61.921 | 277.288 | 0 | 303 |  |  |  | 61.92 | 277.242 | 0 | 309 |  |  |  | 61.921 | 533.4 | 0.151 | 81 | 0
741.06 | 277.406 | 0 | 300 |  |  |  | 61.919 | 277.444 | 0 | 306 |  |  |  | 61.921 | 277.223 | 0 | 314 |  |  |  | 61.92 | 533.49 | 0.156 | 83 | 0
741.56 | 277.406 | 0 | 300 |  |  |  | 61.919 | 277.444 | 0 | 306 |  |  |  | 61.921 | 277.223 | 0 | 314 |  |  |  | 61.92 | 533.49 | 0.156 | 83 | 0
742.06 | 277.34 | 0 | 298 |  |  |  | 61.921 | 277.34 | 0 | 303 |  |  |  | 61.92 | 277.326 | 0 | 312 |  |  |  | 61.92 | 533.4 | 0.154 | 82 | 0
742.56 | 277.34 | 0 | 298 |  |  |  | 61.921 | 277.34 | 0 | 303 |  |  |  | 61.92 | 277.326 | 0 | 312 |  |  |  | 61.92 | 533.4 | 0.154 | 82 | 0
743.06 | 277.416 | 0 | 292 |  |  |  | 61.92 | 277.486 | 0 | 299 |  |  |  | 61.92 | 277.287 | 0 | 307 |  |  |  | 61.92 | 526.89 | 0.151 | 79 | 0
743.56 | 277.416 | 0 | 292 |  |  |  | 61.92 | 277.486 | 0 | 299 |  |  |  | 61.92 | 277.287 | 0 | 307 |  |  |  | 61.92 | 526.89 | 0.151 | 79 | 0
744.06 | 277.301 | 0 | 292 |  |  |  | 61.92 | 277.378 | 0 | 302 |  |  |  | 61.92 | 277.245 | 0 | 306 |  |  |  | 61.92 | 526.94 | 0.157 | 83 | 0
744.56 | 277.301 | 0 | 292 |  |  |  | 61.92 | 277.378 | 0 | 302 |  |  |  | 61.92 | 277.245 | 0 | 306 |  |  |  | 61.92 | 526.94 | 0.157 | 83 | 0
745.06 | 277.367 | 0 | 300 |  |  |  | 61.92 | 277.483 | 0 | 303 |  |  |  | 61.923 | 277.225 | 0 | 312 |  |  |  | 61.92 | 533.34 | 0.155 | 83 | 0
745.56 | 277.367 | 0 | 300 |  |  |  | 61.92 | 277.483 | 0 | 303 |  |  |  | 61.923 | 277.225 | 0 | 312 |  |  |  | 61.92 | 533.34 | 0.155 | 83 | 0
746.06 | 277.317 | 0 | 299 |  |  |  | 61.92 | 277.407 | 0 | 305 |  |  |  | 61.92 | 277.309 | 0 | 309 |  |  |  | 61.92 | 533.44 | 0.157 | 84 | 0
746.56 | 277.317 | 0 | 299 |  |  |  | 61.92 | 277.407 | 0 | 305 |  |  |  | 61.92 | 277.309 | 0 | 309 |  |  |  | 61.92 | 533.44 | 0.157 | 84 | 0
747.06 | 277.364 | 0 | 299 |  |  |  | 61.92 | 277.269 | 0 | 302 |  |  |  | 61.918 | 277.296 | 0 | 316 |  |  |  | 61.921 | 533.46 | 0.157 | 84 | 0
747.56 | 277.364 | 0 | 299 |  |  |  | 61.92 | 277.269 | 0 | 302 |  |  |  | 61.918 | 277.296 | 0 | 316 |  |  |  | 61.921 | 533.46 | 0.157 | 84 | 0
748.06 | 277.397 | 0 | 296 |  |  |  | 61.92 | 277.457 | 0 | 304 |  |  |  | 61.92 | 277.244 | 0 | 316 |  |  |  | 61.92 | 533.4 | 0.156 | 83 | 0
748.56 | 277.397 | 0 | 296 |  |  |  | 61.92 | 277.457 | 0 | 304 |  |  |  | 61.92 | 277.244 | 0 | 316 |  |  |  | 61.92 | 533.4 | 0.156 | 83 | 0
749.06 | 277.366 | 0 | 287 |  |  |  | 61.921 | 277.359 | 0 | 295 |  |  |  | 61.92 | 277.213 | 0 | 306 |  |  |  | 61.92 | 539.71 | 0.155 | 84 | 0
749.56 | 277.366 | 0 | 287 |  |  |  | 61.921 | 277.359 | 0 | 295 |  |  |  | 61.92 | 277.213 | 0 | 306 |  |  |  | 61.92 | 539.71 | 0.155 | 84 | 0
750.06 | 277.401 | 0 | 294 |  |  |  | 61.92 | 277.528 | 0 | 293 |  |  |  | 61.922 | 277.307 | 0 | 306 |  |  |  | 61.923 | 539.81 | 0.155 | 83 | 0
750.56 | 277.401 | 0 | 294 |  |  |  | 61.92 | 277.528 | 0 | 293 |  |  |  | 61.922 | 277.307 | 0 | 306 |  |  |  | 61.923 | 539.81 | 0.155 | 83 | 0
751.06 | 277.314 | 0 | 298 |  |  |  | 61.921 | 277.405 | 0 | 304 |  |  |  | 61.918 | 277.31 | 0 | 315 |  |  |  | 61.919 | 533.24 | 0.151 | 81 | 0
751.56 | 277.314 | 0 | 298 |  |  |  | 61.921 | 277.405 | 0 | 304 |  |  |  | 61.918 | 277.31 | 0 | 315 |  |  |  | 61.919 | 533.24 | 0.151 | 81 | 0
752.06 | 277.389 | 0 | 297 |  |  |  | 61.92 | 277.315 | 0 | 302 |  |  |  | 61.92 | 277.28 | 0 | 310 |  |  |  | 61.921 | 533.28 | 0.152 | 81 | 0
752.56 | 277.389 | 0 | 297 |  |  |  | 61.92 | 277.315 | 0 | 302 |  |  |  | 61.92 | 277.28 | 0 | 310 |  |  |  | 61.921 | 533.28 | 0.152 | 81 | 0
753.06 | 277.297 | 0 | 298 |  |  |  | 61.921 | 277.483 | 0 | 304 |  |  |  | 61.92 | 277.227 | 0 | 317 |  |  |  | 61.92 | 533.43 | 0.157 | 84 | 0
753.56 | 277.297 | 0 | 298 |  |  |  | 61.921 | 277.483 | 0 | 304 |  |  |  | 61.92 | 277.227 | 0 | 317 |  |  |  | 61.92 | 533.43 | 0.157 | 84 | 0
754.06 | 277.359 | 0 | 298 |  |  |  | 61.92 | 277.31 | 0 | 307 |  |  |  | 61.919 | 277.206 | 0 | 308 |  |  |  | 61.92 | 533.31 | 0.157 | 84 | 0
754.56 | 277.359 | 0 | 298 |  |  |  | 61.92 | 277.31 | 0 | 307 |  |  |  | 61.919 | 277.206 | 0 | 308 |  |  |  | 61.92 | 533.31 | 0.157 | 84 | 0
755.06 | 277.328 | 0 | 296 |  |  |  | 61.921 | 277.488 | 0 | 302 |  |  |  | 61.921 | 277.291 | 0 | 308 |  |  |  | 61.919 | 527.04 | 0.153 | 80 | 0
755.56 | 277.328 | 0 | 296 |  |  |  | 61.921 | 277.488 | 0 | 302 |  |  |  | 61.921 | 277.291 | 0 | 308 |  |  |  | 61.919 | 527.04 | 0.153 | 80 | 0
756.06 | 277.374 | 0 | 297 |  |  |  | 61.921 | 277.33 | 0 | 300 |  |  |  | 61.92 | 277.286 | 0 | 311 |  |  |  | 61.921 | 526.99 | 0.153 | 81 | 0
756.56 | 277.374 | 0 | 297 |  |  |  | 61.921 | 277.33 | 0 | 300 |  |  |  | 61.92 | 277.286 | 0 | 311 |  |  |  | 61.921 | 526.99 | 0.153 | 81 | 0
757.06 | 277.4 | 0 | 299 |  |  |  | 61.921 | 277.446 | 0 | 304 |  |  |  | 61.919 | 277.239 | 0 | 312 |  |  |  | 61.92 | 533.47 | 0.15 | 80 | 0
757.56 | 277.4 | 0 | 299 |  |  |  | 61.921 | 277.446 | 0 | 304 |  |  |  | 61.919 | 277.239 | 0 | 312 |  |  |  | 61.92 | 533.47 | 0.15 | 80 | 0
758.06 | 277.38 | 0 | 298 |  |  |  | 61.92 | 277.403 | 0 | 305 |  |  |  | 61.919 | 277.206 | 0 | 313 |  |  |  | 61.921 | 533.44 | 0.16 | 85 | 0
758.59 | 277.38 | 0 | 298 |  |  |  | 61.92 | 277.403 | 0 | 305 |  |  |  | 61.919 | 277.206 | 0 | 313 |  |  |  | 61.921 | 533.44 | 0.16 | 85 | 0
759.09 | 277.418 | 0 | 298 |  |  |  | 61.921 | 277.293 | 0 | 303 |  |  |  | 61.92 | 277.289 | 0 | 313 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 0
759.58 | 277.418 | 0 | 298 |  |  |  | 61.921 | 277.293 | 0 | 303 |  |  |  | 61.92 | 277.289 | 0 | 313 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 0
760.08 | 277.318 | 0 | 296 |  |  |  | 61.921 | 277.417 | 0 | 302 |  |  |  | 61.92 | 277.29 | 0 | 308 |  |  |  | 61.921 | 533.15 | 0.154 | 82 | 0
760.56 | 277.318 | 0 | 296 |  |  |  | 61.921 | 277.417 | 0 | 302 |  |  |  | 61.92 | 277.29 | 0 | 308 |  |  |  | 61.921 | 533.15 | 0.154 | 82 | 0
761.06 | 277.4 | 0 | 290 |  |  |  | 61.92 | 277.288 | 0 | 298 |  |  |  | 61.92 | 277.271 | 0 | 302 |  |  |  | 61.92 | 539.68 | 0.153 | 83 | 0
761.6 | 277.4 | 0 | 290 |  |  |  | 61.92 | 277.288 | 0 | 298 |  |  |  | 61.92 | 277.271 | 0 | 302 |  |  |  | 61.92 | 539.68 | 0.153 | 83 | 0
762.1 | 277.315 | 0 | 290 |  |  |  | 61.921 | 277.53 | 0 | 295 |  |  |  | 61.923 | 277.217 | 0 | 303 |  |  |  | 61.92 | 539.81 | 0.157 | 85 | 0
762.58 | 277.359 | 0 | 299 |  |  |  | 61.92 | 277.364 | 0 | 306 |  |  |  | 61.92 | 277.306 | 0 | 308 |  |  |  | 61.92 | 533.37 | 0.15 | 80 | 0
763.08 | 277.359 | 0 | 299 |  |  |  | 61.92 | 277.364 | 0 | 306 |  |  |  | 61.92 | 277.306 | 0 | 308 |  |  |  | 61.92 | 533.37 | 0.15 | 80 | 0
763.57 | 277.328 | 0 | 300 |  |  |  | 61.92 | 277.241 | 0 | 303 |  |  |  | 61.92 | 277.28 | 0 | 315 |  |  |  | 61.921 | 533.5 | 0.157 | 84 | 0
764.07 | 277.328 | 0 | 300 |  |  |  | 61.92 | 277.241 | 0 | 303 |  |  |  | 61.92 | 277.28 | 0 | 315 |  |  |  | 61.921 | 533.5 | 0.157 | 84 | 0
764.56 | 277.384 | 0 | 300 |  |  |  | 61.921 | 277.384 | 0 | 304 |  |  |  | 61.92 | 277.268 | 0 | 309 |  |  |  | 61.92 | 533.49 | 0.153 | 82 | 0
765.06 | 277.384 | 0 | 300 |  |  |  | 61.921 | 277.384 | 0 | 304 |  |  |  | 61.92 | 277.268 | 0 | 309 |  |  |  | 61.92 | 533.49 | 0.153 | 82 | 0
765.56 | 277.402 | 0 | 297 |  |  |  | 61.92 | 277.282 | 0 | 301 |  |  |  | 61.919 | 277.233 | 0 | 311 |  |  |  | 61.921 | 533.4 | 0.153 | 82 | 0
766.06 | 277.402 | 0 | 297 |  |  |  | 61.92 | 277.282 | 0 | 301 |  |  |  | 61.919 | 277.233 | 0 | 311 |  |  |  | 61.921 | 533.4 | 0.153 | 82 | 0
766.56 | 277.378 | 0 | 301 |  |  |  | 61.921 | 277.461 | 0 | 299 |  |  |  | 61.92 | 277.328 | 0 | 311 |  |  |  | 61.922 | 527.06 | 0.151 | 80 | 0
767.06 | 277.378 | 0 | 301 |  |  |  | 61.921 | 277.461 | 0 | 299 |  |  |  | 61.92 | 277.328 | 0 | 311 |  |  |  | 61.922 | 527.06 | 0.151 | 80 | 0
767.56 | 277.429 | 0 | 291 |  |  |  | 61.921 | 277.334 | 0 | 298 |  |  |  | 61.92 | 277.299 | 0 | 306 |  |  |  | 61.92 | 526.96 | 0.155 | 82 | 0
768.06 | 277.429 | 0 | 291 |  |  |  | 61.921 | 277.334 | 0 | 298 |  |  |  | 61.92 | 277.299 | 0 | 306 |  |  |  | 61.92 | 526.96 | 0.155 | 82 | 0
768.56 | 277.304 | 0 | 298 |  |  |  | 61.921 | 277.411 | 0 | 307 |  |  |  | 61.922 | 277.28 | 0 | 307 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 0
769.06 | 277.304 | 0 | 298 |  |  |  | 61.921 | 277.411 | 0 | 307 |  |  |  | 61.922 | 277.28 | 0 | 307 |  |  |  | 61.92 | 533.4 | 0.152 | 81 | 0
769.56 | 277.404 | 0 | 297 |  |  |  | 61.921 | 277.324 | 0 | 303 |  |  |  | 61.92 | 277.265 | 0 | 313 |  |  |  | 61.921 | 533.46 | 0.155 | 82 | 0
770.06 | 277.404 | 0 | 297 |  |  |  | 61.921 | 277.324 | 0 | 303 |  |  |  | 61.92 | 277.265 | 0 | 313 |  |  |  | 61.921 | 533.46 | 0.155 | 82 | 0
770.56 | 277.308 | 0 | 299 |  |  |  | 61.92 | 277.252 | 0 | 303 |  |  |  | 61.919 | 277.204 | 0 | 309 |  |  |  | 61.92 | 533.46 | 0.151 | 81 | 0
771.06 | 277.308 | 0 | 299 |  |  |  | 61.92 | 277.252 | 0 | 303 |  |  |  | 61.919 | 277.204 | 0 | 309 |  |  |  | 61.92 | 533.46 | 0.151 | 81 | 0
771.56 | 277.365 | 0 | 299 |  |  |  | 61.92 | 277.41 | 0 | 303 |  |  |  | 61.919 | 277.296 | 0 | 310 |  |  |  | 61.921 | 533.37 | 0.156 | 83 | 0
772.06 | 277.365 | 0 | 299 |  |  |  | 61.92 | 277.41 | 0 | 303 |  |  |  | 61.919 | 277.296 | 0 | 310 |  |  |  | 61.921 | 533.37 | 0.156 | 83 | 0
772.56 | 277.331 | 0 | 294 |  |  |  | 61.92 | 277.277 | 0 | 295 |  |  |  | 61.92 | 277.27 | 0 | 304 |  |  |  | 61.919 | 539.66 | 0.157 | 85 | 0
773.06 | 277.331 | 0 | 294 |  |  |  | 61.92 | 277.277 | 0 | 295 |  |  |  | 61.92 | 277.27 | 0 | 304 |  |  |  | 61.919 | 539.66 | 0.157 | 85 | 0
773.56 | 277.373 | 0 | 291 |  |  |  | 61.92 | 277.484 | 0 | 299 |  |  |  | 61.922 | 277.258 | 0 | 306 |  |  |  | 61.921 | 539.87 | 0.155 | 84 | 0
774.06 | 277.373 | 0 | 291 |  |  |  | 61.92 | 277.484 | 0 | 299 |  |  |  | 61.922 | 277.258 | 0 | 306 |  |  |  | 61.921 | 539.87 | 0.155 | 84 | 0
774.56 | 277.385 | 0 | 302 |  |  |  | 61.92 | 277.362 | 0 | 304 |  |  |  | 61.919 | 277.221 | 0 | 310 |  |  |  | 61.92 | 533.46 | 0.15 | 80 | 0
775.06 | 277.385 | 0 | 302 |  |  |  | 61.92 | 277.362 | 0 | 304 |  |  |  | 61.919 | 277.221 | 0 | 310 |  |  |  | 61.92 | 533.46 | 0.15 | 80 | 0
775.56 | 277.356 | 0 | 298 |  |  |  | 61.921 | 277.259 | 0 | 302 |  |  |  | 61.92 | 277.315 | 0 | 314 |  |  |  | 61.92 | 533.44 | 0.155 | 83 | 0
776.06 | 277.356 | 0 | 298 |  |  |  | 61.921 | 277.259 | 0 | 302 |  |  |  | 61.92 | 277.315 | 0 | 314 |  |  |  | 61.92 | 533.44 | 0.155 | 83 | 0
776.56 | 277.424 | 0 | 296 |  |  |  | 61.92 | 277.432 | 0 | 306 |  |  |  | 61.92 | 277.273 | 0 | 312 |  |  |  | 61.921 | 533.49 | 0.157 | 84 | 0
777.06 | 277.424 | 0 | 296 |  |  |  | 61.92 | 277.432 | 0 | 306 |  |  |  | 61.92 | 277.273 | 0 | 312 |  |  |  | 61.921 | 533.49 | 0.157 | 84 | 0
777.56 | 277.327 | 0 | 298 |  |  |  | 61.92 | 277.344 | 0 | 306 |  |  |  | 61.92 | 277.255 | 0 | 314 |  |  |  | 61.92 | 533.45 | 0.156 | 83 | 0
778.06 | 277.327 | 0 | 298 |  |  |  | 61.92 | 277.344 | 0 | 306 |  |  |  | 61.92 | 277.255 | 0 | 314 |  |  |  | 61.92 | 533.45 | 0.156 | 83 | 0
778.56 | 277.382 | 0 | 298 |  |  |  | 61.92 | 277.479 | 0 | 305 |  |  |  | 61.922 | 277.243 | 0 | 308 |  |  |  | 61.92 | 527.16 | 0.157 | 83 | 0
779.06 | 277.382 | 0 | 298 |  |  |  | 61.92 | 277.479 | 0 | 305 |  |  |  | 61.922 | 277.243 | 0 | 308 |  |  |  | 61.92 | 527.16 | 0.157 | 83 | 0
779.56 | 277.336 | 0 | 296 |  |  |  | 61.921 | 277.379 | 0 | 299 |  |  |  | 61.92 | 277.329 | 0 | 308 |  |  |  | 61.92 | 526.93 | 0.153 | 81 | 0
780.06 | 277.336 | 0 | 296 |  |  |  | 61.921 | 277.379 | 0 | 299 |  |  |  | 61.92 | 277.329 | 0 | 308 |  |  |  | 61.92 | 526.93 | 0.153 | 81 | 0
780.56 | 277.367 | 0 | 299 |  |  |  | 61.92 | 277.445 | 0 | 302 |  |  |  | 61.92 | 277.284 | 0 | 312 |  |  |  | 61.921 | 533.42 | 0.154 | 82 | 0
781.06 | 277.367 | 0 | 299 |  |  |  | 61.92 | 277.445 | 0 | 302 |  |  |  | 61.92 | 277.284 | 0 | 312 |  |  |  | 61.921 | 533.42 | 0.154 | 82 | 0
781.56 | 277.33 | 0 | 297 |  |  |  | 61.92 | 277.402 | 0 | 301 |  |  |  | 61.919 | 277.242 | 0 | 309 |  |  |  | 61.921 | 533.37 | 0.153 | 81 | 0
782.06 | 277.33 | 0 | 297 |  |  |  | 61.92 | 277.402 | 0 | 301 |  |  |  | 61.919 | 277.242 | 0 | 309 |  |  |  | 61.921 | 533.37 | 0.153 | 81 | 0
782.56 | 277.396 | 0 | 301 |  |  |  | 61.92 | 277.28 | 0 | 302 |  |  |  | 61.92 | 277.228 | 0 | 315 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 0
783.06 | 277.396 | 0 | 301 |  |  |  | 61.92 | 277.28 | 0 | 302 |  |  |  | 61.92 | 277.228 | 0 | 315 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 0
783.56 | 277.364 | 0 | 298 |  |  |  | 61.92 | 277.481 | 0 | 306 |  |  |  | 61.921 | 277.324 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 0
784.06 | 277.364 | 0 | 298 |  |  |  | 61.92 | 277.481 | 0 | 306 |  |  |  | 61.921 | 277.324 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.151 | 81 | 0
784.56 | 277.354 | 0 | 294 |  |  |  | 61.921 | 277.323 | 0 | 296 |  |  |  | 61.92 | 277.314 | 0 | 305 |  |  |  | 61.921 | 539.63 | 0.15 | 81 | 0
785.06 | 277.354 | 0 | 294 |  |  |  | 61.921 | 277.323 | 0 | 296 |  |  |  | 61.92 | 277.314 | 0 | 305 |  |  |  | 61.921 | 539.63 | 0.15 | 81 | 0
785.56 | 277.421 | 0 | 290 |  |  |  | 61.92 | 277.535 | 0 | 297 |  |  |  | 61.922 | 277.26 | 0 | 307 |  |  |  | 61.919 | 539.83 | 0.148 | 80 | 0
786.06 | 277.421 | 0 | 290 |  |  |  | 61.92 | 277.535 | 0 | 297 |  |  |  | 61.922 | 277.26 | 0 | 307 |  |  |  | 61.919 | 539.83 | 0.148 | 80 | 0
786.56 | 277.318 | 0 | 298 |  |  |  | 61.92 | 277.445 | 0 | 303 |  |  |  | 61.921 | 277.227 | 0 | 312 |  |  |  | 61.919 | 533.45 | 0.154 | 82 | 0
787.06 | 277.318 | 0 | 298 |  |  |  | 61.92 | 277.445 | 0 | 303 |  |  |  | 61.921 | 277.227 | 0 | 312 |  |  |  | 61.919 | 533.45 | 0.154 | 82 | 0
787.56 | 277.38 | 0 | 300 |  |  |  | 61.92 | 277.327 | 0 | 301 |  |  |  | 61.92 | 277.226 | 0 | 313 |  |  |  | 61.919 | 533.45 | 0.157 | 84 | 0
788.06 | 277.38 | 0 | 300 |  |  |  | 61.92 | 277.327 | 0 | 301 |  |  |  | 61.92 | 277.226 | 0 | 313 |  |  |  | 61.919 | 533.45 | 0.157 | 84 | 0
788.56 | 277.332 | 0 | 300 |  |  |  | 61.921 | 277.465 | 0 | 301 |  |  |  | 61.92 | 277.319 | 0 | 313 |  |  |  | 61.92 | 533.37 | 0.152 | 81 | 0
789.06 | 277.332 | 0 | 300 |  |  |  | 61.921 | 277.465 | 0 | 301 |  |  |  | 61.92 | 277.319 | 0 | 313 |  |  |  | 61.92 | 533.37 | 0.152 | 81 | 0
789.56 | 277.383 | 0 | 297 |  |  |  | 61.92 | 277.33 | 0 | 303 |  |  |  | 61.92 | 277.279 | 0 | 313 |  |  |  | 61.921 | 533.38 | 0.153 | 82 | 0
790.09 | 277.383 | 0 | 297 |  |  |  | 61.92 | 277.33 | 0 | 303 |  |  |  | 61.92 | 277.279 | 0 | 313 |  |  |  | 61.921 | 533.38 | 0.153 | 82 | 0
790.59 | 277.317 | 0 | 299 |  |  |  | 61.92 | 277.492 | 0 | 300 |  |  |  | 61.921 | 277.232 | 0 | 312 |  |  |  | 61.92 | 527.14 | 0.155 | 82 | 0
791.08 | 277.317 | 0 | 299 |  |  |  | 61.92 | 277.492 | 0 | 300 |  |  |  | 61.921 | 277.232 | 0 | 312 |  |  |  | 61.92 | 527.14 | 0.155 | 82 | 0
791.58 | 277.395 | 0 | 297 |  |  |  | 61.92 | 277.342 | 0 | 303 |  |  |  | 61.92 | 277.207 | 0 | 307 |  |  |  | 61.921 | 526.91 | 0.157 | 83 | 0
792.06 | 277.395 | 0 | 297 |  |  |  | 61.92 | 277.342 | 0 | 303 |  |  |  | 61.92 | 277.207 | 0 | 307 |  |  |  | 61.921 | 526.91 | 0.157 | 83 | 0
792.56 | 277.346 | 0 | 296 |  |  |  | 61.921 | 277.482 | 0 | 303 |  |  |  | 61.921 | 277.316 | 0 | 307 |  |  |  | 61.92 | 533.35 | 0.156 | 83 | 0
793.1 | 277.346 | 0 | 296 |  |  |  | 61.921 | 277.482 | 0 | 303 |  |  |  | 61.921 | 277.316 | 0 | 307 |  |  |  | 61.92 | 533.35 | 0.156 | 83 | 0
793.6 | 277.373 | 0 | 299 |  |  |  | 61.921 | 277.4 | 0 | 303 |  |  |  | 61.92 | 277.309 | 0 | 309 |  |  |  | 61.921 | 533.36 | 0.154 | 82 | 0
794.09 | 277.444 | 0 | 298 |  |  |  | 61.921 | 277.265 | 0 | 303 |  |  |  | 61.92 | 277.256 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.149 | 79 | 0
794.59 | 277.444 | 0 | 298 |  |  |  | 61.921 | 277.265 | 0 | 303 |  |  |  | 61.92 | 277.256 | 0 | 310 |  |  |  | 61.92 | 533.39 | 0.149 | 79 | 0
795.07 | 277.351 | 0 | 296 |  |  |  | 61.92 | 277.497 | 0 | 304 |  |  |  | 61.92 | 277.211 | 0 | 311 |  |  |  | 61.921 | 533.41 | 0.157 | 84 | 0
795.57 | 277.351 | 0 | 296 |  |  |  | 61.92 | 277.497 | 0 | 304 |  |  |  | 61.92 | 277.211 | 0 | 311 |  |  |  | 61.921 | 533.41 | 0.157 | 84 | 0
796.06 | 277.399 | 0 | 296 |  |  |  | 61.921 | 277.367 | 0 | 299 |  |  |  | 61.92 | 277.299 | 0 | 303 |  |  |  | 61.92 | 539.52 | 0.156 | 84 | 0
796.56 | 277.399 | 0 | 296 |  |  |  | 61.921 | 277.367 | 0 | 299 |  |  |  | 61.92 | 277.299 | 0 | 303 |  |  |  | 61.92 | 539.52 | 0.156 | 84 | 0
797.06 | 277.374 | 0 | 292 |  |  |  | 61.92 | 277.516 | 0 | 300 |  |  |  | 61.923 | 277.29 | 0 | 304 |  |  |  | 61.921 | 539.79 | 0.151 | 81 | 0
797.56 | 277.374 | 0 | 292 |  |  |  | 61.92 | 277.516 | 0 | 300 |  |  |  | 61.923 | 277.29 | 0 | 304 |  |  |  | 61.921 | 539.79 | 0.151 | 81 | 0
798.06 | 277.416 | 0 | 298 |  |  |  | 61.92 | 277.387 | 0 | 302 |  |  |  | 61.919 | 277.274 | 0 | 311 |  |  |  | 61.919 | 533.54 | 0.156 | 83 | 0
798.56 | 277.416 | 0 | 298 |  |  |  | 61.92 | 277.387 | 0 | 302 |  |  |  | 61.919 | 277.274 | 0 | 311 |  |  |  | 61.919 | 533.54 | 0.156 | 83 | 0
799.06 | 277.334 | 0 | 298 |  |  |  | 61.921 | 277.312 | 0 | 308 |  |  |  | 61.92 | 277.214 | 0 | 309 |  |  |  | 61.921 | 533.47 | 0.155 | 83 | 0
799.56 | 277.334 | 0 | 298 |  |  |  | 61.921 | 277.312 | 0 | 308 |  |  |  | 61.92 | 277.214 | 0 | 309 |  |  |  | 61.921 | 533.47 | 0.155 | 83 | 0
800.06 | 277.417 | 0 | 299 |  |  |  | 61.921 | 277.418 | 0 | 302 |  |  |  | 61.92 | 277.302 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 0
800.56 | 277.417 | 0 | 299 |  |  |  | 61.921 | 277.418 | 0 | 302 |  |  |  | 61.92 | 277.302 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.154 | 82 | 0
801.06 | 277.336 | 0 | 302 |  |  |  | 61.92 | 277.301 | 0 | 302 |  |  |  | 61.919 | 277.293 | 0 | 307 |  |  |  | 61.921 | 533.3 | 0.155 | 83 | 0
801.56 | 277.336 | 0 | 302 |  |  |  | 61.92 | 277.301 | 0 | 302 |  |  |  | 61.919 | 277.293 | 0 | 307 |  |  |  | 61.921 | 533.3 | 0.155 | 83 | 0
802.06 | 277.359 | 0 | 295 |  |  |  | 61.92 | 277.491 | 0 | 304 |  |  |  | 61.922 | 277.299 | 0 | 314 |  |  |  | 61.92 | 527.36 | 0.154 | 81 | 0
802.56 | 277.359 | 0 | 295 |  |  |  | 61.92 | 277.491 | 0 | 304 |  |  |  | 61.922 | 277.299 | 0 | 314 |  |  |  | 61.92 | 527.36 | 0.154 | 81 | 0
803.06 | 277.432 | 0 | 295 |  |  |  | 61.92 | 277.362 | 0 | 303 |  |  |  | 61.921 | 277.246 | 0 | 305 |  |  |  | 61.921 | 526.93 | 0.147 | 78 | 0
803.56 | 277.432 | 0 | 295 |  |  |  | 61.92 | 277.362 | 0 | 303 |  |  |  | 61.921 | 277.246 | 0 | 305 |  |  |  | 61.921 | 526.93 | 0.147 | 78 | 0
804.06 | 277.366 | 0 | 294 |  |  |  | 61.921 | 277.384 | 0 | 301 |  |  |  | 61.919 | 277.205 | 0 | 311 |  |  |  | 61.92 | 533.25 | 0.158 | 84 | 0
804.56 | 277.366 | 0 | 294 |  |  |  | 61.921 | 277.384 | 0 | 301 |  |  |  | 61.919 | 277.205 | 0 | 311 |  |  |  | 61.92 | 533.25 | 0.158 | 84 | 0
805.06 | 277.409 | 0 | 299 |  |  |  | 61.92 | 277.384 | 0 | 301 |  |  |  | 61.92 | 277.284 | 0 | 311 |  |  |  | 61.921 | 533.35 | 0.152 | 81 | 0
805.56 | 277.409 | 0 | 299 |  |  |  | 61.92 | 277.384 | 0 | 301 |  |  |  | 61.92 | 277.284 | 0 | 311 |  |  |  | 61.921 | 533.35 | 0.152 | 81 | 0
806.06 | 277.373 | 0 | 296 |  |  |  | 61.921 | 277.247 | 0 | 302 |  |  |  | 61.92 | 277.278 | 0 | 313 |  |  |  | 61.92 | 533.36 | 0.157 | 84 | 0
806.56 | 277.373 | 0 | 296 |  |  |  | 61.921 | 277.247 | 0 | 302 |  |  |  | 61.92 | 277.278 | 0 | 313 |  |  |  | 61.92 | 533.36 | 0.157 | 84 | 0
807.06 | 277.428 | 0 | 297 |  |  |  | 61.921 | 277.428 | 0 | 305 |  |  |  | 61.921 | 277.263 | 0 | 313 |  |  |  | 61.921 | 533.55 | 0.159 | 85 | 0
807.56 | 277.428 | 0 | 297 |  |  |  | 61.921 | 277.428 | 0 | 305 |  |  |  | 61.921 | 277.263 | 0 | 313 |  |  |  | 61.921 | 533.55 | 0.159 | 85 | 0
808.06 | 277.33 | 0 | 293 |  |  |  | 61.92 | 277.31 | 0 | 299 |  |  |  | 61.919 | 277.209 | 0 | 307 |  |  |  | 61.921 | 539.52 | 0.148 | 80 | 0
808.56 | 277.33 | 0 | 293 |  |  |  | 61.92 | 277.31 | 0 | 299 |  |  |  | 61.919 | 277.209 | 0 | 307 |  |  |  | 61.921 | 539.52 | 0.148 | 80 | 0
809.06 | 277.413 | 0 | 291 |  |  |  | 61.92 | 277.461 | 0 | 297 |  |  |  | 61.922 | 277.315 | 0 | 304 |  |  |  | 61.921 | 539.77 | 0.154 | 83 | 0
809.56 | 277.413 | 0 | 291 |  |  |  | 61.92 | 277.461 | 0 | 297 |  |  |  | 61.922 | 277.315 | 0 | 304 |  |  |  | 61.921 | 539.77 | 0.154 | 83 | 0
810.06 | 277.326 | 0 | 301 |  |  |  | 61.918 | 277.346 | 0 | 304 |  |  |  | 61.92 | 277.273 | 0 | 311 |  |  |  | 61.921 | 533.62 | 0.151 | 81 | 0
810.56 | 277.326 | 0 | 301 |  |  |  | 61.918 | 277.346 | 0 | 304 |  |  |  | 61.92 | 277.273 | 0 | 311 |  |  |  | 61.921 | 533.62 | 0.151 | 81 | 0
811.06 | 277.352 | 0 | 299 |  |  |  | 61.92 | 277.251 | 0 | 305 |  |  |  | 61.921 | 277.277 | 0 | 310 |  |  |  | 61.921 | 533.4 | 0.155 | 83 | 0
811.56 | 277.352 | 0 | 299 |  |  |  | 61.92 | 277.251 | 0 | 305 |  |  |  | 61.921 | 277.277 | 0 | 310 |  |  |  | 61.921 | 533.4 | 0.155 | 83 | 0
812.06 | 277.428 | 0 | 298 |  |  |  | 61.92 | 277.426 | 0 | 303 |  |  |  | 61.92 | 277.246 | 0 | 313 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
812.56 | 277.428 | 0 | 298 |  |  |  | 61.92 | 277.426 | 0 | 303 |  |  |  | 61.92 | 277.246 | 0 | 313 |  |  |  | 61.92 | 533.41 | 0.156 | 83 | 0
813.06 | 277.368 | 0 | 302 |  |  |  | 61.92 | 277.276 | 0 | 301 |  |  |  | 61.919 | 277.329 | 0 | 312 |  |  |  | 61.92 | 533.41 | 0.151 | 81 | 0
813.56 | 277.368 | 0 | 302 |  |  |  | 61.92 | 277.276 | 0 | 301 |  |  |  | 61.919 | 277.329 | 0 | 312 |  |  |  | 61.92 | 533.41 | 0.151 | 81 | 0
814.06 | 277.401 | 0 | 296 |  |  |  | 61.921 | 277.494 | 0 | 305 |  |  |  | 61.921 | 277.275 | 0 | 313 |  |  |  | 61.921 | 527.48 | 0.155 | 82 | 0
814.56 | 277.401 | 0 | 296 |  |  |  | 61.921 | 277.494 | 0 | 305 |  |  |  | 61.921 | 277.275 | 0 | 313 |  |  |  | 61.921 | 527.48 | 0.155 | 82 | 0
815.06 | 277.365 | 0 | 297 |  |  |  | 61.92 | 277.35 | 0 | 299 |  |  |  | 61.92 | 277.253 | 0 | 312 |  |  |  | 61.92 | 526.97 | 0.154 | 81 | 0
815.56 | 277.365 | 0 | 297 |  |  |  | 61.92 | 277.35 | 0 | 299 |  |  |  | 61.92 | 277.253 | 0 | 312 |  |  |  | 61.92 | 526.97 | 0.154 | 81 | 0
816.06 | 277.429 | 0 | 296 |  |  |  | 61.921 | 277.344 | 0 | 298 |  |  |  | 61.92 | 277.238 | 0 | 310 |  |  |  | 61.92 | 533.21 | 0.154 | 82 | 0
816.56 | 277.429 | 0 | 296 |  |  |  | 61.921 | 277.344 | 0 | 298 |  |  |  | 61.92 | 277.238 | 0 | 310 |  |  |  | 61.92 | 533.21 | 0.154 | 82 | 0
817.06 | 277.303 | 0 | 297 |  |  |  | 61.92 | 277.418 | 0 | 302 |  |  |  | 61.92 | 277.333 | 0 | 315 |  |  |  | 61.923 | 533.47 | 0.15 | 80 | 0
817.56 | 277.303 | 0 | 297 |  |  |  | 61.92 | 277.418 | 0 | 302 |  |  |  | 61.92 | 277.333 | 0 | 315 |  |  |  | 61.923 | 533.47 | 0.15 | 80 | 0
818.06 | 277.372 | 0 | 299 |  |  |  | 61.921 | 277.293 | 0 | 306 |  |  |  | 61.919 | 277.304 | 0 | 313 |  |  |  | 61.921 | 533.47 | 0.156 | 83 | 0
818.56 | 277.372 | 0 | 299 |  |  |  | 61.921 | 277.293 | 0 | 306 |  |  |  | 61.919 | 277.304 | 0 | 313 |  |  |  | 61.921 | 533.47 | 0.156 | 83 | 0
819.06 | 277.324 | 0 | 297 |  |  |  | 61.919 | 277.486 | 0 | 308 |  |  |  | 61.92 | 277.263 | 0 | 310 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 0
819.56 | 277.324 | 0 | 297 |  |  |  | 61.919 | 277.486 | 0 | 308 |  |  |  | 61.92 | 277.263 | 0 | 310 |  |  |  | 61.92 | 533.47 | 0.152 | 81 | 0
820.06 | 277.333 | 0 | 299 |  |  |  | 61.92 | 277.339 | 0 | 297 |  |  |  | 61.92 | 277.242 | 0 | 305 |  |  |  | 61.92 | 539.2 | 0.15 | 81 | 0
820.6 | 277.333 | 0 | 299 |  |  |  | 61.92 | 277.339 | 0 | 297 |  |  |  | 61.92 | 277.242 | 0 | 305 |  |  |  | 61.92 | 539.2 | 0.15 | 81 | 0
821.1 | 277.38 | 0 | 293 |  |  |  | 61.921 | 277.51 | 0 | 295 |  |  |  | 61.923 | 277.221 | 0 | 304 |  |  |  | 61.92 | 539.87 | 0.157 | 85 | 0
821.58 | 277.38 | 0 | 293 |  |  |  | 61.921 | 277.51 | 0 | 295 |  |  |  | 61.923 | 277.221 | 0 | 304 |  |  |  | 61.92 | 539.87 | 0.157 | 85 | 0
822.08 | 277.352 | 0 | 300 |  |  |  | 61.92 | 277.41 | 0 | 305 |  |  |  | 61.921 | 277.317 | 0 | 314 |  |  |  | 61.921 | 533.77 | 0.153 | 82 | 0
822.56 | 277.352 | 0 | 300 |  |  |  | 61.92 | 277.41 | 0 | 305 |  |  |  | 61.921 | 277.317 | 0 | 314 |  |  |  | 61.921 | 533.77 | 0.153 | 82 | 0
823.06 | 277.381 | 0 | 299 |  |  |  | 61.92 | 277.299 | 0 | 304 |  |  |  | 61.919 | 277.272 | 0 | 313 |  |  |  | 61.921 | 533.54 | 0.157 | 84 | 0
823.6 | 277.381 | 0 | 299 |  |  |  | 61.92 | 277.299 | 0 | 304 |  |  |  | 61.919 | 277.272 | 0 | 313 |  |  |  | 61.921 | 533.54 | 0.157 | 84 | 0
824.1 | 277.337 | 0 | 296 |  |  |  | 61.921 | 277.459 | 0 | 304 |  |  |  | 61.921 | 277.23 | 0 | 312 |  |  |  | 61.921 | 533.53 | 0.154 | 82 | 0
824.59 | 277.423 | 0 | 297 |  |  |  | 61.92 | 277.331 | 0 | 303 |  |  |  | 61.919 | 277.219 | 0 | 312 |  |  |  | 61.92 | 533.39 | 0.145 | 77 | 0
825.09 | 277.423 | 0 | 297 |  |  |  | 61.92 | 277.331 | 0 | 303 |  |  |  | 61.919 | 277.219 | 0 | 312 |  |  |  | 61.92 | 533.39 | 0.145 | 77 | 0
825.57 | 277.295 | 0 | 302 |  |  |  | 61.92 | 277.517 | 0 | 299 |  |  |  | 61.922 | 277.317 | 0 | 311 |  |  |  | 61.92 | 527.61 | 0.154 | 81 | 0
826.07 | 277.295 | 0 | 302 |  |  |  | 61.92 | 277.517 | 0 | 299 |  |  |  | 61.922 | 277.317 | 0 | 311 |  |  |  | 61.92 | 527.61 | 0.154 | 81 | 0
826.56 | 277.384 | 0 | 299 |  |  |  | 61.921 | 277.383 | 0 | 300 |  |  |  | 61.92 | 277.296 | 0 | 310 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 0
827.06 | 277.384 | 0 | 299 |  |  |  | 61.921 | 277.383 | 0 | 300 |  |  |  | 61.92 | 277.296 | 0 | 310 |  |  |  | 61.92 | 526.92 | 0.152 | 80 | 0
827.56 | 277.329 | 0 | 295 |  |  |  | 61.92 | 277.377 | 0 | 303 |  |  |  | 61.921 | 277.252 | 0 | 311 |  |  |  | 61.921 | 533.01 | 0.149 | 80 | 0
828.06 | 277.329 | 0 | 295 |  |  |  | 61.92 | 277.377 | 0 | 303 |  |  |  | 61.921 | 277.252 | 0 | 311 |  |  |  | 61.921 | 533.01 | 0.149 | 80 | 0
828.56 | 277.334 | 0 | 304 |  |  |  | 61.921 | 277.449 | 0 | 304 |  |  |  | 61.919 | 277.228 | 0 | 314 |  |  |  | 61.92 | 533.5 | 0.151 | 80 | 0
829.06 | 277.334 | 0 | 304 |  |  |  | 61.921 | 277.449 | 0 | 304 |  |  |  | 61.919 | 277.228 | 0 | 314 |  |  |  | 61.92 | 533.5 | 0.151 | 80 | 0
829.56 | 277.393 | 0 | 297 |  |  |  | 61.921 | 277.315 | 0 | 300 |  |  |  | 61.92 | 277.315 | 0 | 313 |  |  |  | 61.919 | 533.42 | 0.152 | 81 | 0
830.06 | 277.393 | 0 | 297 |  |  |  | 61.921 | 277.315 | 0 | 300 |  |  |  | 61.92 | 277.315 | 0 | 313 |  |  |  | 61.919 | 533.42 | 0.152 | 81 | 0
830.56 | 277.344 | 0 | 297 |  |  |  | 61.921 | 277.525 | 0 | 303 |  |  |  | 61.92 | 277.308 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 0
831.06 | 277.344 | 0 | 297 |  |  |  | 61.921 | 277.525 | 0 | 303 |  |  |  | 61.92 | 277.308 | 0 | 310 |  |  |  | 61.921 | 533.41 | 0.154 | 82 | 0
831.56 | 277.4 | 0 | 296 |  |  |  | 61.921 | 277.4 | 0 | 298 |  |  |  | 61.919 | 277.252 | 0 | 306 |  |  |  | 61.921 | 539.2 | 0.153 | 82 | 0
832.06 | 277.4 | 0 | 296 |  |  |  | 61.921 | 277.4 | 0 | 298 |  |  |  | 61.919 | 277.252 | 0 | 306 |  |  |  | 61.921 | 539.2 | 0.153 | 82 | 0
832.56 | 277.322 | 0 | 291 |  |  |  | 61.92 | 277.502 | 0 | 298 |  |  |  | 61.923 | 277.221 | 0 | 309 |  |  |  | 61.919 | 539.89 | 0.154 | 83 | 0
833.06 | 277.322 | 0 | 291 |  |  |  | 61.92 | 277.502 | 0 | 298 |  |  |  | 61.923 | 277.221 | 0 | 309 |  |  |  | 61.919 | 539.89 | 0.154 | 83 | 0
833.56 | 277.4 | 0 | 301 |  |  |  | 61.92 | 277.393 | 0 | 307 |  |  |  | 61.92 | 277.311 | 0 | 313 |  |  |  | 61.922 | 533.73 | 0.154 | 82 | 0
834.06 | 277.4 | 0 | 301 |  |  |  | 61.92 | 277.393 | 0 | 307 |  |  |  | 61.92 | 277.311 | 0 | 313 |  |  |  | 61.922 | 533.73 | 0.154 | 82 | 0
834.56 | 277.298 | 0 | 299 |  |  |  | 61.92 | 277.288 | 0 | 300 |  |  |  | 61.919 | 277.317 | 0 | 309 |  |  |  | 61.921 | 533.36 | 0.15 | 80 | 0
835.06 | 277.298 | 0 | 299 |  |  |  | 61.92 | 277.288 | 0 | 300 |  |  |  | 61.919 | 277.317 | 0 | 309 |  |  |  | 61.921 | 533.36 | 0.15 | 80 | 0
835.56 | 277.355 | 0 | 303 |  |  |  | 61.921 | 277.431 | 0 | 300 |  |  |  | 61.919 | 277.282 | 0 | 311 |  |  |  | 61.92 | 533.52 | 0.155 | 83 | 0
836.06 | 277.355 | 0 | 303 |  |  |  | 61.921 | 277.431 | 0 | 300 |  |  |  | 61.919 | 277.282 | 0 | 311 |  |  |  | 61.92 | 533.52 | 0.155 | 83 | 0
836.56 | 277.327 | 0 | 302 |  |  |  | 61.921 | 277.327 | 0 | 305 |  |  |  | 61.919 | 277.241 | 0 | 314 |  |  |  | 61.92 | 533.42 | 0.155 | 82 | 0
837.06 | 277.327 | 0 | 302 |  |  |  | 61.921 | 277.327 | 0 | 305 |  |  |  | 61.919 | 277.241 | 0 | 314 |  |  |  | 61.92 | 533.42 | 0.155 | 82 | 0
837.56 | 277.348 | 0 | 298 |  |  |  | 61.92 | 277.506 | 0 | 306 |  |  |  | 61.923 | 277.214 | 0 | 304 |  |  |  | 61.919 | 527.54 | 0.155 | 82 | 0
838.06 | 277.348 | 0 | 298 |  |  |  | 61.92 | 277.506 | 0 | 306 |  |  |  | 61.923 | 277.214 | 0 | 304 |  |  |  | 61.919 | 527.54 | 0.155 | 82 | 0
838.56 | 277.379 | 0 | 295 |  |  |  | 61.921 | 277.368 | 0 | 301 |  |  |  | 61.921 | 277.299 | 0 | 311 |  |  |  | 61.92 | 526.97 | 0.151 | 79 | 0
839.06 | 277.379 | 0 | 295 |  |  |  | 61.921 | 277.368 | 0 | 301 |  |  |  | 61.921 | 277.299 | 0 | 311 |  |  |  | 61.92 | 526.97 | 0.151 | 79 | 0
839.56 | 277.355 | 0 | 290 |  |  |  | 61.921 | 277.34 | 0 | 296 |  |  |  | 61.919 | 277.293 | 0 | 309 |  |  |  | 61.92 | 532.83 | 0.151 | 80 | 0
840.06 | 277.355 | 0 | 290 |  |  |  | 61.921 | 277.34 | 0 | 296 |  |  |  | 61.919 | 277.293 | 0 | 309 |  |  |  | 61.92 | 532.83 | 0.151 | 80 | 0
840.56 | 277.4 | 0 | 299 |  |  |  | 61.921 | 277.451 | 0 | 304 |  |  |  | 61.92 | 277.244 | 0 | 310 |  |  |  | 61.92 | 533.49 | 0.153 | 82 | 0
841.06 | 277.4 | 0 | 299 |  |  |  | 61.921 | 277.451 | 0 | 304 |  |  |  | 61.92 | 277.244 | 0 | 310 |  |  |  | 61.92 | 533.49 | 0.153 | 82 | 0
841.56 | 277.318 | 0 | 298 |  |  |  | 61.921 | 277.277 | 0 | 302 |  |  |  | 61.919 | 277.19 | 0 | 312 |  |  |  | 61.919 | 533.34 | 0.153 | 82 | 0
842.06 | 277.318 | 0 | 298 |  |  |  | 61.921 | 277.277 | 0 | 302 |  |  |  | 61.919 | 277.19 | 0 | 312 |  |  |  | 61.919 | 533.34 | 0.153 | 82 | 0
842.56 | 277.398 | 0 | 294 |  |  |  | 61.921 | 277.434 | 0 | 299 |  |  |  | 61.919 | 277.298 | 0 | 310 |  |  |  | 61.92 | 533.35 | 0.152 | 81 | 0
843.06 | 277.398 | 0 | 294 |  |  |  | 61.921 | 277.434 | 0 | 299 |  |  |  | 61.919 | 277.298 | 0 | 310 |  |  |  | 61.92 | 533.35 | 0.152 | 81 | 0
843.56 | 277.29 | 0 | 294 |  |  |  | 61.92 | 277.337 | 0 | 301 |  |  |  | 61.92 | 277.288 | 0 | 309 |  |  |  | 61.921 | 539.14 | 0.153 | 82 | 0
844.06 | 277.29 | 0 | 294 |  |  |  | 61.92 | 277.337 | 0 | 301 |  |  |  | 61.92 | 277.288 | 0 | 309 |  |  |  | 61.921 | 539.14 | 0.153 | 82 | 0
844.56 | 277.363 | 0 | 295 |  |  |  | 61.92 | 277.504 | 0 | 297 |  |  |  | 61.925 | 277.261 | 0 | 305 |  |  |  | 61.921 | 539.86 | 0.154 | 83 | 0
845.06 | 277.363 | 0 | 295 |  |  |  | 61.92 | 277.504 | 0 | 297 |  |  |  | 61.925 | 277.261 | 0 | 305 |  |  |  | 61.921 | 539.86 | 0.154 | 83 | 0
845.56 | 277.337 | 0 | 301 |  |  |  | 61.92 | 277.393 | 0 | 306 |  |  |  | 61.92 | 277.214 | 0 | 313 |  |  |  | 61.92 | 533.94 | 0.153 | 82 | 0
846.06 | 277.337 | 0 | 301 |  |  |  | 61.92 | 277.393 | 0 | 306 |  |  |  | 61.92 | 277.214 | 0 | 313 |  |  |  | 61.92 | 533.94 | 0.153 | 82 | 0
846.56 | 277.352 | 0 | 297 |  |  |  | 61.92 | 277.274 | 0 | 304 |  |  |  | 61.919 | 277.311 | 0 | 313 |  |  |  | 61.92 | 533.49 | 0.152 | 81 | 0
847.06 | 277.352 | 0 | 297 |  |  |  | 61.92 | 277.274 | 0 | 304 |  |  |  | 61.919 | 277.311 | 0 | 313 |  |  |  | 61.92 | 533.49 | 0.152 | 81 | 0
847.56 | 277.39 | 0 | 298 |  |  |  | 61.921 | 277.444 | 0 | 305 |  |  |  | 61.919 | 277.286 | 0 | 310 |  |  |  | 61.92 | 533.4 | 0.151 | 81 | 0
848.06 | 277.39 | 0 | 298 |  |  |  | 61.921 | 277.444 | 0 | 305 |  |  |  | 61.919 | 277.286 | 0 | 310 |  |  |  | 61.92 | 533.4 | 0.151 | 81 | 0
848.56 | 277.354 | 0 | 299 |  |  |  | 61.919 | 277.274 | 0 | 301 |  |  |  | 61.919 | 277.275 | 0 | 313 |  |  |  | 61.921 | 533.44 | 0.15 | 80 | 0
849.06 | 277.354 | 0 | 299 |  |  |  | 61.919 | 277.274 | 0 | 301 |  |  |  | 61.919 | 277.275 | 0 | 313 |  |  |  | 61.921 | 533.44 | 0.15 | 80 | 0
849.56 | 277.403 | 0 | 298 |  |  |  | 61.921 | 277.495 | 0 | 300 |  |  |  | 61.923 | 277.235 | 0 | 307 |  |  |  | 61.919 | 527.68 | 0.156 | 83 | 0
850.06 | 277.403 | 0 | 298 |  |  |  | 61.921 | 277.495 | 0 | 300 |  |  |  | 61.923 | 277.235 | 0 | 307 |  |  |  | 61.919 | 527.68 | 0.156 | 83 | 0
850.56 | 277.31 | 0 | 298 |  |  |  | 61.92 | 277.346 | 0 | 299 |  |  |  | 61.919 | 277.322 | 0 | 311 |  |  |  | 61.92 | 526.98 | 0.149 | 78 | 0
851.06 | 277.31 | 0 | 298 |  |  |  | 61.92 | 277.346 | 0 | 299 |  |  |  | 61.919 | 277.322 | 0 | 311 |  |  |  | 61.92 | 526.98 | 0.149 | 78 | 0
851.56 | 277.385 | 0 | 296 |  |  |  | 61.921 | 277.383 | 0 | 297 |  |  |  | 61.921 | 277.282 | 0 | 311 |  |  |  | 61.921 | 532.82 | 0.153 | 82 | 0
852.09 | 277.385 | 0 | 296 |  |  |  | 61.921 | 277.383 | 0 | 297 |  |  |  | 61.921 | 277.282 | 0 | 311 |  |  |  | 61.921 | 532.82 | 0.153 | 82 | 0
852.59 | 277.301 | 0 | 296 |  |  |  | 61.92 | 277.402 | 0 | 308 |  |  |  | 61.92 | 277.269 | 0 | 309 |  |  |  | 61.92 | 533.29 | 0.154 | 82 | 0
853.08 | 277.301 | 0 | 296 |  |  |  | 61.92 | 277.402 | 0 | 308 |  |  |  | 61.92 | 277.269 | 0 | 309 |  |  |  | 61.92 | 533.29 | 0.154 | 82 | 0
853.58 | 277.362 | 0 | 299 |  |  |  | 61.919 | 277.277 | 0 | 304 |  |  |  | 61.919 | 277.259 | 0 | 313 |  |  |  | 61.92 | 533.36 | 0.152 | 81 | 0
854.06 | 277.362 | 0 | 299 |  |  |  | 61.919 | 277.277 | 0 | 304 |  |  |  | 61.919 | 277.259 | 0 | 313 |  |  |  | 61.92 | 533.36 | 0.152 | 81 | 0
854.56 | 277.33 | 0 | 296 |  |  |  | 61.918 | 277.431 | 0 | 300 |  |  |  | 61.92 | 277.341 | 0 | 310 |  |  |  | 61.922 | 533.31 | 0.149 | 80 | 0
855.1 | 277.33 | 0 | 296 |  |  |  | 61.918 | 277.431 | 0 | 300 |  |  |  | 61.92 | 277.341 | 0 | 310 |  |  |  | 61.922 | 533.31 | 0.149 | 80 | 0
855.6 | 277.36 | 0 | 293 |  |  |  | 61.921 | 277.32 | 0 | 303 |  |  |  | 61.92 | 277.302 | 0 | 308 |  |  |  | 61.921 | 538.97 | 0.15 | 81 | 0
856.09 | 277.402 | 0 | 289 |  |  |  | 61.921 | 277.495 | 0 | 298 |  |  |  | 61.923 | 277.267 | 0 | 307 |  |  |  | 61.919 | 539.83 | 0.155 | 83 | 0
856.59 | 277.402 | 0 | 289 |  |  |  | 61.921 | 277.495 | 0 | 298 |  |  |  | 61.923 | 277.267 | 0 | 307 |  |  |  | 61.919 | 539.83 | 0.155 | 83 | 0
857.07 | 277.35 | 0 | 303 |  |  |  | 61.921 | 277.35 | 0 | 305 |  |  |  | 61.919 | 277.261 | 0 | 313 |  |  |  | 61.919 | 533.91 | 0.153 | 82 | 0
857.57 | 277.35 | 0 | 303 |  |  |  | 61.921 | 277.35 | 0 | 305 |  |  |  | 61.919 | 277.261 | 0 | 313 |  |  |  | 61.919 | 533.91 | 0.153 | 82 | 0
858.06 | 277.41 | 0 | 299 |  |  |  | 61.921 | 277.265 | 0 | 303 |  |  |  | 61.92 | 277.221 | 0 | 312 |  |  |  | 61.92 | 533.38 | 0.153 | 82 | 0
858.56 | 277.41 | 0 | 299 |  |  |  | 61.921 | 277.265 | 0 | 303 |  |  |  | 61.92 | 277.221 | 0 | 312 |  |  |  | 61.92 | 533.38 | 0.153 | 82 | 0
859.06 | 277.293 | 0 | 296 |  |  |  | 61.921 | 277.469 | 0 | 303 |  |  |  | 61.92 | 277.313 | 0 | 312 |  |  |  | 61.921 | 533.43 | 0.152 | 81 | 0
859.56 | 277.293 | 0 | 296 |  |  |  | 61.921 | 277.469 | 0 | 303 |  |  |  | 61.92 | 277.313 | 0 | 312 |  |  |  | 61.921 | 533.43 | 0.152 | 81 | 0
860.06 | 277.379 | 0 | 302 |  |  |  | 61.92 | 277.336 | 0 | 305 |  |  |  | 61.919 | 277.269 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.15 | 80 | 0
860.56 | 277.379 | 0 | 302 |  |  |  | 61.92 | 277.336 | 0 | 305 |  |  |  | 61.919 | 277.269 | 0 | 311 |  |  |  | 61.92 | 533.44 | 0.15 | 80 | 0
861.06 | 277.296 | 0 | 297 |  |  |  | 61.921 | 277.522 | 0 | 301 |  |  |  | 61.921 | 277.237 | 0 | 308 |  |  |  | 61.919 | 527.73 | 0.149 | 79 | 0
861.56 | 277.296 | 0 | 297 |  |  |  | 61.921 | 277.522 | 0 | 301 |  |  |  | 61.921 | 277.237 | 0 | 308 |  |  |  | 61.919 | 527.73 | 0.149 | 79 | 0
862.06 | 277.35 | 0 | 294 |  |  |  | 61.92 | 277.381 | 0 | 301 |  |  |  | 61.919 | 277.224 | 0 | 305 |  |  |  | 61.919 | 526.91 | 0.152 | 80 | 0
862.56 | 277.35 | 0 | 294 |  |  |  | 61.92 | 277.381 | 0 | 301 |  |  |  | 61.919 | 277.224 | 0 | 305 |  |  |  | 61.919 | 526.91 | 0.152 | 80 | 0
863.06 | 277.327 | 0 | 298 |  |  |  | 61.92 | 277.481 | 0 | 300 |  |  |  | 61.924 | 277.33 | 0 | 311 |  |  |  | 61.921 | 532.77 | 0.152 | 81 | 0
863.56 | 277.327 | 0 | 298 |  |  |  | 61.92 | 277.481 | 0 | 300 |  |  |  | 61.924 | 277.33 | 0 | 311 |  |  |  | 61.921 | 532.77 | 0.152 | 81 | 0
864.06 | 277.346 | 0 | 297 |  |  |  | 61.92 | 277.398 | 0 | 304 |  |  |  | 61.918 | 277.289 | 0 | 313 |  |  |  | 61.92 | 533.47 | 0.151 | 80 | 0
864.56 | 277.346 | 0 | 297 |  |  |  | 61.92 | 277.398 | 0 | 304 |  |  |  | 61.918 | 277.289 | 0 | 313 |  |  |  | 61.92 | 533.47 | 0.151 | 80 | 0
865.06 | 277.392 | 0 | 297 |  |  |  | 61.921 | 277.324 | 0 | 304 |  |  |  | 61.92 | 277.243 | 0 | 313 |  |  |  | 61.921 | 533.48 | 0.158 | 84 | 0
865.56 | 277.392 | 0 | 297 |  |  |  | 61.921 | 277.324 | 0 | 304 |  |  |  | 61.92 | 277.243 | 0 | 313 |  |  |  | 61.921 | 533.48 | 0.158 | 84 | 0
866.06 | 277.338 | 0 | 297 |  |  |  | 61.92 | 277.443 | 0 | 305 |  |  |  | 61.92 | 277.224 | 0 | 307 |  |  |  | 61.919 | 533.35 | 0.149 | 79 | 0
866.56 | 277.338 | 0 | 297 |  |  |  | 61.92 | 277.443 | 0 | 305 |  |  |  | 61.92 | 277.224 | 0 | 307 |  |  |  | 61.919 | 533.35 | 0.149 | 79 | 0
867.06 | 277.406 | 0 | 292 |  |  |  | 61.921 | 277.343 | 0 | 303 |  |  |  | 61.92 | 277.315 | 0 | 307 |  |  |  | 61.92 | 539.01 | 0.153 | 82 | 0
867.56 | 277.406 | 0 | 292 |  |  |  | 61.921 | 277.343 | 0 | 303 |  |  |  | 61.92 | 277.315 | 0 | 307 |  |  |  | 61.92 | 539.01 | 0.153 | 82 | 0
868.06 | 277.305 | 0 | 294 |  |  |  | 61.921 | 277.535 | 0 | 299 |  |  |  | 61.923 | 277.298 | 0 | 305 |  |  |  | 61.92 | 539.88 | 0.161 | 87 | 0
868.56 | 277.305 | 0 | 294 |  |  |  | 61.921 | 277.535 | 0 | 299 |  |  |  | 61.923 | 277.298 | 0 | 305 |  |  |  | 61.92 | 539.88 | 0.161 | 87 | 0
869.06 | 277.37 | 0 | 298 |  |  |  | 61.92 | 277.41 | 0 | 300 |  |  |  | 61.92 | 277.245 | 0 | 313 |  |  |  | 61.92 | 533.9 | 0.151 | 81 | 0
869.56 | 277.37 | 0 | 298 |  |  |  | 61.92 | 277.41 | 0 | 300 |  |  |  | 61.92 | 277.245 | 0 | 313 |  |  |  | 61.92 | 533.9 | 0.151 | 81 | 0
870.06 | 277.312 | 0 | 301 |  |  |  | 61.921 | 277.446 | 0 | 307 |  |  |  | 61.919 | 277.217 | 0 | 308 |  |  |  | 61.921 | 533.46 | 0.154 | 82 | 0
870.56 | 277.312 | 0 | 301 |  |  |  | 61.921 | 277.446 | 0 | 307 |  |  |  | 61.919 | 277.217 | 0 | 308 |  |  |  | 61.921 | 533.46 | 0.154 | 82 | 0
871.06 | 277.348 | 0 | 299 |  |  |  | 61.92 | 277.47 | 0 | 302 |  |  |  | 61.92 | 277.312 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.156 | 83 | 0
871.56 | 277.348 | 0 | 299 |  |  |  | 61.92 | 277.47 | 0 | 302 |  |  |  | 61.92 | 277.312 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.156 | 83 | 0
872.06 | 277.325 | 0 | 296 |  |  |  | 61.92 | 277.295 | 0 | 308 |  |  |  | 61.92 | 277.302 | 0 | 313 |  |  |  | 61.919 | 533.38 | 0.155 | 83 | 0
872.56 | 277.325 | 0 | 296 |  |  |  | 61.92 | 277.295 | 0 | 308 |  |  |  | 61.92 | 277.302 | 0 | 313 |  |  |  | 61.919 | 533.38 | 0.155 | 83 | 0
873.06 | 277.357 | 0 | 298 |  |  |  | 61.919 | 277.471 | 0 | 303 |  |  |  | 61.919 | 277.266 | 0 | 311 |  |  |  | 61.92 | 527.81 | 0.153 | 81 | 0
873.56 | 277.357 | 0 | 298 |  |  |  | 61.919 | 277.471 | 0 | 303 |  |  |  | 61.919 | 277.266 | 0 | 311 |  |  |  | 61.92 | 527.81 | 0.153 | 81 | 0
874.06 | 277.382 | 0 | 294 |  |  |  | 61.92 | 277.395 | 0 | 302 |  |  |  | 61.92 | 277.216 | 0 | 308 |  |  |  | 61.92 | 527.1 | 0.151 | 80 | 0
874.56 | 277.382 | 0 | 294 |  |  |  | 61.92 | 277.395 | 0 | 302 |  |  |  | 61.92 | 277.216 | 0 | 308 |  |  |  | 61.92 | 527.1 | 0.151 | 80 | 0
875.06 | 277.336 | 0 | 297 |  |  |  | 61.92 | 277.53 | 0 | 301 |  |  |  | 61.924 | 277.306 | 0 | 309 |  |  |  | 61.919 | 532.73 | 0.157 | 84 | 0
875.56 | 277.336 | 0 | 297 |  |  |  | 61.92 | 277.53 | 0 | 301 |  |  |  | 61.924 | 277.306 | 0 | 309 |  |  |  | 61.919 | 532.73 | 0.157 | 84 | 0
876.06 | 277.399 | 0 | 299 |  |  |  | 61.921 | 277.375 | 0 | 301 |  |  |  | 61.919 | 277.293 | 0 | 308 |  |  |  | 61.921 | 533.46 | 0.152 | 81 | 0
876.56 | 277.399 | 0 | 299 |  |  |  | 61.921 | 277.375 | 0 | 301 |  |  |  | 61.919 | 277.293 | 0 | 308 |  |  |  | 61.921 | 533.46 | 0.152 | 81 | 0
877.06 | 277.31 | 0 | 298 |  |  |  | 61.921 | 277.27 | 0 | 304 |  |  |  | 61.919 | 277.276 | 0 | 313 |  |  |  | 61.92 | 533.34 | 0.154 | 82 | 0
877.56 | 277.31 | 0 | 298 |  |  |  | 61.921 | 277.27 | 0 | 304 |  |  |  | 61.919 | 277.276 | 0 | 313 |  |  |  | 61.92 | 533.34 | 0.154 | 82 | 0
878.06 | 277.379 | 0 | 302 |  |  |  | 61.92 | 277.481 | 0 | 304 |  |  |  | 61.92 | 277.222 | 0 | 311 |  |  |  | 61.921 | 533.46 | 0.157 | 84 | 0
878.56 | 277.379 | 0 | 302 |  |  |  | 61.92 | 277.481 | 0 | 304 |  |  |  | 61.92 | 277.222 | 0 | 311 |  |  |  | 61.921 | 533.46 | 0.157 | 84 | 0
879.06 | 277.33 | 0 | 296 |  |  |  | 61.921 | 277.303 | 0 | 300 |  |  |  | 61.919 | 277.224 | 0 | 310 |  |  |  | 61.919 | 538.94 | 0.159 | 86 | 0
879.56 | 277.33 | 0 | 296 |  |  |  | 61.921 | 277.303 | 0 | 300 |  |  |  | 61.919 | 277.224 | 0 | 310 |  |  |  | 61.919 | 538.94 | 0.159 | 86 | 0
880.06 | 277.376 | 0 | 295 |  |  |  | 61.921 | 277.512 | 0 | 298 |  |  |  | 61.922 | 277.293 | 0 | 305 |  |  |  | 61.921 | 539.84 | 0.155 | 84 | 0
880.56 | 277.376 | 0 | 295 |  |  |  | 61.921 | 277.512 | 0 | 298 |  |  |  | 61.922 | 277.293 | 0 | 305 |  |  |  | 61.921 | 539.84 | 0.155 | 84 | 0
881.06 | 277.337 | 0 | 299 |  |  |  | 61.921 | 277.318 | 0 | 304 |  |  |  | 61.92 | 277.293 | 0 | 313 |  |  |  | 61.92 | 534.07 | 0.151 | 81 | 0
881.56 | 277.337 | 0 | 299 |  |  |  | 61.921 | 277.318 | 0 | 304 |  |  |  | 61.92 | 277.293 | 0 | 313 |  |  |  | 61.92 | 534.07 | 0.151 | 81 | 0
882.06 | 277.362 | 0 | 302 |  |  |  | 61.919 | 277.448 | 0 | 302 |  |  |  | 61.92 | 277.252 | 0 | 309 |  |  |  | 61.921 | 533.52 | 0.156 | 83 | 0
882.56 | 277.362 | 0 | 302 |  |  |  | 61.919 | 277.448 | 0 | 302 |  |  |  | 61.92 | 277.252 | 0 | 309 |  |  |  | 61.921 | 533.52 | 0.156 | 83 | 0
883.06 | 277.407 | 0 | 299 |  |  |  | 61.921 | 277.423 | 0 | 300 |  |  |  | 61.92 | 277.201 | 0 | 312 |  |  |  | 61.921 | 533.52 | 0.157 | 84 | 0
883.59 | 277.407 | 0 | 299 |  |  |  | 61.921 | 277.423 | 0 | 300 |  |  |  | 61.92 | 277.201 | 0 | 312 |  |  |  | 61.921 | 533.52 | 0.157 | 84 | 0
884.09 | 277.327 | 0 | 293 |  |  |  | 61.921 | 277.307 | 0 | 302 |  |  |  | 61.92 | 277.288 | 0 | 313 |  |  |  | 61.92 | 533.4 | 0.159 | 85 | 0
884.58 | 277.327 | 0 | 293 |  |  |  | 61.921 | 277.307 | 0 | 302 |  |  |  | 61.92 | 277.288 | 0 | 313 |  |  |  | 61.92 | 533.4 | 0.159 | 85 | 0
885.08 | 277.406 | 0 | 294 |  |  |  | 61.92 | 277.414 | 0 | 300 |  |  |  | 61.92 | 277.27 | 0 | 311 |  |  |  | 61.92 | 527.87 | 0.159 | 84 | 0
885.56 | 277.406 | 0 | 294 |  |  |  | 61.92 | 277.414 | 0 | 300 |  |  |  | 61.92 | 277.27 | 0 | 311 |  |  |  | 61.92 | 527.87 | 0.159 | 84 | 0
886.06 | 277.308 | 0 | 298 |  |  |  | 61.921 | 277.285 | 0 | 297 |  |  |  | 61.919 | 277.269 | 0 | 308 |  |  |  | 61.921 | 526.96 | 0.156 | 82 | 0
886.56 | 277.308 | 0 | 298 |  |  |  | 61.921 | 277.285 | 0 | 297 |  |  |  | 61.919 | 277.269 | 0 | 308 |  |  |  | 61.921 | 526.96 | 0.156 | 82 | 0
887.06 | 277.369 | 0 | 300 |  |  |  | 61.92 | 277.486 | 0 | 304 |  |  |  | 61.923 | 277.222 | 0 | 306 |  |  |  | 61.919 | 532.79 | 0.155 | 83 | 0
887.56 | 277.369 | 0 | 300 |  |  |  | 61.92 | 277.486 | 0 | 304 |  |  |  | 61.923 | 277.222 | 0 | 306 |  |  |  | 61.919 | 532.79 | 0.155 | 83 | 0
888.06 | 277.314 | 0 | 299 |  |  |  | 61.921 | 277.317 | 0 | 301 |  |  |  | 61.92 | 277.305 | 0 | 307 |  |  |  | 61.919 | 533.37 | 0.156 | 83 | 0
888.56 | 277.314 | 0 | 299 |  |  |  | 61.921 | 277.317 | 0 | 301 |  |  |  | 61.92 | 277.305 | 0 | 307 |  |  |  | 61.919 | 533.37 | 0.156 | 83 | 0
889.06 | 277.37 | 0 | 296 |  |  |  | 61.92 | 277.477 | 0 | 303 |  |  |  | 61.922 | 277.268 | 0 | 309 |  |  |  | 61.92 | 533.39 | 0.158 | 85 | 0
889.56 | 277.37 | 0 | 296 |  |  |  | 61.92 | 277.477 | 0 | 303 |  |  |  | 61.922 | 277.268 | 0 | 309 |  |  |  | 61.92 | 533.39 | 0.158 | 85 | 0
890.06 | 277.288 | 0 | 297 |  |  |  | 61.919 | 277.356 | 0 | 305 |  |  |  | 61.92 | 277.264 | 0 | 308 |  |  |  | 61.919 | 533.4 | 0.157 | 84 | 0
890.58 | 277.367 | 0 | 294 |  |  |  | 61.92 | 277.221 | 0 | 295 |  |  |  | 61.919 | 277.236 | 0 | 307 |  |  |  | 61.921 | 539.24 | 0.155 | 84 | 0
891.08 | 277.367 | 0 | 294 |  |  |  | 61.92 | 277.221 | 0 | 295 |  |  |  | 61.919 | 277.236 | 0 | 307 |  |  |  | 61.921 | 539.24 | 0.155 | 84 | 0
891.57 | 277.422 | 0 | 289 |  |  |  | 61.921 | 277.458 | 0 | 298 |  |  |  | 61.92 | 277.328 | 0 | 305 |  |  |  | 61.92 | 539.89 | 0.154 | 83 | 0
892.07 | 277.422 | 0 | 289 |  |  |  | 61.921 | 277.458 | 0 | 298 |  |  |  | 61.92 | 277.328 | 0 | 305 |  |  |  | 61.92 | 539.89 | 0.154 | 83 | 0
892.56 | 277.33 | 0 | 299 |  |  |  | 61.92 | 277.344 | 0 | 304 |  |  |  | 61.92 | 277.278 | 0 | 312 |  |  |  | 61.92 | 533.77 | 0.157 | 84 | 0
893.06 | 277.33 | 0 | 299 |  |  |  | 61.92 | 277.344 | 0 | 304 |  |  |  | 61.92 | 277.278 | 0 | 312 |  |  |  | 61.92 | 533.77 | 0.157 | 84 | 0
893.56 | 277.41 | 0 | 301 |  |  |  | 61.92 | 277.449 | 0 | 298 |  |  |  | 61.922 | 277.25 | 0 | 311 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 0
894.06 | 277.41 | 0 | 301 |  |  |  | 61.92 | 277.449 | 0 | 298 |  |  |  | 61.922 | 277.25 | 0 | 311 |  |  |  | 61.92 | 533.43 | 0.152 | 81 | 0
894.56 | 277.313 | 0 | 296 |  |  |  | 61.921 | 277.343 | 0 | 304 |  |  |  | 61.92 | 277.241 | 0 | 311 |  |  |  | 61.921 | 533.45 | 0.158 | 85 | 0
895.06 | 277.313 | 0 | 296 |  |  |  | 61.921 | 277.343 | 0 | 304 |  |  |  | 61.92 | 277.241 | 0 | 311 |  |  |  | 61.921 | 533.45 | 0.158 | 85 | 0
895.56 | 277.37 | 0 | 299 |  |  |  | 61.92 | 277.341 | 0 | 308 |  |  |  | 61.919 | 277.337 | 0 | 313 |  |  |  | 61.92 | 533.54 | 0.156 | 83 | 0
896.06 | 277.37 | 0 | 299 |  |  |  | 61.92 | 277.341 | 0 | 308 |  |  |  | 61.919 | 277.337 | 0 | 313 |  |  |  | 61.92 | 533.54 | 0.156 | 83 | 0
896.56 | 277.319 | 0 | 301 |  |  |  | 61.921 | 277.394 | 0 | 302 |  |  |  | 61.92 | 277.316 | 0 | 307 |  |  |  | 61.92 | 527.66 | 0.156 | 83 | 0
897.06 | 277.319 | 0 | 301 |  |  |  | 61.921 | 277.394 | 0 | 302 |  |  |  | 61.92 | 277.316 | 0 | 307 |  |  |  | 61.92 | 527.66 | 0.156 | 83 | 0
897.56 | 277.37 | 0 | 294 |  |  |  | 61.921 | 277.308 | 0 | 301 |  |  |  | 61.918 | 277.266 | 0 | 308 |  |  |  | 61.921 | 526.93 | 0.159 | 84 | 0
898.06 | 277.37 | 0 | 294 |  |  |  | 61.921 | 277.308 | 0 | 301 |  |  |  | 61.918 | 277.266 | 0 | 308 |  |  |  | 61.921 | 526.93 | 0.159 | 84 | 0
898.56 | 277.286 | 0 | 297 |  |  |  | 61.918 | 277.467 | 0 | 302 |  |  |  | 61.919 | 277.247 | 0 | 307 |  |  |  | 61.92 | 532.86 | 0.157 | 84 | 0
899.06 | 277.286 | 0 | 297 |  |  |  | 61.918 | 277.467 | 0 | 302 |  |  |  | 61.919 | 277.247 | 0 | 307 |  |  |  | 61.92 | 532.86 | 0.157 | 84 | 0
899.56 | 277.361 | 0 | 298 |  |  |  | 61.92 | 277.33 | 0 | 301 |  |  |  | 61.92 | 277.302 | 0 | 309 |  |  |  | 61.922 | 533.46 | 0.161 | 86 | 0
900.06 | 277.361 | 0 | 298 |  |  |  | 61.92 | 277.33 | 0 | 301 |  |  |  | 61.92 | 277.302 | 0 | 309 |  |  |  | 61.922 | 533.46 | 0.161 | 86 | 0
900.56 | 277.421 | 0 | 294 |  |  |  | 61.92 | 277.519 | 0 | 303 |  |  |  | 61.922 | 277.314 | 0 | 311 |  |  |  | 61.92 | 533.51 | 0.154 | 82 | 0
901.06 | 277.421 | 0 | 294 |  |  |  | 61.92 | 277.519 | 0 | 303 |  |  |  | 61.922 | 277.314 | 0 | 311 |  |  |  | 61.92 | 533.51 | 0.154 | 82 | 0
901.56 | 277.33 | 0 | 297 |  |  |  | 61.921 | 277.408 | 0 | 299 |  |  |  | 61.92 | 277.274 | 0 | 311 |  |  |  | 61.921 | 533.43 | 0.154 | 82 | 0
902.06 | 277.33 | 0 | 297 |  |  |  | 61.921 | 277.408 | 0 | 299 |  |  |  | 61.92 | 277.274 | 0 | 311 |  |  |  | 61.921 | 533.43 | 0.154 | 82 | 0
902.56 | 277.404 | 0 | 295 |  |  |  | 61.921 | 277.287 | 0 | 300 |  |  |  | 61.92 | 277.234 | 0 | 310 |  |  |  | 61.919 | 539.13 | 0.156 | 84 | 0
903.06 | 277.404 | 0 | 295 |  |  |  | 61.921 | 277.287 | 0 | 300 |  |  |  | 61.92 | 277.234 | 0 | 310 |  |  |  | 61.919 | 539.13 | 0.156 | 84 | 0
903.56 | 277.328 | 0 | 292 |  |  |  | 61.921 | 277.435 | 0 | 299 |  |  |  | 61.921 | 277.218 | 0 | 305 |  |  |  | 61.921 | 539.82 | 0.156 | 84 | 0
904.06 | 277.328 | 0 | 292 |  |  |  | 61.921 | 277.435 | 0 | 299 |  |  |  | 61.921 | 277.218 | 0 | 305 |  |  |  | 61.921 | 539.82 | 0.156 | 84 | 0
904.56 | 277.37 | 0 | 299 |  |  |  | 61.919 | 277.34 | 0 | 308 |  |  |  | 61.92 | 277.309 | 0 | 313 |  |  |  | 61.92 | 533.81 | 0.154 | 82 | 0
905.06 | 277.37 | 0 | 299 |  |  |  | 61.919 | 277.34 | 0 | 308 |  |  |  | 61.92 | 277.309 | 0 | 313 |  |  |  | 61.92 | 533.81 | 0.154 | 82 | 0
905.56 | 277.321 | 0 | 296 |  |  |  | 61.92 | 277.508 | 0 | 303 |  |  |  | 61.923 | 277.289 | 0 | 310 |  |  |  | 61.921 | 533.36 | 0.151 | 81 | 0
906.06 | 277.321 | 0 | 296 |  |  |  | 61.92 | 277.508 | 0 | 303 |  |  |  | 61.923 | 277.289 | 0 | 310 |  |  |  | 61.921 | 533.36 | 0.151 | 81 | 0
906.56 | 277.365 | 0 | 298 |  |  |  | 61.92 | 277.399 | 0 | 305 |  |  |  | 61.921 | 277.239 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.155 | 82 | 0
907.06 | 277.365 | 0 | 298 |  |  |  | 61.92 | 277.399 | 0 | 305 |  |  |  | 61.921 | 277.239 | 0 | 311 |  |  |  | 61.92 | 533.49 | 0.155 | 82 | 0
907.56 | 277.279 | 0 | 299 |  |  |  | 61.916 | 277.504 | 0 | 302 |  |  |  | 61.919 | 277.221 | 0 | 311 |  |  |  | 61.921 | 533.42 | 0.158 | 84 | 0
908.06 | 277.279 | 0 | 299 |  |  |  | 61.916 | 277.504 | 0 | 302 |  |  |  | 61.919 | 277.221 | 0 | 311 |  |  |  | 61.921 | 533.42 | 0.158 | 84 | 0
908.56 | 277.361 | 0 | 299 |  |  |  | 61.921 | 277.439 | 0 | 301 |  |  |  | 61.92 | 277.299 | 0 | 311 |  |  |  | 61.92 | 527.7 | 0.155 | 82 | 0
909.06 | 277.361 | 0 | 299 |  |  |  | 61.921 | 277.439 | 0 | 301 |  |  |  | 61.92 | 277.299 | 0 | 311 |  |  |  | 61.92 | 527.7 | 0.155 | 82 | 0
909.56 | 277.423 | 0 | 296 |  |  |  | 61.921 | 277.281 | 0 | 304 |  |  |  | 61.92 | 277.285 | 0 | 309 |  |  |  | 61.92 | 526.94 | 0.154 | 81 | 0
910.06 | 277.423 | 0 | 296 |  |  |  | 61.921 | 277.281 | 0 | 304 |  |  |  | 61.92 | 277.285 | 0 | 309 |  |  |  | 61.92 | 526.94 | 0.154 | 81 | 0
910.56 | 277.334 | 0 | 295 |  |  |  | 61.92 | 277.52 | 0 | 298 |  |  |  | 61.92 | 277.235 | 0 | 310 |  |  |  | 61.919 | 532.95 | 0.154 | 82 | 0
911.06 | 277.334 | 0 | 295 |  |  |  | 61.92 | 277.52 | 0 | 298 |  |  |  | 61.92 | 277.235 | 0 | 310 |  |  |  | 61.919 | 532.95 | 0.154 | 82 | 0
911.56 | 277.397 | 0 | 297 |  |  |  | 61.921 | 277.351 | 0 | 301 |  |  |  | 61.92 | 277.209 | 0 | 313 |  |  |  | 61.921 | 533.56 | 0.157 | 84 | 0
912.06 | 277.397 | 0 | 297 |  |  |  | 61.921 | 277.351 | 0 | 301 |  |  |  | 61.92 | 277.209 | 0 | 313 |  |  |  | 61.921 | 533.56 | 0.157 | 84 | 0
912.56 | 277.332 | 0 | 296 |  |  |  | 61.919 | 277.508 | 0 | 304 |  |  |  | 61.923 | 277.308 | 0 | 311 |  |  |  | 61.919 | 533.33 | 0.155 | 82 | 0
913.06 | 277.332 | 0 | 296 |  |  |  | 61.919 | 277.508 | 0 | 304 |  |  |  | 61.923 | 277.308 | 0 | 311 |  |  |  | 61.919 | 533.33 | 0.155 | 82 | 0
913.56 | 277.386 | 0 | 299 |  |  |  | 61.921 | 277.418 | 0 | 305 |  |  |  | 61.919 | 277.293 | 0 | 312 |  |  |  | 61.92 | 533.32 | 0.154 | 82 | 0
914.06 | 277.386 | 0 | 299 |  |  |  | 61.921 | 277.418 | 0 | 305 |  |  |  | 61.919 | 277.293 | 0 | 312 |  |  |  | 61.92 | 533.32 | 0.154 | 82 | 0
914.56 | 277.307 | 0 | 300 |  |  |  | 61.92 | 277.343 | 0 | 301 |  |  |  | 61.919 | 277.27 | 0 | 309 |  |  |  | 61.919 | 539.06 | 0.158 | 85 | 0
915.06 | 277.307 | 0 | 300 |  |  |  | 61.92 | 277.343 | 0 | 301 |  |  |  | 61.919 | 277.27 | 0 | 309 |  |  |  | 61.919 | 539.06 | 0.158 | 85 | 0
915.56 | 277.386 | 0 | 294 |  |  |  | 61.92 | 277.475 | 0 | 298 |  |  |  | 61.92 | 277.221 | 0 | 307 |  |  |  | 61.92 | 539.77 | 0.159 | 86 | 0
916.06 | 277.386 | 0 | 294 |  |  |  | 61.92 | 277.475 | 0 | 298 |  |  |  | 61.92 | 277.221 | 0 | 307 |  |  |  | 61.92 | 539.77 | 0.159 | 86 | 0
916.56 | 277.273 | 0 | 300 |  |  |  | 61.917 | 277.316 | 0 | 308 |  |  |  | 61.918 | 277.309 | 0 | 313 |  |  |  | 61.92 | 533.95 | 0.157 | 84 | 0
917.06 | 277.273 | 0 | 300 |  |  |  | 61.917 | 277.316 | 0 | 308 |  |  |  | 61.918 | 277.309 | 0 | 313 |  |  |  | 61.92 | 533.95 | 0.157 | 84 | 0
917.56 | 277.355 | 0 | 298 |  |  |  | 61.921 | 277.45 | 0 | 305 |  |  |  | 61.92 | 277.295 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 0
918.1 | 277.355 | 0 | 298 |  |  |  | 61.921 | 277.45 | 0 | 305 |  |  |  | 61.92 | 277.295 | 0 | 311 |  |  |  | 61.92 | 533.45 | 0.153 | 82 | 0
918.6 | 277.428 | 0 | 301 |  |  |  | 61.92 | 277.329 | 0 | 306 |  |  |  | 61.919 | 277.284 | 0 | 313 |  |  |  | 61.92 | 533.32 | 0.158 | 84 | 0
919.07 | 277.428 | 0 | 301 |  |  |  | 61.92 | 277.329 | 0 | 306 |  |  |  | 61.919 | 277.284 | 0 | 313 |  |  |  | 61.92 | 533.32 | 0.158 | 84 | 0
919.57 | 277.327 | 0 | 301 |  |  |  | 61.92 | 277.536 | 0 | 305 |  |  |  | 61.922 | 277.224 | 0 | 313 |  |  |  | 61.921 | 533.38 | 0.158 | 84 | 0
920.06 | 277.327 | 0 | 301 |  |  |  | 61.92 | 277.536 | 0 | 305 |  |  |  | 61.922 | 277.224 | 0 | 313 |  |  |  | 61.921 | 533.38 | 0.158 | 84 | 0
920.56 | 277.387 | 0 | 297 |  |  |  | 61.921 | 277.377 | 0 | 304 |  |  |  | 61.919 | 277.318 | 0 | 310 |  |  |  | 61.922 | 527.68 | 0.153 | 81 | 0
921.1 | 277.341 | 0 | 297 |  |  |  | 61.921 | 277.258 | 0 | 299 |  |  |  | 61.92 | 277.295 | 0 | 305 |  |  |  | 61.919 | 526.93 | 0.151 | 79 | 0
921.6 | 277.341 | 0 | 297 |  |  |  | 61.921 | 277.258 | 0 | 299 |  |  |  | 61.92 | 277.295 | 0 | 305 |  |  |  | 61.919 | 526.93 | 0.151 | 79 | 0
922.08 | 277.384 | 0 | 295 |  |  |  | 61.919 | 277.45 | 0 | 301 |  |  |  | 61.919 | 277.286 | 0 | 309 |  |  |  | 61.92 | 532.76 | 0.155 | 82 | 0
922.58 | 277.384 | 0 | 295 |  |  |  | 61.919 | 277.45 | 0 | 301 |  |  |  | 61.919 | 277.286 | 0 | 309 |  |  |  | 61.92 | 532.76 | 0.155 | 82 | 0
923.07 | 277.307 | 0 | 295 |  |  |  | 61.92 | 277.311 | 0 | 304 |  |  |  | 61.919 | 277.263 | 0 | 311 |  |  |  | 61.92 | 533.37 | 0.157 | 84 | 0
923.57 | 277.307 | 0 | 295 |  |  |  | 61.92 | 277.311 | 0 | 304 |  |  |  | 61.919 | 277.263 | 0 | 311 |  |  |  | 61.92 | 533.37 | 0.157 | 84 | 0
924.06 | 277.373 | 0 | 293 |  |  |  | 61.921 | 277.475 | 0 | 303 |  |  |  | 61.922 | 277.209 | 0 | 311 |  |  |  | 61.921 | 533.38 | 0.154 | 82 | 0
924.56 | 277.373 | 0 | 293 |  |  |  | 61.921 | 277.475 | 0 | 303 |  |  |  | 61.922 | 277.209 | 0 | 311 |  |  |  | 61.921 | 533.38 | 0.154 | 82 | 0
925.06 | 277.28 | 0 | 299 |  |  |  | 61.918 | 277.359 | 0 | 302 |  |  |  | 61.92 | 277.286 | 0 | 310 |  |  |  | 61.919 | 533.45 | 0.156 | 83 | 0
925.56 | 277.28 | 0 | 299 |  |  |  | 61.918 | 277.359 | 0 | 302 |  |  |  | 61.92 | 277.286 | 0 | 310 |  |  |  | 61.919 | 533.45 | 0.156 | 83 | 0
926.06 | 277.347 | 0 | 296 |  |  |  | 61.921 | 277.351 | 0 | 299 |  |  |  | 61.92 | 277.259 | 0 | 308 |  |  |  | 61.921 | 539.08 | 0.154 | 83 | 0
926.56 | 277.347 | 0 | 296 |  |  |  | 61.921 | 277.351 | 0 | 299 |  |  |  | 61.92 | 277.259 | 0 | 308 |  |  |  | 61.921 | 539.08 | 0.154 | 83 | 0
927.06 | 277.414 | 0 | 295 |  |  |  | 61.921 | 277.369 | 0 | 295 |  |  |  | 61.92 | 277.264 | 0 | 302 |  |  |  | 61.921 | 539.88 | 0.159 | 86 | 0
927.56 | 277.414 | 0 | 295 |  |  |  | 61.921 | 277.369 | 0 | 295 |  |  |  | 61.92 | 277.264 | 0 | 302 |  |  |  | 61.921 | 539.88 | 0.159 | 86 | 0
928.06 | 277.334 | 0 | 301 |  |  |  | 61.921 | 277.291 | 0 | 307 |  |  |  | 61.919 | 277.221 | 0 | 312 |  |  |  | 61.92 | 534.04 | 0.154 | 82 | 0
928.56 | 277.334 | 0 | 301 |  |  |  | 61.921 | 277.291 | 0 | 307 |  |  |  | 61.919 | 277.221 | 0 | 312 |  |  |  | 61.92 | 534.04 | 0.154 | 82 | 0
929.06 | 277.374 | 0 | 296 |  |  |  | 61.92 | 277.408 | 0 | 300 |  |  |  | 61.92 | 277.321 | 0 | 312 |  |  |  | 61.92 | 533.28 | 0.154 | 82 | 0
929.56 | 277.374 | 0 | 296 |  |  |  | 61.92 | 277.408 | 0 | 300 |  |  |  | 61.92 | 277.321 | 0 | 312 |  |  |  | 61.92 | 533.28 | 0.154 | 82 | 0
930.06 | 277.348 | 0 | 300 |  |  |  | 61.919 | 277.276 | 0 | 303 |  |  |  | 61.92 | 277.271 | 0 | 311 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 0
930.56 | 277.348 | 0 | 300 |  |  |  | 61.919 | 277.276 | 0 | 303 |  |  |  | 61.92 | 277.271 | 0 | 311 |  |  |  | 61.92 | 533.42 | 0.152 | 81 | 0
931.06 | 277.382 | 0 | 297 |  |  |  | 61.921 | 277.458 | 0 | 304 |  |  |  | 61.923 | 277.251 | 0 | 312 |  |  |  | 61.921 | 533.25 | 0.157 | 84 | 0
931.56 | 277.382 | 0 | 297 |  |  |  | 61.921 | 277.458 | 0 | 304 |  |  |  | 61.923 | 277.251 | 0 | 312 |  |  |  | 61.921 | 533.25 | 0.157 | 84 | 0
932.06 | 277.314 | 0 | 297 |  |  |  | 61.92 | 277.356 | 0 | 304 |  |  |  | 61.92 | 277.23 | 0 | 310 |  |  |  | 61.921 | 527.74 | 0.157 | 83 | 0
932.56 | 277.314 | 0 | 297 |  |  |  | 61.92 | 277.356 | 0 | 304 |  |  |  | 61.92 | 277.23 | 0 | 310 |  |  |  | 61.921 | 527.74 | 0.157 | 83 | 0
933.39 | 277.386 | 0 | 294 |  |  |  | 61.921 | 277.233 | 0 | 299 |  |  |  | 61.92 | 277.33 | 0 | 307 |  |  |  | 61.919 | 526.97 | 0.154 | 81 | 0
933.57 | 277.386 | 0 | 294 |  |  |  | 61.921 | 277.233 | 0 | 299 |  |  |  | 61.92 | 277.33 | 0 | 307 |  |  |  | 61.919 | 526.97 | 0.154 | 81 | 0
934.06 | 277.468 | 0 | 295 |  |  |  | 58.578 | 277.659 | 0 | 301 |  |  |  | 58.58 | 277.46 | 0 | 310 |  |  |  | 58.58 | 532.75 | 0.156 | 83 | 0
934.56 | 277.468 | 0 | 295 |  |  |  | 58.578 | 277.659 | 0 | 301 |  |  |  | 58.58 | 277.46 | 0 | 310 |  |  |  | 58.58 | 532.75 | 0.156 | 83 | 0
935.06 | 278.786 | 0 | 298 |  |  |  | 58.58 | 278.778 | 0 | 297 |  |  |  | 58.58 | 278.501 | 0 | 307 |  |  |  | 58.58 | 533.06 | 0.155 | 82 | 0
935.56 | 278.786 | 0 | 298 |  |  |  | 58.58 | 278.778 | 0 | 297 |  |  |  | 58.58 | 278.501 | 0 | 307 |  |  |  | 58.58 | 533.06 | 0.155 | 82 | 0
936.06 | 278.435 | 0 | 299 |  |  |  | 58.58 | 278.489 | 0 | 303 |  |  |  | 58.583 | 277.985 | 0 | 316 |  |  |  | 58.58 | 533.41 | 0.155 | 83 | 0
936.56 | 278.435 | 0 | 299 |  |  |  | 58.58 | 278.489 | 0 | 303 |  |  |  | 58.583 | 277.985 | 0 | 316 |  |  |  | 58.58 | 533.41 | 0.155 | 83 | 0
937.06 | 277.974 | 0 | 300 |  |  |  | 58.581 | 277.989 | 0 | 304 |  |  |  | 58.579 | 277.78 | 0 | 315 |  |  |  | 58.58 | 533.43 | 0.152 | 81 | 0
937.56 | 277.974 | 0 | 300 |  |  |  | 58.581 | 277.989 | 0 | 304 |  |  |  | 58.579 | 277.78 | 0 | 315 |  |  |  | 58.58 | 533.43 | 0.152 | 81 | 0
938.06 | 277.776 | 0 | 294 |  |  |  | 58.581 | 277.777 | 0 | 301 |  |  |  | 58.58 | 277.573 | 0 | 310 |  |  |  | 58.58 | 537.22 | 0.152 | 81 | 0
938.56 | 277.776 | 0 | 294 |  |  |  | 58.581 | 277.777 | 0 | 301 |  |  |  | 58.58 | 277.573 | 0 | 310 |  |  |  | 58.58 | 537.22 | 0.152 | 81 | 0
939.06 | 277.601 | 0 | 292 |  |  |  | 58.581 | 277.644 | 0 | 296 |  |  |  | 58.58 | 277.429 | 0 | 308 |  |  |  | 58.58 | 539.74 | 0.157 | 85 | 0
939.56 | 277.601 | 0 | 292 |  |  |  | 58.581 | 277.644 | 0 | 296 |  |  |  | 58.58 | 277.429 | 0 | 308 |  |  |  | 58.58 | 539.74 | 0.157 | 85 | 0
940.06 | 277.564 | 0 | 302 |  |  |  | 58.581 | 277.406 | 0 | 304 |  |  |  | 58.58 | 277.356 | 0 | 316 |  |  |  | 58.58 | 536.54 | 0.159 | 85 | 0
940.56 | 277.564 | 0 | 302 |  |  |  | 58.581 | 277.406 | 0 | 304 |  |  |  | 58.58 | 277.356 | 0 | 316 |  |  |  | 58.58 | 536.54 | 0.159 | 85 | 0
941.06 | 277.38 | 0 | 299 |  |  |  | 58.58 | 277.551 | 0 | 304 |  |  |  | 58.579 | 277.439 | 0 | 309 |  |  |  | 58.582 | 533.4 | 0.158 | 84 | 0
941.56 | 277.38 | 0 | 299 |  |  |  | 58.58 | 277.551 | 0 | 304 |  |  |  | 58.579 | 277.439 | 0 | 309 |  |  |  | 58.582 | 533.4 | 0.158 | 84 | 0
942.06 | 277.453 | 0 | 297 |  |  |  | 58.58 | 277.388 | 0 | 300 |  |  |  | 58.581 | 277.395 | 0 | 309 |  |  |  | 58.58 | 533.35 | 0.152 | 81 | 0
942.56 | 277.453 | 0 | 297 |  |  |  | 58.58 | 277.388 | 0 | 300 |  |  |  | 58.581 | 277.395 | 0 | 309 |  |  |  | 58.58 | 533.35 | 0.152 | 81 | 0
943.06 | 277.37 | 0 | 300 |  |  |  | 58.58 | 277.594 | 0 | 304 |  |  |  | 58.583 | 277.358 | 0 | 312 |  |  |  | 58.579 | 533.3 | 0.157 | 84 | 0